## 
Central Electricity Regulatory Commission
Capital Cost Benchmarking for Transmission Lines

## L
CERC
Capital Cost Benchmarking
Formatting of Headers / Dividers
| Sheet Header 1 | CERC | SheetHeader1
| Sheet Header 2 | Capital Cost Benchmarking | SheetHeader2
| Sheet Header 3 |  | SheetHeader3
| Header 1 | Header 1 | Header1
| Header 2 | Header 2 | Header2
| Header 3 | Header 3 | Header3
| Inputs Divider | Operational Assumptions | Inputs_Divider
| Table Heading 2 | Table Heading 2 | Table_Heading2
Individual Cell Assumptions
| Standard Assumption | 100 | Assumptions
| Offsheet Reference | 100 | Offsheet
| Flex Cell | 100 | Assumption_Flex
| Name Inputs | Cost Type | Technical_Input
| Technical Input | 1000 | Input
| Empy Cell |  | Empty_Cell
| Background for Flag | 0 | Flag
Infrastructure
| Line Total | 100 | Line_Summary
| Units | USD | Unit
| Operation Line (Non-Addition) | 100 | Line_Operation
| Operation (Addition / Total) | 100 | Line_Total
| Closing Balance | 100 | Line_ClosingBal
| Key Line | 100 | Line_Key
Development Styles
| WIP | W | WIP

## User Guide
CERC
Capital Cost Benchmarking
Use Guide
| 1 | Month and Year of Escalation
The desired month and year of escalation may be chosen from the drop down list
| 2 | Insulators
Three different types of insulators have been incorporated in the Model. - Standard type of Porcelain insulators - Anti-fog insulators for use in coastal and other polluted areas - Polymer insulators User to select the type of insulator, using the drop down list
| 3 | Type of Terrain
User to select the applicable terrain type. Options of Plain and Hilly terrain have been provided in drop down list
| 4 | Voltage Level
User to select the applicable voltage level. Options of 400 kV and 765 kV have been provided in drop down list
| 5 | Conductor Configuration
User may select from the options from drop down list. This options include: :- - ACSR Twin Moose - ACSR Triple Moose - ACSR Quad Moose - ACSR Twin Bersimis - ACSR Triple Bersmis - ACSR Quad Bersimis
| 6 | Wind Zone
As per IS 802:1995, India has been classified into 6 wind zones with the following wind speeds
| S.No. | Wind Zone | Wind Speed in m/sec
| 1 | Wind Zone-1 | 33
| 2 | Wind Zone-2 | 39
| 3 | Wind Zone-3 | 44
| 4 | Wind Zone-4 | 47
| 5 | Wind Zone-5 | 50
| 6 | Wind Zone-6 | 55
User to select the applicable wind zone
| 7 | Terrain Category
As per IS-802;1995 each wind zone is further classified into three terrain categories for determining the drag coefficient as follows:
| 1 | Terrain Category-1: Normal Cross-country terrain with very few obstacles
| 2 | Terrain Category-2 : Coastal areas, deserts and large stretches of water
| 3 | Terrain Category-3: Urban built up areas or forest areas
User to select the applicable wind zone
| 8 | Circuit Type
User to select from the applicable circuit type. The option of single and double circuit has been provided in the drop down list
| 9 | Number of Towers
User to manually feed the number of towers for A , B, C and D type respectively. In case of non-availability of data following standards may be used
Standard for Number of Tower per 100 kM of length
| S.No. | Type of Tower | Hilly | Plain
| 1 | A' Type towers | 70 | 210
| 2 | B' Type towers | 90 | 25
| 3 | C' Type towers | 45 | 25
| 4 | D' Type towers | 80 | 20
| 10 | Length of Line
Length of Line as applicable to feed by user manually
| 11 | Number of River Crossings
Number of River Crossings as applicable to be fed by user manually
| 12 | In case a line passes through multiple wind zones, length of line shall be segregated accordingly. The user shall run the model multiple times (twice or thrice or more) as the case may be to obtain the cost. The other details should be obtained for all the sections of the line.

## Computation_Sheet
CERC
Capital Cost Benchmarking
| Choose Month and Year | 2009-05-01
 | time axis 2004-01-01 to 2014-03-01
| Pariculars | Values
| Insulator Type | Standard |  | Select from the drop down list | 2004-10-01: Standard
| Type of Terrain | Plain |  | Select from the drop down list | 2004-10-01: Antifog
| Voltage Level | 765 kV |  | Select from the drop down list | 2004-10-01: Polymer
| Conductor Configuration | ACSR Quad Moose |  | Select from the drop down list | 2004-10-01: Plain
| Wind Zone | Wind Zone-4 |  | Select from the drop down list | 2004-10-01: Hilly
| Terrain Category | Terrian Category-2 |  | Select from the drop down list | 2004-10-01: Terrian Category-1
| Circuit Type | Single Circuit |  | Select from the drop down list | 2004-10-01: Terrian Category-2
| Length of Line (Km) | 100 |  | Feed manually | 2004-10-01: Terrian Category-3
| Number of A-Type of Towers | 0 |  | Feed manually
| Number of B-Type of Towers | 0 |  | Feed manually | 2004-10-01: Wind Zone-1
| Number of C-Type of Towers | 0 |  | Feed manually | 2004-10-01: Wind Zone-2
| Number of D-Type of Towers | 4 |  | Feed manually | 2004-10-01: Wind Zone-3
Wind Zone-4
Wind Zone-5
Wind Zone-6
400 kV
| Cost of Line (Rs.Lakh/Ckt Km) | 19.6628 |  |  | 2004-10-01: 765 kV
Single Circuit
Double Circuit
| Total Cost -excluding river crossings (INR Lakhs) | 1966.282
ACSR Twin Moose
| Cost per River Crossing (INR Lakhs) | 175 |  |  | 2004-10-01: ACSR Triple Moose
| Number of River Crossings | 0 |  | Feed manually | 2004-10-01: ACSR Quad Moose
ACSR Twin Bersimis
| Total Cost of Tranmission Line (INR Crores) | 19.6628 |  |  | 2004-10-01: ACSR Triple Bersimis
ACSR Quad Bersimis
Taxes and Duties
|  | Present | Updated
| Excise Duty (on Ex-Works Price) | 8% | 0%
| Cess on ED (on Excise Duty) | 3% | 0%
| Central Sales Tax (on Ex-Works Price + ED + Cess) | 2% | 0%
| ED+ Cess | 8.24%
| Central sales Tax | 2.165%
| Total | 10.4%
Transportation Charges
| Tower Parts | 4%
| ACSR Conductor | 1%
| Ground Wire | 3%
| Insulators | 4.5%
| Reinforcements | 3%
| Other Materials | 2%

## Search
CERC
Capital Cost Benchmarking
| Choose of the Component | Stone bound wire netting | HT Tower parts
MS Tower parts
Stubs-HT
| Name of the Project | Unit Rate of Component (INR) | Stubs-MS
| Pichore-Gwalior | 2954.4665 | Hex. Bolts and Nuts
| Bina-Pichore | 4124.842 | Anti theft Bolts and Nuts
| Sasaram-Fatepur | 2882.2445 | Earthing Pipe type
| Balia-Luknow | 1912.5152 | Earthing Counterpoise
| Raigarh-Raipur | 3794.2109 | River Crossing locations (MT)
| Muvattupuzha-North | 7215.7361 | Danger Plate
| Ranchi-1-Sipat | 2780.3658 | Number Plate
| Gaya-Balia | 1603.4969 | Phase Plate (Set of three)
| BINA-GWALIOR | 3995.9893 | Circuit plates
| DURGAPUR-MAITHON | 1037.1458 | Anti climbing device
| Kanpur-Ballabhgrh | 991.8932 | Bird guard
| Vapi-Navi Mumbai | 1304.6029 | ACSR Moose Conductor
| Edamon-Muvattupuzha(Part-I) | 1784.0231 | GSS Ground wire
| Kaithal-Meerut | 1060.9083 | Single 'V' suspension
| Ranchi-Rourkela | 0 | Double 'V' Suspension
| Maithon RB TPS -Ranchi | 0 | Single 'I' Pilot
| Mejia 'B' TPS-Maithon(PG) | 3115.4898 | Single 'V' Pilot
| Rourkela-Raigrah | 2467.6635 | Double 'I' suspension
| Sasaram-Biharsharif | 0 | Single 'I' suspension
| Ranchi(old)-Ranchi(new)(Line-1) | 2588.9573 | Single tension string
| Ranchi(old)-Ranchi(new)(Line-2) | 2588.9573 | Double tension string
| Maithon RB TPS- Maithon (PG) | 0 | MSC joints for conductors
| Maithon -Jamshedpur(LILO atMejia 'B' TPS) | 0 | MSC joints for GW
| Edamon- Muvattupuzha(Part II) | 170.0702 | Flexible copper earth bonds
| Bokaro TPS-Kodarma TPS | 0 | Vibration dampers for GW
| Kodarma-Gaya | 0 | Quad spacer damper for conductor
| Pindwara-Kankroli | 2661.2984 | Quad rigid spacer for conductor
| Madurai-Trivandrum | 0 | Vibration damper for conductor
Rigid spacer for jumpers
Earthwire suspension clamps
Earthwire tension clamps
Repair sleeve for conductor
T-Connector for ACSR Moose Conductor.
Bundle spacer for line
Repair Sleeves for Ground wire
Span markers
Obstruction lights
Wind measuring equipments
Detailed survey
Check survey
Soil Investigation
All kinds except FR and HR
Fissured rock
Hard rock
River Crossing locations
All kinds except FR and HR
Fissured rock
Hard rock
Dry soil
Wet soil
Dry Fissured Rock
Wet Fissured Rock
Hard Rock
1:1½:3 Concreting
1:3:6 Concreting
Reinforcements
Installation of stubs
Erection of towers
Installation of earthing of towers
Earthing Pipe type
Earthing River Crossing Tower
Earthing Counterpoise
Installation of tower accessories
River Crossing Location -Pile Foundation
Protection to tower footing
Random rubble masonry
Stone bound wire netting
Back filling
M15 concrete for top seal cover of revetments
Installation of Insulators and stringing
Stringing across river crossing
Painting of towers (MT) etc.
Transportation

## Database
CERC
Capital Cost Benchmarking
| Insulator Type | Type of Terrain | Voltage Level | Conductor Configuration | Wind Zone | Terrain Category | Circuit Type | Cost/km (Rs.Lakh)
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 33.1288
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 33.1036
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 33.0414
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 33.2979
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 33.264
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 33.1786
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 33.4523
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 33.4113
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 33.3074
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 33.5492
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 33.5041
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 33.3893
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 33.6487
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 33.5995
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 33.474
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 33.8192
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 33.7634
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 33.6202
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 47.2087
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 47.1757
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 47.0948
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 47.4293
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 47.3845
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 47.2729
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 47.6318
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 47.5775
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 47.4408
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 47.7594
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 47.6995
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 47.5481
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 47.8906
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 47.8252
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 47.6593
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 48.1162
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 48.0416
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 47.8518
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 62.1099
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 62.0709
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 61.9758
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 62.3704
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 62.3172
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 62.1851
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 62.6109
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 62.5461
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 62.3836
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 62.763
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 62.6912
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 62.5108
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 62.9198
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 62.8412
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 62.643
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 18.9186
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 18.8859
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 18.8214
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 18.6225
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 18.6078
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 18.5799
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 18.6953
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 18.6753
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 18.6369
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 18.7616
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 18.7375
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 18.6906
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 18.8032
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 18.7767
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 18.7248
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 18.8458
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 18.8169
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 18.7602
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 18.9186
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 18.8859
| Standard | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 18.8214
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 25.6337
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 25.6149
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 25.5798
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 25.7256
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 25.6999
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 25.6512
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 25.81
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 25.7788
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 25.719
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 25.863
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 25.8287
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 25.7624
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 25.9175
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 25.88
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 25.8074
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 26.0109
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 25.9683
| Standard | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 25.8853
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 33.4784
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 33.4558
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 33.4139
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 33.5884
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 33.5574
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 33.499
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 33.6897
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 33.652
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 33.58
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 33.7536
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 33.7119
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 33.632
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 33.8193
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 33.7738
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 33.6861
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 33.9323
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 33.8804
| Standard | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 33.7799
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 19.3878
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 19.3627
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 19.3155
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 19.5169
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 19.4832
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 19.4186
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 19.6342
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 19.5935
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 19.5152
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 19.7074
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 19.6628
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 19.5764
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 19.7823
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 19.7339
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 19.6396
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 19.9101
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 19.8553
| Standard | Plain | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 19.7484
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 26.3954
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 26.3674
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 26.3158
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 26.5357
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 26.4982
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 26.4278
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 26.6627
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 26.6178
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 26.5325
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 26.7418
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 26.6927
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 26.5988
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 26.8225
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 26.7692
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 26.6671
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 26.9598
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 26.8998
| Standard | Plain | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 26.7843
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 36.1978
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 36.1646
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 36.104
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 36.363
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 36.3183
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 36.2352
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 36.513
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 36.4593
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 36.3583
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 36.6067
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 36.5478
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 36.4365
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 36.7024
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 36.6385
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 36.5172
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 36.8656
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 36.7934
| Standard | Plain | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 36.6559
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 34.5901
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 34.5623
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 34.4939
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 34.777
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 34.7394
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 34.645
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 34.9486
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 34.903
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 34.7875
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 35.0567
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 35.0063
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 34.8785
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 35.1679
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 35.1129
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 34.9727
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 35.3591
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 35.2964
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 35.136
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 48.7035
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 48.6668
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 48.5769
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 48.9498
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 48.8997
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 48.7749
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 49.1771
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 49.1161
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 48.9627
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 49.3208
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 49.2533
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 49.083
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 49.469
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 49.3951
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 49.208
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 49.7246
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 49.64
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 49.4251
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 63.4775
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 63.4336
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 63.3267
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 63.7716
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 63.7113
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 63.5621
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 64.0445
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 63.9708
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 63.7865
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 64.2176
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 64.1359
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 63.9307
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 64.3966
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 64.3069
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 64.0809
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 64.7063
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 64.6032
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 64.3427
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 20.037
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 20.021
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 19.9908
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 20.1163
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 20.0945
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 20.0526
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 20.189
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 20.1625
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 20.1112
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 20.2346
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 20.2055
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 20.1486
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 20.2816
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 20.2498
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 20.1874
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 20.362
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 20.3259
| Standard | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 20.2546
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 27.0598
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 27.0391
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 27.0007
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 27.1609
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 27.1326
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 27.079
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 27.2541
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 27.2196
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 27.1536
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 27.3129
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 27.2748
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 27.2015
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 27.3735
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 27.3318
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 27.2513
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 27.4777
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 27.4302
| Standard | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 27.3377
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 34.8357
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 34.8107
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 34.7647
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 34.9575
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 34.9231
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 34.8584
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 35.0703
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 35.0282
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 34.9482
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 35.1416
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 35.0951
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 35.006
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 35.2152
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 35.1642
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 35.0662
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 35.3421
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 35.2837
| Standard | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 35.1711
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 20.8229
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 20.7956
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 20.7445
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 20.9635
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 20.9266
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 20.8564
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 21.0917
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 21.0472
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 20.9615
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 21.1721
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 21.1232
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 21.0285
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 21.2546
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 21.2012
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 21.0977
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 21.3957
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 21.3352
| Standard | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 21.2173
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 27.8899
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 27.8571
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 27.7969
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 28.0555
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 28.0111
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 27.928
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 28.2068
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 28.1531
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 28.0516
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 28.3018
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 28.2427
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 28.1304
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 28.3992
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 28.3348
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 28.212
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 28.566
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 28.4929
| Standard | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 28.3529
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 37.6483
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 37.6056
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 37.5284
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 37.8624
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 37.8041
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 37.6965
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 38.0598
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 37.9888
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 37.8563
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 38.1843
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 38.1058
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 37.9588
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 38.3125
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 38.2267
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 38.0653
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 38.5331
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 38.4352
| Standard | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 38.25
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 33.265
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 33.2398
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 33.1776
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 33.4341
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 33.4001
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 33.3148
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 33.5885
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 33.5475
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 33.4436
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 33.6854
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 33.6403
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 33.5255
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 33.7849
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 33.7357
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 33.6102
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 33.9554
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 33.8995
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 33.7564
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 47.3449
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 47.3119
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 47.231
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 47.5655
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 47.5207
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 47.409
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 47.768
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 47.7137
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 47.577
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 47.8955
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 47.8357
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 47.6843
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 48.0268
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 47.9614
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 47.7954
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 48.2524
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 48.1778
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 47.9879
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 62.3186
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 62.2796
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 62.1845
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 62.5791
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 62.5259
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 62.3937
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 62.8196
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 62.7548
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 62.5923
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 62.9716
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 62.8999
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 62.7195
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 63.1285
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 63.0499
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 62.8517
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 63.3989
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 63.309
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 63.0812
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 18.7225
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 18.7077
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 18.6798
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 18.7952
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 18.7752
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 18.7368
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 18.8616
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 18.8375
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 18.7905
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 18.9031
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 18.8766
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 18.8248
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 18.9457
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 18.9169
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 18.8602
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 19.0185
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 18.9859
| Antifog | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 18.9213
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 25.7336
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 25.7148
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 25.6797
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 25.8255
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 25.7999
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 25.7511
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 25.9099
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 25.8788
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 25.8189
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 25.9629
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 25.9286
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 25.8623
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 26.0174
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 25.98
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 25.9073
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 26.1109
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 26.0683
| Antifog | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 25.9853
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 33.6146
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 33.5919
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 33.5501
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 33.7245
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 33.6935
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 33.6351
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 33.8259
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 33.7881
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 33.7162
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 33.8898
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 33.8481
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 33.7682
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 33.9555
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 33.91
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 33.8223
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 34.0685
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 34.0166
| Antifog | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 33.9161
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 19.6591
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 19.634
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 19.5868
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 19.7883
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 19.7545
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 19.6899
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 19.9055
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 19.8649
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 19.7865
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 19.9787
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 19.9341
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 19.8477
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 20.0536
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 20.0052
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 19.911
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 20.1814
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 20.1267
| Antifog | Plain | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 20.0197
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 26.5598
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 26.5319
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 26.4803
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 26.7002
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 26.6627
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 26.5923
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 26.8272
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 26.7823
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 26.697
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 26.9063
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 26.8571
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 26.7633
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 26.987
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 26.9337
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 26.8315
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 27.1243
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 27.0643
| Antifog | Plain | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 26.9487
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 36.5554
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 36.5222
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 36.4617
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 36.7206
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 36.6759
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 36.5929
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 36.8706
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 36.8169
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 36.716
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 36.9643
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 36.9054
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 36.7941
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 37.0601
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 36.9961
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 36.8748
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 37.2232
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 37.151
| Antifog | Plain | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 37.0135
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 34.7262
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 34.6985
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 34.63
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 34.9132
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 34.8756
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 34.7812
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 35.0848
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 35.0392
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 34.9237
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 35.1928
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 35.1425
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 35.0146
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 35.304
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 35.2491
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 35.1089
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 35.4953
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 35.4326
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 35.2722
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 48.8397
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 48.803
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 48.7131
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 49.0859
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 49.0358
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 48.9111
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 49.3133
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 49.2522
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 49.0989
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 49.457
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 49.3895
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 49.2192
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 49.6052
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 49.5312
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 49.3442
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 49.8608
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 49.7762
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 49.5613
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 63.6136
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 63.5698
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 63.4629
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 63.9077
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 63.8475
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 63.6983
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 64.1807
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 64.1069
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 63.9226
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 64.3538
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 64.2721
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 64.0669
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 64.5328
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 64.4431
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 64.2171
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 64.8425
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 64.7394
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 64.4789
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 20.137
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 20.1209
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 20.0907
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 20.2162
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 20.1944
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 20.1525
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 20.2889
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 20.2625
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 20.2111
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 20.3346
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 20.3054
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 20.2485
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 20.3815
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 20.3497
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 20.2874
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 20.462
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 20.4258
| Antifog | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 20.3546
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 27.1597
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 27.1391
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 27.1007
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 27.2608
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 27.2325
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 27.1789
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 27.354
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 27.3196
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 27.2535
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 27.4128
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 27.3748
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 27.3014
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 27.4734
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 27.4318
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 27.3512
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 27.5777
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 27.5301
| Antifog | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 27.4377
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 34.9357
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 34.9107
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 34.8646
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 35.0574
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 35.023
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 34.9584
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 35.1702
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 35.1281
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 35.0481
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 35.2415
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 35.195
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 35.106
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 35.3152
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 35.2641
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 35.1662
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 35.4421
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 35.3837
| Antifog | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 35.271
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 21.0942
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 21.0669
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 21.0158
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 21.2348
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 21.1979
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 21.1277
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 21.363
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 21.3185
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 21.2329
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 21.4434
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 21.3945
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 21.2998
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 21.5259
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 21.4726
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 21.3691
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 21.6671
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 21.6065
| Antifog | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 21.4886
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 28.1612
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 28.1285
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 28.0683
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 28.3268
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 28.2824
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 28.1993
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 28.4781
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 28.4244
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 28.3229
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 28.5731
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 28.514
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 28.4018
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 28.6705
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 28.6061
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 28.4834
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 28.8373
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 28.7642
| Antifog | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 28.6243
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 37.9196
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 37.877
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 37.7997
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 38.1337
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 38.0754
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 37.9678
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 38.3311
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 38.2601
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 38.1276
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 38.4556
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 38.3772
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 38.2301
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 38.5838
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 38.498
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 38.3366
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 38.8045
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 38.7065
| Antifog | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 38.5214
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 35.1798
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 35.1137
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 35.3867
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 35.3504
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 35.2595
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 35.2595
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 35.552
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 35.508
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 35.3967
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 35.6561
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 35.6075
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 35.4843
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 35.7631
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 35.7101
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 35.5751
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 35.9472
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 35.8867
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 35.7322
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 50.292
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 50.2059
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 50.5626
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 50.5147
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 50.3954
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 50.3954
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 50.78
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 50.7216
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 50.5749
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 50.9174
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 50.8528
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 50.6899
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 51.0591
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 50.9883
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 50.8093
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 51.3035
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 51.2225
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 51.0169
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 66.2699
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 66.2283
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 66.127
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 66.5484
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 66.4913
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 66.35
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 66.8069
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 66.737
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 66.5623
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 66.9709
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 66.8934
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 66.6989
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 67.1406
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 67.0554
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 66.8412
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 67.4341
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 67.3363
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 67.0892
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 19.646
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 19.6165
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 19.7386
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 19.7174
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 19.6767
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 19.6767
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 19.8092
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 19.7834
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 19.7335
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 19.8535
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 19.8251
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 19.7699
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 19.899
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 19.8681
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 19.8075
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 19.977
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 19.9418
| Standard | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 19.8727
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 27.1731
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 27.1359
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 27.2908
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 27.2635
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 27.2116
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 27.2116
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 27.3809
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 27.3475
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 27.2837
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 27.4377
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 27.4008
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 27.3299
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 27.4962
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 27.4559
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 27.378
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 27.5967
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 27.5507
| Standard | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 27.4615
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 34.7703
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 34.7259
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 34.9115
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 34.8784
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 34.8162
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 34.8162
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 35.0199
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 34.9794
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 34.9025
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 35.0885
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 35.0437
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 34.9581
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 35.1593
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 35.1101
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 35.0159
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 35.2812
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 35.225
| Standard | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 35.1167
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 20.3964
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 20.3465
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 20.5598
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 20.5239
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 20.4555
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 20.4555
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 20.6845
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 20.641
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 20.5577
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 20.7625
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 20.7148
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 20.6227
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 20.8426
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 20.7905
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 20.69
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 20.9794
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 20.9204
| Standard | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 20.8059
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 28.0102
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 27.9476
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 28.217
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 28.1706
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 28.084
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 28.084
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 28.3753
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 28.3189
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 28.2128
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 28.4748
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 28.4127
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 28.2951
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 28.5771
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 28.5092
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 28.3805
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 28.7526
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 28.6753
| Standard | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 28.5281
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 38.3525
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 38.2779
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 38.5998
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 38.5436
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 38.44
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 38.44
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 38.7897
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 38.7212
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 38.5937
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 38.9094
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 38.8338
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 38.6923
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 39.0326
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 38.9499
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 38.7946
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 39.2445
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 39.1502
| Standard | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 38.9722
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 36.6666
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 36.6371
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 36.5645
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 36.8657
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 36.8255
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 36.7249
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 37.0494
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 37.0004
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 36.8768
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 37.1655
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 37.1113
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 36.9741
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 37.2853
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 37.2259
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 37.0751
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 37.4919
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 37.4239
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 37.2507
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 51.8201
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 51.781
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 51.6854
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 52.083
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 52.0293
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 51.8961
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 52.327
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 52.2613
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 52.0967
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 52.4818
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 52.4089
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 52.2257
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 52.642
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 52.5619
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 52.36
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 52.9191
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 52.8271
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 52.5942
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 67.635
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 67.5882
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 67.4745
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 67.9493
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 67.8847
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 67.7252
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 68.2427
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 68.1632
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 67.9652
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 68.4296
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 68.3412
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 68.12
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 68.6234
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 68.5261
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 68.2818
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 68.9598
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 68.8475
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 68.5647
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 21.0756
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 21.0586
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 21.0267
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 21.1595
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 21.1363
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 21.092
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 21.2368
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 21.2085
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 21.154
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 21.2855
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 21.2543
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 21.1937
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 21.3356
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 21.3015
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 21.235
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 21.4219
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 21.383
| Standard | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 21.3067
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 28.6185
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 28.5966
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 28.5559
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 28.7259
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 28.6957
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 28.6388
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 28.8254
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 28.7885
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 28.718
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 28.8884
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 28.8475
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 28.769
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 28.9535
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 28.9086
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 28.8222
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 29.0657
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 29.0143
| Standard | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 28.9149
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 36.9148
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 36.8882
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 36.8393
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 37.0444
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 37.0076
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 36.9388
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 37.165
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 37.1199
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 37.0344
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 37.2416
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 37.1915
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 37.0961
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 37.3209
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 37.2658
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 37.1606
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 37.4579
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 37.3947
| Standard | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 37.2731
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 21.8573
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 21.8284
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 21.7744
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 22.0062
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 21.967
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 21.8925
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 22.1426
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 22.095
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 22.0039
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 22.2283
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 22.1758
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 22.0749
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 22.3165
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 22.2591
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 22.1486
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 22.4677
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 22.4024
| Standard | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 22.2761
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 29.4983
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 29.4609
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 29.3924
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 29.6879
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 29.6367
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 29.5416
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 29.8627
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 29.8003
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 29.6832
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 29.9731
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 29.9041
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 29.774
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 30.0868
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 30.0113
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 29.8684
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 30.2826
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 30.1963
| Standard | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 30.0323
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 39.7204
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 39.6751
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 39.593
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 39.9485
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 39.8861
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 39.7715
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 40.1597
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 40.0834
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 39.9417
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 40.2934
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 40.2089
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 40.0512
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 40.4315
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 40.3388
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 40.1652
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 40.6697
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 40.5635
| Standard | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 40.3637
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 35.3428
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 35.3239
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 35.2602
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 35.5233
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 35.4884
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 35.4007
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 35.6828
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 35.6404
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 35.533
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 35.7833
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 35.7365
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 35.6175
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 35.8867
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 35.8355
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 35.7052
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 36.0646
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 36.0062
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 35.8569
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 50.4633
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 50.222
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 50.1449
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 50.4642
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 50.4214
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 50.3149
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 50.6591
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 50.6068
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 50.4756
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 50.7826
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 50.7246
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 50.5786
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 50.9103
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 50.8466
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 50.6859
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 51.1314
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 51.0582
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 50.8727
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 66.4786
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 66.4477
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 66.3497
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 66.7576
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 66.7023
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 66.5655
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 67.0082
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 66.9405
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 66.7712
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 67.1674
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 67.0922
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 66.9036
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 67.3321
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 67.2495
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 67.0416
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 67.6173
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 67.5222
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 67.2823
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 19.7615
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 19.7502
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 0
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 19.8395
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 19.819
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 19.7798
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 19.9075
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 19.8827
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 19.8346
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 19.9502
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 19.9229
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 19.8697
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 19.9941
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 19.9643
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 19.906
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 20.0693
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 20.0355
| Antifog | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 19.9688
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 522.3902
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 27.2785
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 27.2427
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 27.3919
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 27.3656
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 27.3156
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 27.4787
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 27.4466
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 27.3851
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 27.5335
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 27.498
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 27.4297
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 27.59
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 27.5511
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 27.476
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 27.6871
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 27.6427
| Antifog | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 27.5566
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 35.6946
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 35.6769
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 35.6341
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 35.813
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 35.7811
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 35.7211
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 35.9177
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 35.8786
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 35.8044
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 35.9839
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 35.9406
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 35.858
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 36.0522
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 36.0048
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 35.9139
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 36.1701
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 36.1158
| Antifog | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 36.0112
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 20.6944
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 20.6752
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 20.6272
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 20.8324
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 20.7979
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 20.7321
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 20.9523
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 20.9107
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 20.8305
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 21.0275
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 20.9817
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 20.8931
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 21.1046
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 21.0546
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 20.9578
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 21.2364
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 21.1798
| Antifog | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 21.0695
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 28.3157
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 28.291
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 28.2308
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 28.4899
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 28.4453
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 28.3619
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 28.6423
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 28.5881
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 28.486
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 28.7381
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 28.6784
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 28.5652
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 28.8366
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 28.7714
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 28.6474
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 29.0058
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 28.9315
| Antifog | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 28.7897
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 40.2641
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 38.7212
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 38.6495
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 38.9593
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 38.9052
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 38.8054
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 39.1422
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 39.0763
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 38.9535
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 39.2576
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 39.1848
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 39.0485
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 39.3764
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 39.2968
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 39.1471
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 39.5809
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 39.49
| Antifog | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 39.3183
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 36.8028
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 36.7733
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 36.7006
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 37.0019
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 36.9617
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 36.8611
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 37.1856
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 37.1366
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 37.013
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 37.3017
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 37.2475
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 37.1102
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 37.4215
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 37.3621
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 37.2113
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 37.6281
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 37.5601
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 37.3868
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 51.9562
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 51.9171
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 51.8216
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 52.2192
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 52.1655
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 52.0323
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 52.4632
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 52.3975
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 52.2329
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 52.618
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 52.5451
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 52.3618
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 52.7781
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 52.6981
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 52.4962
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 53.0552
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 52.9632
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 52.7304
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 67.7712
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 67.7244
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 67.6107
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 68.0855
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 68.0209
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 67.8614
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 68.3789
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 68.2994
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 68.1013
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 68.5658
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 68.4774
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 68.2562
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 68.7596
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 68.6622
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 68.418
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 69.096
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 68.9837
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 68.7009
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 21.1755
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 21.1585
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 21.1266
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 21.2594
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 21.2363
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 21.1919
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 21.3367
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 21.3085
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 21.2539
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 21.3854
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 21.3542
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 21.2936
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 21.4356
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 21.4015
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 21.3349
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 21.5218
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 21.4829
| Antifog | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 21.4066
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 28.7184
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 28.6965
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 28.6558
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 28.8258
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 28.7957
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 28.7387
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 28.9253
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 28.8884
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 28.818
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 28.9884
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 28.9475
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 28.869
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 29.0534
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 29.0086
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 28.9222
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 29.1657
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 29.1143
| Antifog | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 29.0148
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 37.0147
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 36.9881
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 36.9392
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 37.1443
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 37.1076
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 37.0387
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 37.265
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 37.2198
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 37.1343
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 37.3416
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 37.2915
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 37.196
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 37.4208
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 37.3658
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 37.2605
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 37.5579
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 37.4946
| Antifog | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 37.3731
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 22.1286
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 22.0997
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 22.0458
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 22.2775
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 22.2383
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 22.1639
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 22.4139
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 22.3663
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 22.2752
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 22.4996
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 22.4472
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 22.3463
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 22.5878
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 22.5305
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 22.4199
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 22.739
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 22.6738
| Antifog | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 22.5474
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 29.7696
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 29.7322
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 29.6638
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 29.9592
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 29.9081
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 29.8129
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 30.134
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 30.0717
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 29.9545
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 30.2444
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 30.1754
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 30.0454
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 30.3581
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 30.2826
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 30.1397
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 30.554
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 30.4677
| Antifog | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 30.3037
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 40.2641
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 40.2188
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 40.1368
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 40.4922
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 40.4299
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 40.3152
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 40.7034
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 40.6271
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 40.4854
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 40.8371
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 40.7526
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 40.5949
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 40.9752
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 40.8825
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 40.7089
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 41.2134
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 41.1072
| Antifog | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 40.9074
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 59.6511
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 59.1047
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 57.7071
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 63.2861
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 62.587
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 60.7901
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 66.5086
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 65.6796
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 63.5436
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 68.5139
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 67.6055
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 65.2629
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 70.5682
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 69.5792
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 67.027
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 74.0943
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 72.9675
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 70.0585
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 79.4513
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 78.7462
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 76.9614
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 84.0844
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 83.1762
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 80.8665
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 88.2153
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 87.1332
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 84.3741
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 90.7955
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 89.6066
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 86.5725
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 93.4455
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 92.1478
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 88.834
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 98.0086
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 96.5244
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 92.7326
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 104.8102
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 103.9387
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 101.745
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 110.4986
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 109.3722
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 106.5239
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 115.5857
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 114.2402
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 110.8292
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 118.7693
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 117.2889
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 113.5327
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 122.0437
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 120.4256
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 116.3176
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 127.6913
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 125.8368
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 121.1265
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 32.5864
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 32.2079
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 31.4564
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 34.4185
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 33.94
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 32.9851
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 36.0247
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 35.4624
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 34.337
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 37.0168
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 36.4039
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 35.1756
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 38.0277
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 37.3637
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 36.0321
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 39.7509
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 39.0006
| Polymer | Plain | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 37.4946
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 42.31
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 41.8342
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 40.9059
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 44.5685
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 43.9636
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 42.7771
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 46.5583
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 45.8445
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 44.4404
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 47.7912
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 47.0114
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 45.4755
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 49.0503
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 48.2037
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 46.5349
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 51.2025
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 50.2427
| Polymer | Plain | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 48.3491
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 53.9712
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 53.407
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 52.3171
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 56.6226
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 55.9022
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 54.5034
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 58.9673
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 58.1147
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 56.4539
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 60.4237
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 59.4905
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 57.6707
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 61.9136
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 60.8988
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 58.9183
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 64.4657
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 63.3122
| Polymer | Plain | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 61.0592
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 61.0429
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 60.4544
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 58.9524
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 64.9751
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 64.2165
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 62.2718
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 68.4832
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 67.5788
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 65.2545
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 70.6756
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 69.6815
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 67.1246
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 72.9285
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 71.8429
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 69.0491
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 76.8102
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 75.5677
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 72.3686
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 81.2469
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 80.4805
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 78.5452
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 86.3054
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 85.3108
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 82.7877
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 90.8454
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 89.6536
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 86.6228
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 93.6936
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 92.38
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 89.0366
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 96.6281
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 95.19
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 91.5274
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 101.7007
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 100.0481
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 95.8376
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Double Circuit | 107.004
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Double Circuit | 106.0522
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Double Circuit | 103.6624
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Double Circuit | 113.2449
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Double Circuit | 112.0053
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Double Circuit | 108.8789
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Double Circuit | 118.8635
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Double Circuit | 117.3742
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Double Circuit | 113.6088
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Double Circuit | 122.3954
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Double Circuit | 120.7516
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Double Circuit | 116.5919
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Double Circuit | 126.0394
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Double Circuit | 124.2373
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Double Circuit | 119.6743
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Double Circuit | 132.3492
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Double Circuit | 130.2739
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Double Circuit | 125.0174
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 33.3952
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 32.9958
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 32.2045
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 35.3359
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 34.8278
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 33.8164
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 37.0466
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 36.4467
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 35.2491
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 38.1071
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 37.4514
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 36.141
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 39.1907
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 38.4786
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 37.0542
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 41.0442
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 40.2362
| Polymer | Hilly | 400 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 38.6187
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 43.2565
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 42.7509
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 41.7667
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 45.6665
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 45.0194
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 43.7535
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 47.8023
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 47.0348
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 45.5292
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 49.1309
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 48.29
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 46.6385
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 50.4917
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 49.5763
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 47.7769
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 52.826
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 51.7836
| Polymer | Hilly | 400 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 49.7332
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | 55.0554
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | 54.4524
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | 53.2906
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | 57.9013
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | 57.126
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | 55.6249
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | 60.4335
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | 59.511
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | 57.7195
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | 62.0129
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | 61.0003
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | 59.0314
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | 63.6333
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | 62.5291
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | 60.3803
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | 66.4194
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | 65.1585
| Polymer | Hilly | 400 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | 62.7032
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Moose | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 62.4603
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 61.8547
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 60.3101
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 66.4859
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 65.7071
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 63.713
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 70.0725
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 69.1446
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 66.764
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 72.3126
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 71.2931
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 68.6752
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 74.6139
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 73.5008
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 70.6413
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 78.5775
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 77.3039
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 74.0309
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 82.9238
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 82.1705
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 80.2667
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 87.863
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 86.8913
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 84.4252
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 92.2746
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 91.1147
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 88.1643
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 95.0341
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 93.7583
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 90.5105
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 97.8713
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 96.4773
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 92.9264
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 102.7631
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 101.1661
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 97.0964
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 109.392
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 108.4596
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 106.1155
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 115.4695
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 114.2624
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 111.2157
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 120.9146
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 119.47
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 115.8154
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 124.3275
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 122.7362
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 118.7073
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 127.8416
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 126.1004
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 121.6895
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 133.911
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 131.912
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 126.8458
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 33.7651
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 33.364
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 32.5702
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 35.6965
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 35.1891
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 34.1805
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 37.3914
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 36.7944
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 35.6048
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 38.4392
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 37.7879
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 36.4888
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 39.5077
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 38.8016
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 37.3921
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 41.3308
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 40.5319
| Polymer | Plain | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 38.9361
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 44.0332
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 43.5273
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 42.5428
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 46.4249
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 45.7813
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 44.5231
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 48.5346
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 47.7742
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 46.2837
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 49.8432
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 49.0117
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 47.3801
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 51.1807
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 50.2772
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 48.5031
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 53.4693
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 52.4436
| Polymer | Plain | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 50.4279
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 56.2304
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 55.6295
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 54.4709
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 59.0461
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 58.2782
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 56.7911
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 61.5394
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 60.6291
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 58.8617
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 63.0898
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 62.0927
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 60.1544
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 64.6774
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 63.5921
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 61.4808
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 67.3998
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 66.1644
| Polymer | Plain | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 63.7593
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Plain | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 63.7034
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 63.062
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 61.4292
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 67.9808
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 67.1512
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 65.0314
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 71.8102
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 70.8177
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 68.2765
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 74.2097
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 73.1167
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 70.3158
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 76.6802
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 75.4843
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 72.4182
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 80.947
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 79.5741
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 76.053
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 84.7723
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 83.9527
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 81.8861
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 90.1721
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 89.1065
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 86.4091
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 95.028
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 93.7485
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 90.5027
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 98.0792
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 96.6673
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 93.0826
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 101.2264
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 99.6788
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 95.7476
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 106.6742
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 104.8928
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 100.3656
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Double Circuit | 111.6565
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Double Circuit | 110.6369
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Double Circuit | 108.0804
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Double Circuit | 118.3333
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Double Circuit | 117.003
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Double Circuit | 113.6542
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Double Circuit | 124.3569
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Double Circuit | 122.7553
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Double Circuit | 118.7147
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Double Circuit | 128.1496
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Double Circuit | 126.3796
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Double Circuit | 121.9106
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Double Circuit | 132.0674
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Double Circuit | 130.1246
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Double Circuit | 125.2167
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Double Circuit | 138.861
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Double Circuit | 136.6198
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Double Circuit | 130.9558
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 34.5852
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 34.1616
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 33.3252
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 36.633
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 36.0936
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 35.0244
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 38.4402
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 37.8025
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 36.5353
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 39.5617
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 38.8641
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 37.4765
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 40.7086
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 39.9503
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 38.4408
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 42.6723
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 41.8107
| Polymer | Hilly | 400 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 40.0944
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 44.9966
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 44.4585
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 43.414
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 47.5516
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 46.8623
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 45.5185
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 49.819
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 49.0003
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 47.4001
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 51.2312
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 50.3333
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 48.5766
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 52.6788
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 51.7004
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 49.7848
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 55.1651
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 54.0493
| Polymer | Hilly | 400 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 51.8633
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | 57.3373
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | 56.6943
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | 55.4582
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | 60.3631
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | 59.5356
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | 57.9378
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | 63.0594
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | 62.0732
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | 60.164
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | 64.7433
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | 63.6597
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | 61.5597
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | 66.4728
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | 65.2899
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | 62.9958
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | 69.45
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | 68.0972
| Polymer | Hilly | 400 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | 65.4719
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Twin Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Triple Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-1 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-2 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-3 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-4 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-5 | Terrian Category-3 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-1 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-2 | Single Circuit | NA
| Polymer | Hilly | 765 kV | ACSR Quad Bersimis | Wind Zone-6 | Terrian Category-3 | Single Circuit | NA

## Actual Cost
CERC
Capital Cost Benchmarking
Project Cost (Actual- Excluding Taxes and Duties)
| Particulars | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
| Name of the Line | Pichore-Gwalior | Bina-Pichore | Sasaram-Fatepur | Balia-Luknow | Raigarh-Raipur | Muvattupuzha-North | Ranchi-1-Sipat | Gaya-Balia | BINA-GWALIOR | DURGAPUR-MAITHON | Kanpur-Ballabhgrh | Vapi-Navi Mumbai | Edamon-Muvattupuzha(Part-I) | Kaithal-Meerut | Ranchi-Rourkela | Maithon RB TPS -Ranchi | Mejia 'B' TPS-Maithon(PG) | Rourkela-Raigrah | Sasaram-Biharsharif | Ranchi(old)-Ranchi(new)(Line-1) | Ranchi(old)-Ranchi(new)(Line-2) | Maithon RB TPS- Maithon (PG) | Maithon -Jamshedpur(LILO atMejia 'B' TPS) | Edamon- Muvattupuzha(Part II) | Bokaro TPS-Kodarma TPS | Kodarma-Gaya | Pindwara-Kankroli | Madurai-Trivandrum | Bareili-Moradabad and other lines | Agra-Jaipur (Package-A2) | Malerkotla-Jallandhar etc. | Jodhpur-Merta | PPSP-DURGPUR | Thamnar-Raipur(Kumhari) | Nandikur-Hassan | BTPS-HIRIYUR | Bhoopalapally TPP to Warangal
| Voltage class | 765 kV | 765 kV | 765 kV | 765 kV | 400 kV | 400 kV | 765kV | 765kV | 765kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV
| DC or SC | SC | SC | SC | SC | DC | DC | S/C | S/C | S/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | S/C | S/C | D/C | D/C | D/C | D/C | D/C
| Type of Conductor | ACSR Bersimis | ACSR Bersimis | ACSR Bersimis | ACSR Bersimis | ACSR Moose | ACSR, MOOSE | ACSR Bersimis | ACSR Bersimis | ACSR Bersimis | ACSR LAPWING | ACSR Moose | ACSR Moose | ACSR Moose |  | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose
| No. of Conductors in the bundle | Quad | Quad | Quad | Quad | Twin | Quad | Quad | Quad | Quad | TWIN | Twin | Twin | Quad | Quad Bundle | Twin | Twin | Twin | Twin | Quad | Quad | Quad | TWIN | TWIN | Quad | TWIN | Quad | Twin | Twin | Twin | Twin | Twin | Twin | Twin | Twin | Quad | Twin | Twin
| Wind Zone | 1: 4; 2: 4; 3: 4; 4: 4; 5: 2; 35: 2; 36: 2; 37: 3
| Route length | 117.5 | 122.5 | 168 | 158 | 214 | 77.29 | 292 | 235 | 122.5 | 73 | 132 | 185 | 73.64 | 160 | 143 | 200 | 57 | 210 | 195 | 72 | 72 | 30 | 50 | 8 | 110 | 80 | 114 | 106 | 165 | 110 | 118 | 110 | 185 | 204 | 179 | 151 | 44
| Month and Year of Commissioning | 2007-01-01 | 2007-01-01 | 2008-03-01 | 2007-12-07 | 2007-01-01 | 2007-11-01 | 2008-02-01 | 2007-12-01 | 2007-01-01 | 2007-06-11 | 2007-07-11 | 2007-06-11 | 2007-11-11 | 2007-07-11 | 2007-01-01 | 2007-02-11 | 2008-02-11 | 2007-01-07 | 2008-02-08 | 2008-01-01 | 2008-01-01 | 2008-02-01 | 2008-02-01 | 2007-11-07 | 2008-02-08 | 2008-02-08 | 2006-10-06 | 2005-03-05 | 2004-05-01 | 2004-01-01 | 2004-07-01 | 2008-02-01 | 2007-01-01 | 2005-09-01 | 2008-09-01 | 2008-02-01 | 2008-11-01
I | SUPPLY | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate
1 | a) HT Tower parts | 48901 | 43570 | 58261.8 | 46240 | 51999 | 55266 | 52572 | 50014 | 43570 | 54880 | 45045 | 44178 | 49132 | 44798 | 56981 | 54000 | 54000 | 55929 | 64636 | 61996 | 61996 | 48940 | 48940 | 49130 | 51300 | 51300 | 49021 | 67694 | 54386 | 42400 | 39599.81 | 0 | 0 | 49625 | 69878 | 59318 | 0
| b) MS Tower parts | 45293 | 39981 | 53353.8499 | 41702 | 49000 | 49899 | 49135 | 41783 | 39981 | 50862 | 42075 | 42486 | 44245 | 42075 | 52959 | 50000 | 50000 | 52262 | 57037 | 54326 | 54326 | 44571 | 44571 | 44242 | 47500 | 47500 | 46306 | 61415 | 48269 | 40000 | 46291.4 | 63430 | 473097524 | 45198 | 60773 | 55464 | 75854
| c) Stubs-HT | 48901 | 43570 | 58261.797 | 46240 | 51999 | 55266 | 52572 | 50014 | 43570 | 54880 | 45045 | 44178 | 49136 | 8910 | 56981 | 54000 | 54000 | 55929 | 64636 | 61996 | 61996 | 48940 | 48940 | 49131 | 51300 | 51300 | 49021 | 67694 | 54386 | 42400 | 39599.81 | 0 | 0 | 49625 | 0 | 0 | 0
| d) Stubs-MS | 45295 | 39983 | 53353.85 | 41702 | 49000 | 49899 | 49135 | 41783 | 39983 | 50862 | 42075 | 42486 | 44249 | 8910 | 52959 | 50000 | 50000 | 52262 | 57037 | 54326 | 54326 | 44571 | 44571 | 44250 | 47500 | 47500 | 46306 | 61415 | 48269 | 40000 | 46291.4 | 0 | 0 | 45198 | 0 | 0 | 0
2 | Bolts and Nuts
| a) Hex. Bolts and Nuts | 75867 | 58858 | 91378 | 74585 | 62350 | 68511 | 88191 | 73818 | 58859 | 74480 | 79200 | 67455 | 58554 | 79200 | 77211 | 77686 | 77686 | 66906 | 88381 | 87786 | 87786 | 84676 | 84676 | 58554 | 73802 | 73802 | 72463 | 103012 | 67571 | 60000 | 100266.4 | 102244 | 1838902 | 64318 | 74905 | 0 | 0
| b) Anti theft Bolts and Nuts | 132548 | 85154 | 187420 | 137788 | 105248 | 114185 | 188961 | 132873 | 85154 | 122500 | 128700 | 103678 | 108257 | 128700 | 132542 | 155373 | 155373 | 126259 | 166621 | 160941 | 160941 | 156028 | 156028 | 108257 | 147604 | 147604 | 202831 | 245268 | 134743 | 90000 | 100266.4 | 0 | 0 | 137822 | 0 | 79625 | 0
3 | a) Earthing Pipe type | 2479 | 1845 | 1782 | 1793 | 1319 | 1713 | 2945 | 1544 | 1845 | 1470 | 1485 | 1794 | 1624 | 1485 | 2477 | 1549 | 1549 | 1864 | 1697 | 2107 | 2107 | 2043 | 2043 | 1624 | 1472 | 1472 | 2372 | 1763 | 2304 | 1500 | 2418 | 2989 | 0 | 5743 | 1728 | 2266 | 3145
| b) Earthing Counterpoise | 6065 | 6365 |  |  | 4344 | 5709 | 6639 |  | 6365 |  |  | 7537 | 4868 | 69299 | 5995 | 7000 | 7000 | 6500 | 145 | 6500 | 6500 | 6500 | 6500 | 4868 |  | 6542 | 5993 | 6818 | 0 | 3500 | 0 | 7526 | 0 | 6890 | 3024 | 6646 | 250
| c) River Crossing locations (MT) | 19: 71897; 22: 67499
4 | Tower Accessories
| a) Danger Plate | 280 | 212 | 283 | 291 | 113 | 171 | 211 | 144 | 212 | 147 | 149 | 149 | 217 | 147 | 279 | 132 | 132 | 144 | 178 | 157 | 157 | 330 | 330 | 217 | 125 | 125 | 265 | 142 | 308 | 150 | 167.5 | 201 | 0 | 172 | 130 | 308 | 332
| b) Number Plate | 280 | 212 | 283 | 291 | 113 | 171 | 211 | 144 | 212 | 147 | 149 | 149 | 217 | 147 | 279 | 126 | 126 | 144 | 178 | 157 | 157 | 330 | 330 | 217 | 120 | 120 | 265 | 142 | 308 | 150 | 167.5 | 201 | 0 | 172 | 0 | 308 | 332
| d) Circuit plates |  |  |  |  | 0 | 0 | 0 | 144 | 0 | 147 | 0 | 149 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 308 | 150 | 66 | 0 | 0 | 345 | 86 | 308 | 332
| c) Phase Plate (Set of three) | 280 | 530 | 283 | 291 | 107 | 171 | 58 | 144 | 530 | 147 | 149 | 149 | 217 | 147 | 279 | 131 | 131 | 144 | 178 | 157 | 157 | 330 | 330 | 217 | 124 | 124 | 265 | 142 | 308 | 150 | 167.5 | 201 | 0 | 345 | 207 | 599 | 332
| e) Anti climbing device | 6375 | 5304 | 6059 | 6223 | 5214 | 3426 | 7087 | 5839 | 606 | 2940 | 3465 | 5503 | 5411 | 3465 | 6372 | 6552 | 6552 | 4388 | 7215 | 6224 | 6224 | 7057 | 7057 | 5411 | 6224 | 6224 | 6556 | 6622 | 4712 | 3000 | 7576.4 | 58832.0179 | 0 | 5743 | 2851 | 7391461 | 6000
| f) Bird guard | 928 | 606 | [7 empty] | 147 |  |  |  | 149 |  | 207 | 207 |  | 2659 | 2261 | 2261 | 1257 | 1257 |  | 197 | 197 | 795 | 0 | 232 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0
5 | ACSR Moose Conductor | 1: 236649.1605
| ACSR Bersimis Conductor | 1: 254654.5772
6 | GSS Ground wire | 38453 | 29553 | 46154 | 38040 | 25417 | 31990 | 51970 | 37950 | 29553 | 44090 | 44382 | 35566 | 31453 | 43799 | 38259 | 40762 | 40762 | 35047 | 49837 | 46219 | 46219 | 49305 | 49305 | 31543 | 38724 | 38724 | 39643 | 43069 | 45664 | 29500 | 41575.09 | 54550 | 25464 | 34369 | 35856 | 42603 | 53465
7 | Hardware fittings | 20: 46219; 21: 46219
| a) Single 'V' suspension | 1: 33277; 2: 27280; 3: 22400; 4: 18738; 7: 25375; 8: 20038; 9: 27280; 28: 0; 29: 0; 30: 0; 31: 0; 32: 17185; 33: 10181; 34: 0; 35: 12854; 36: 0; 37: 0
| b) Double 'V' Suspension | 1: 64302; 2: 50822; 3: 44074; 4: 38279; 7: 51037; 8: 40936; 9: 50822; 28: 0; 29: 27256; 30: 0; 31: 0; 32: 27696; 33: 0; 34: 0; 35: 0; 36: 0; 37: 0
| c) Single 'I' Pilot | 39031 | 30917 | 28264 | 33941 | 4129 | 28589 | 33708 | 36298 |  | 8265 | 5863 | 4606 | 26285 |  | 6577 | 4816 |  | 6348 | 32599 | 24316 | 24316 |  |  | 26285 | 4575 | 24841 | 6287 | 6205 | 5188 | 4200 | 6464.12 | 7534 | 4330 | 6150 | 0 | 23220 | 6356
| d) Single 'V' Pilot | 1: 17103; 2: 14397; 3: 14691; 4: 13379; 7: 14739; 8: 14307; 9: 14397; 28: 0; 29: 0; 30: 0; 31: 0; 32: 0; 33: 0; 34: 0; 35: 0; 36: 0; 37: 0
| e) Double 'I' suspension | 28892 | 24249 | 20815 | 19076 |  | 15207 | 23995 | 20401 | 24249 |  |  |  | 13982 | [5 empty] | 21589 | 20666 | 20666 |  |  | 13982 |  | 15890 |  | 0 | 0 | 0 | 0 | 15476 | 0 | 12903 | 0 | 48398 | 0
| f) Quad Tension string | 81280 | 67391 | 53926 | 53214 |  | 33256 | 61806 | 56907 | 67391 |  |  |  | 30577 | [5 empty] | 44379 | 41609 | 41609 |  |  | 30577 |  | 33114 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26666 | 0 | 0
| Standard Insulators 120 kN | 1: 647
| Standard Insulators 160 kN | 1: 776
| Standard Insulators 210 kN | 1: 850
| Antifog Insulator 120 kN | 1: 997
| Antifog Insulator 160 kN | 1: 1126
| Antifog Insulator 210 kN | 1: 1350
| Polymer Insulator - 120 kN String | 1: 21149
| Polymer Insulator - 160 kN String | 1: 23498
| g) Single 'I' suspension |  |  |  |  | 7532 |  |  | 0 | 30917 | 13732 | 8733 | 7783 |  |  | 9786 | 6862 | 6862 | 8887 |  |  |  | 7882 | 7882 |  | 6519 | 0 | 9245 | 9762 | 7750 | 6400 | 10045.98 | 10708 | 0 | 9045 | 0 | 26954 | 10145
| h) Single tension string | 11: 9790; 12: 7549; 15: 10974; 16: 8662; 18: 9946; 19: 19575; 28: 0; 29: 0; 30: 6500; 31: 0; 32: 12433; 33: 6992; 34: 0; 35: 0; 36: 0; 37: 0
| I) Double tension string | 5: 11360; 10: 24029; 11: 14793; 12: 13903; 15: 16578; 16: 12534; 17: 12534; 18: 15342; 22: 14154; 23: 14154; 25: 11907; 27: 16144; 28: 15599; 29: 12764; 30: 9350; 31: 15675.09; 32: 20375; 33: 10249; 34: 15194; 35: 0; 36: 59553; 37: 19435
8 | Conductor and GW Accessories
| a) MSC joints for conductors | 1667 | 1394 | 1467 | 1117 | 773 | 724 | 1373 | 1194 | 1394 | 2025 | 1062 | 921 | 666 |  | 1190 | 881 | 881 | 1111 | 1058 | 880 | 880 | 960 | 960 | 666 | 837 | 840 | 1110 | 0 | 0 | 670 | 0 | 1270 | 775 | 1110 | 688 | 952 | 1120
| b) MSC joints for GW | 371 | 303 | 325 | 219 | 253 | 182 | 223 | 235 | 303 | 365 | 301 | 246 | 168 |  | 338 | 233 | 233 | 317 | 275 | 242 | 242 | 221 | 221 | 168 | 221 | 221 | 394 | 289 | 242 | 220 | 209.56 | 343 | 166 | 319 | 181 | 297 | 370
| c) Flexible copper earth bonds | 524 | 455 | 455 | 509 | 257 | 354 | 568 | 545 | 455 | 497 | 434 | 401 | 325 |  | 462 | 518 | 518 | 476 | 608 | 361 | 361 | 562 | 562 | 325 | 492 | 492 | 474 | 329 | 286 | 290 | 369.56 | 0 | 214 | 445 | 0 | 0 | 561
| d) Vibration dampers for GW | 433 | 354 | 399 | 344 | 306 | 314 | 321 | 369 | 354 | 440 | 353 | 322 | 288 |  | 409 | 297 | 297 | 383 | 363 | 302 | 302 | 320 | 320 | 288 | 282 | 282 | 401 | 392 | 318 | 250 | 375.6 | 458 | 240 | 386 | 317 | 409 | 498
| e) Quad spacer damper for conductor | 2784 | 2273 | 2279 | 1933 |  | 1825 | 2301 | 2067 | 2273 |  |  |  | 1678 | [5 empty] | 2274 | 1828 | 1828 |  |  | 1678 |  | 1725 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1342 | 913 | 0
| f) Quad rigid spacer for conductor | 1269 | 1062 | 1011 | 897 |  | 816 | 1109 |  | 1062 |  |  |  | 751 | [5 empty] | 1086 | 944 | 944 |  |  | 751 |  | 818 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 678 | 488 | 0
| g) Vibration damper for conductor |  |  |  |  | 618 |  |  |  |  | 973 | 798 | 748 |  |  | 894 | 764 | 764 | 820 |  |  |  | 823 | 823 |  | 726 | 0 | 839 | 839 | 749 | 550 | 870.48 | 1107 | 496 | 821 | 619 | 917 | 992
| h) Rigid spacer for jumpers |  |  |  |  | 411 |  |  | 960 |  | 559 | 450 | 347 |  |  | 506 | 336 | 336 | 466 |  |  |  | 345 | 345 |  | 319 | 0 | 493 | 392 | 354 | 550 | 457.81 | 473 | 293 | 0 | 0 | 0 | 600
| i) Earthwire suspension clamps | 822 | 658 | 674 | 500 | 360 | 405 | 716 | 564 | 658 | 835 | 694 | 491 | 372 | 278 | 776 | 647 | 647 | 720 | 768 | 638 | 638 | 711 | 711 | 372 | 615 | 614.27 | 764 | 839 | 613 | 450 | 793.1 | 1661 | 465 | 723 | 426 | 613 | 658
| j) Earthwire tension clamps | 836 | 658 | 673 | 527 | 485 | 490 | 779 | 537 | 658 | 829 | 724 | 597 | 451 | 636 | 771 | 751 | 751 | 719 | 899 | 663 | 663 | 775 | 775 | 451 | 713 | 712 | 740 | 804 | 617 | 420 | 794.72 | 1775 | 485 | 700 | 467 | 584 | 666
| i) Repair sleeve for conductor |  |  | 918 | 591 |  | 262 | 799 | 632 |  | 1086 | 610 | 322 | 241 |  | 762 | 324 | 324 | 423 | 377 | 338 | 338 | 353 | 353 | 241 | 308 | 309 |  | 0 | 0 | 490 | 0 | 473 | 297 | 445 | 226 | 403 | 475
| j) T-Connector for ACSR Moose Conductor. | 11: 1549; 12: 1047; 15: 1651; 16: 1320; 17: 1320; 18: 1335; 19: 1580; 28: 0; 29: 0; 30: 1100; 31: 0; 32: 0; 33: 1095; 34: 0; 35: 0; 36: 0; 37: 0
| k) Bundle spacer for line | 5: 592; 10: 1124; 11: 914; 12: 725; 15: 1025; 16: 802; 17: 802; 18: 937; 22: 823; 23: 823; 25: 762; 27: 1011; 28: 981; 29: 854; 30: 600; 31: 1030.07; 32: 1091; 33: 761; 34: 939; 35: 0; 36: 0; 37: 980
| l) Repair Sleeves for Ground wire | 28: 0; 29: 0; 30: 0; 31: 0; 32: 98; 33: 0; 34: 0; 35: 181; 36: 0; 37: 0
9 | Aviation Requirements | 10: 245023; 11: 98997.5; 12: 149418.33; 13: 130371; 15: 153064
| a) Span markers | 3: 5471; 14: 5939; 17: 5827; 19: 6521; 20: 109733; 21: 109733; 28: 0; 29: 7003; 30: 0; 31: 8775.73; 32: 0; 33: 0; 34: 0; 35: 0; 36: 0; 37: 0
| b) Obstruction lights | 3: 315568; 4: 578629; 8: 369091; 17: 22000; 19: 400000; 20: 400000; 21: 400000; 28: 0; 29: 0; 30: 0; 31: 828785.62; 32: 7657; 33: 0; 34: 0; 35: 0; 36: 0; 37: 0
| c) Wind measuring equipments |  |  | 134510 | 138179 | 87337 | 100000 | 98373 | 100662 |  | 245023 |  |  |  | 98999 |  | 178032 | 178032 | 74538 | 108666 | 131679 | 131679 | 156639 | 156639 | 130363 | 169130 | 169130 | 257128 | 245266 | 300947 | 525000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
II | ERECTION
1 | Detailed survey | 10156 | 9000 | 13370 | 7077 | 18860 | 10002 | 9640 | 15102 | 9000 |  | 5750 | 6969 | 14035 | 5940 | 8474 | 20621 | 20621 | 8996 | 9875 | 9750 | 9750 | 12641 | 12641 | 14996 | 20131 | 20131 | 16806 | 6215 | 9644 | 10418 | 13000 | 20000 | 20000 | 7554 | 0 | 0 | 12595
2 | Check survey | 9148 | 5328 | 11494 | 5784 | 6287 | 7500 | 6136 | 10068 | 5328 | 7840 | 3287 | 4045 | 13319 | 2970 | 8593 | 8887 | 8887 | 3299 | 7900 | 7313 | 7313 | 10112 | 10112 | 14161 | 9395 | 9395 | 14161 | 2855 | 9173 | 6449 | 0 | 0 | 15000 | 4969 | 4919 | 26398 | 2820
3 | Soil Investigation
| a) All kinds except FR and HR | 7687 | 8115 | 6929 | 5790 | 12575 |  | 8986 | 6545 | 8115 | 9800 | 3287 | 7730 |  | 3960 | 11881 | 7072 | 7072 | 10496 | 8986 | 6338 | 6338 | 8427 | 8427 |  | 6718 | 6718 | 10581 | 0 | 14042 | 17662.36 | 6500 | 0 | 6000 | 3559 | 0 | 0 | 0
| b) Fissured rock | 22422 | 19974 |  |  | 23575 |  | 11232 | 6545 | 19974 | 11760 |  | 19027 |  |  | 47522 | 17679 | 17679 | 11995 | 8986 | 6338 | 6338 | 25281 | 25281 |  | 16795 | 16795 | 26452 | 0 | 0 | 0 | 0 | 0 | 0 | 3559 | 0 | 0 | 0
| c) Hard rock | 22422 | 31211 |  |  |  |  | 12730 | 50339 | 31211 | 17640 | [5 empty] | 29465 |  |  | 8986 | 7800 | 7800 | 101125 |  |  | 27992 | 27992 | 26452 | 0 | 0 | 0 | 0 | 0 | 0 | 3561 | 0 | 0 | 0
| d) River Crossing locations | 19: 24688; 22: 101125; 28: 0; 29: 70212; 30: 0; 31: 13000; 32: 0; 33: 0; 34: 0; 35: 0; 36: 0; 37: 0
4 | Benching
| a) All kinds except FR and HR | 96 | 100 | 111 |  | 79 | 164 | 177 | 75 |  | 59 | 25 | 128 | 72 | 30 | 90 | 95 |  | 120 | 74 | 78 | 78 |  |  | 72 | 71 | 71 | 93 | 0 | 0 | 139 | 195 | 110 | 0 | 465 | 94 | 145 | 84
| b) Fissured rock | 256 | 312 |  |  |  | 219 | 421 |  | 100 | 196 |  | 192 | 165 |  | 268 | 245 |  | 135 |  | 293 | 293 |  |  | 167 | 233 | 233 | 430 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 269 | 483 | 0
| c) Hard rock | 447 | 499 |  |  |  | 383 | 964 |  | 312 | 490 |  |  | 550 |  | 416 | 701 |  | 600 |  | 341 | 341 |  |  | 556 | 588 | 588 | 794 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 4000 | 0 | 0
5 | Excavation | 9: 499
| a) Dry soil | 104 | 155 | 108 | 102 | 117 | 164 | 177 | 101 | 155 | 59 | 103 | 102 | 129 | 99 | 101 | 98 | 98 | 120 | 99 | 107 | 107 | 152 | 152 | 137 | 98 | 98 | 159 | 118 | 132 | 184 | 195 | 150 | 250 | 145 | 1500 | 155 | 182
| b) Wet soil | 115 | 155 | 111 | 106 | 157 | 192 | 195 | 101 | 155 | 59 | 103 | 127 | 142 | 99 | 113 | 121 | 121 | 135 | 148 | 107 | 107 | 169 | 169 | 151 | 120 | 120 | 185 | 137 | 158 | 184 | 286 | 150 | 250 | 198 | 3000 | 180 | 11.15
| c) Dry Fissured Rock | 352 | 321 |  |  | 551 | 438 | 421 | 327 | 321 | 225 |  | 169 | 450 |  | 345 | 295 | 295 | 412 | 395 | 390 | 390 | 463 | 463 | 481 | 296 | 296 | 628 | 319 | 0 | 546 | 0 | 600 | 400 | 492 | 3000 | 677 | 274
| d) Wet Fissured Rock | 352 | 321 |  |  | 589 | 438 | 473 |  | 321 | 245 |  | 169 |  |  | 356 | 326 | 326 | 427 |  | 390 | 390 |  | 480 |  | 344 | 344 | 694 | 0 | 0 | 0 | 0 | 0 | 400 | 538 | 150 | 958 | 100
| e) Hard Rock | 577 | 1248 |  |  | 942 | 548 | 964 |  | 1248 | 588 |  |  | 836 |  | 891 | 1002 | 1002 |  |  | 878 | 878 |  | 758 |  | 840 | 840 | 1124 | 0 | 0 | 0 | 0 | 700 | 800 | 1133 | 0 | 1354 | 595
6 | 1:1½:3 Concreting | 5321 | 5795 | 5451 | 5183 | 5098 | 4782 | 6010 | 5334 | 5795 | 3527 | 3942 | 4615 | 6903 | 4010 | 5569 | 5822 | 5822 | 5542 | 5431 | 5363 | 5363 | 6686 | 6686 | 7399 | 5691 | 5691 | 5983 | 5420 | 6619 | 5705 | 4160 | 5300 | 214693084 | 5197 | 6691 | 8513 | 6611
7 | 1:3:6 Concreting | 4112 | 4777 | 4430 | 4281 | 3901 | 3655 | 4097 | 4330 | 4777 | 2547 | 3121 | 3715 | 5529 | 3069 | 4382 | 4848 | 4848 | 3552 | 4444 | 4388 | 4388 | 5285 | 5285 | 5917 | 5001 | 5001 | 4665 | 4542 | 5290 | 5061 | 3705 | 4300 | 7000 | 4165 | 5268 | 6520 | 4146
8 | Reinforcements | 42344 | 47307 | 70288 | 49856 | 54742 | 39537 | 75378 | 41784 | 47307 | 33075 | 39442 | 38358 | 50631 | 36828 | 37885 | 56370 | 56370 | 49128 | 59250 | 48750 | 48750 | 69144 | 69144 | 54078 | 54210 | 54210 | 44748 | 37281 | 58178 | 33239 | 40300 | 0 | 35000 | 37254 | 0 | 63672 | 75486
9 | Installation of stubs | 5125 | 23344 | 4156 | 2895 | 9429 | 2200 | 2180 | 2679 | 23344 | 2744 | 286 | 3208 | 5146 | 2475 | 3640 | 5897 | 5897 | 3449 | 19750 | 19500 | 2992 | 5899 | 5899 | 5497 | 7251 | 7251 | 6613 | 3360 | 8777 | 9922 | 1950 | 2500 | 8000 | 27788 | 49000 | 0 | 11010
10 | Erection of towers | 3028 | 4546 | 3226 | 3079 | 3380 | 2849 | 2180 | 2679 | 4586 | 1960 | 2136 | 2364 | 4703 | 2266 | 3110 | 2826 | 2826 | 3370 | 5235 | 4875 | 2890 | 3829 | 3829 | 5033 | 2800 | 2801 | 3502 | 3188 | 4100 | 3671 | 3120 | 2320.7839 | 73850027 | 3205 | 3981 | 5353.93 | 5880
11 | Installation of earthing of towers
| a) Earthing Pipe type | 1794 | 1499 | 1524 | 1158 | 2200 | 1500 | 101 | 3121 | 1499 | 1078 | 1233 | 1428 | 2573 | 1485 | 1188 | 2133 | 2133 | 1725 | 4938 | 1950 | 1950 | 2022 | 2022 | 2749 | 2163 | 2163 | 2645 | 1678 | 2106 | 2778 | 6500 | 2000 | 1636000 | 1333 | 1840 | 3481 | 3050
| b) Earthing River Crossing Tower | 8: 3121; 14: 39600; 17: 23572; 19: 71897; 22: 25281; 25: 3359; 28: 0; 29: 43883; 30: 4465; 31: 19500; 32: 0; 33: 0; 34: 0; 35: 0; 36: 0; 37: 0
| c) Earthing Counterpoise | 3075 | 2748 |  |  | 3458 | 8000 | 5000 | 4000 | 2748 | 5000 |  | 2617 | 4504 | 14856 | 2500 | 3600 | 4000 | 4500 | 5500 | 3500 | 3500 | 4000 | 3500 | 4810 |  | 3359 | 4960 | 3360 | 0 | 0 | 0 | 6000 | 0 | 2664 | 2451 | 4641 | 2630
12 | Installation of tower accessories | 28: 0; 29: 0; 30: 0; 31: 0; 32: 0; 33: 313800; 34: 0; 35: 0; 36: 0; 37: 0
13 | River Crossing Location -Pile Foundation | 17: 200363; 22: 0; 23: 101125; 28: 0; 29: 0; 30: 0; 31: 0; 32: 0; 33: 24852000; 34: 0; 35: 0; 36: 0; 37: 0
14 | Protection to tower footing
| a) Random rubble masonry | 2745 | 3745 | 2682 | 3163 | 2046 | 2302 | 2630 | 1510 | 3745 | 1323 | 1479 | 1189 | 1955 | 1485 | 2522 | 3378 | 3378 | 2546 | 1481 | 2438 | 2438 | 2951 | 2951 | 1974 | 2967 | 2967 | 2554 | 2561 | 2763 | 3175 | 1820 | 2500 | 4500 | 3997 | 5300 | 4259 | 2895
| b) Stone bound wire netting | 2692.6667 | 3759.3333 | 2771 | 1801 | 3458 | 6795 | 2630 | 1510 | 3746 | 1176 | 904 | 1189 | 1680 | 990 |  |  | 2947 | 2249 |  | 2438 | 2438 |  |  | 155 |  |  | 2554 | 0 | 2633 | 0 | 2600 | 0 | 0 | 0 | 0 | 0 | 142
| c) Back filling | 89 | 80 | 131 | 90 | 110 | 164 | 421 | 92 | 80 |  | 49 | 53 | 75 | 50 | 83 |  |  | 150 | 74 | 122 | 122 | 118 | 118 | 78 | 71 | 71 | 99 | 118 | 105 | 141 | 117 | 110 | 200 | 0 | 0 | 0 | 350
| d) M15 concrete for top seal cover of revetments | 4292 | 4970 | 4860 | 3435 | 4500 | 4159 | 5008 | 4833 | 4970 | 3136 | 3451 | 2926 | 7150 | 1485 | 4971 | 4415 | 4415 | 3923 | 4938 | 4875 | 4875 | 5208 | 5208 | 7222 | 4213 | 4213 | 4260 | 0 | 4720 | 0 | 3640 | 0 | 0 | 0 | 0 | 0 | 0
15 | Installation of Insulators and stringing | 159996 | 141922 | 214959 | 158952 | 125735 | 353285 | 246250 | 100683 | 141922 | 107800 | 115038 | 97480 | 348646 | 170000 | 110552 | 129647 | 129647 | 202420 |  | 194025 | 194025 | 172885 | 172885 | 413306 | 128763 | 170191 | 344922 | 176593 | 0 | 182565 | 97500 | 165000 | 43008075 | 190480 | 159944 | 208544 | 245455
| Stringing across river crossing | 8: 201365; 19: 250000
16 | Aviation requirement | 10: 9791; 13: 102934; 14: 2475; 24: 109943; 28: 0; 29: 0; 30: 0; 31: 4550; 32: 0; 33: 0; 34: 0; 35: 0; 36: 0; 37: 0
| a) Painting of towers (MT) etc. | 1: 9609; 3: 6235; 4: 7720; 7: 7187; 8: 3524; 11: 2054; 17: 4950; 19: 4838; 20: 4875; 21: 4875
17 | Transportation | 28: 0; 29: 0; 30: 0; 31: 0; 32: 0; 33: 0; 34: 0; 35: 0; 36: 0; 37: 0
18 | Aviation requirment materials | [5 empty] | 20000 |  | 10068 |  | 9791 | 4094 | 5947 |  |  | 71288 | 5893 |  | 59976 |  |  |  | 50562 | 50562 |  | 5598 | 5598 | 79355 | 13428 | 0 | 0 | 11700 | 25000 | 0 | 0 | 0 | 0 | 0
| a) Painting of towers (MT) etc. | 1: 9609; 2: 0; 3: 6235; 4: 7720; 5: 0; 6: 0; 7: 7187; 8: 3524; 9: 0; 10: 0; 11: 2054; 12: 0; 13: 0

## Indices & PV
CERC
Capital Cost Benchmarking
Data for Indices
| Month/Year | Notations | Units | [123 empty] | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | time axis 2004-01-01 to 2014-03-01
Item
| Structural Steel Heavy Angles | S1/So | Rs./MT | 2004-01-01: 24208; 2004-02-01: 24208; 2004-03-01: 24208; 2004-04-01: 29323; 2004-05-01: 29323; 2004-06-01: 29323; 2004-07-01: 31615; 2004-08-01: 31615; 2004-09-01: 31871; 2004-10-01: 31871; 2004-11-01: 31871; 2004-12-01: 31871; 2005-01-01: 30113; 2005-02-01: 30113; 2005-03-01: 30113; 2005-04-01: 30113; 2005-05-01: 30113; 2005-06-01: 30161; 2005-07-01: 30161; 2005-08-01: 30161; 2005-09-01: 30161; 2005-10-01: 30161; 2005-11-01: 30161; 2005-12-01: 30161; 2006-01-01: 30161; 2006-02-01: 30161; 2006-03-01: 30180; 2006-04-01: 30113; 2006-05-01: 32444; 2006-06-01: 32255; 2006-07-01: 32444; 2006-08-01: 32160; 2006-09-01: 32538; 2006-10-01: 32633; 2006-11-01: 32538; 2006-12-01: 32538; 2007-01-07: 33153; 2007-02-07: 38889; 2007-03-07: 33209; 2007-04-07: 33587; 2007-05-07: 33681; 2007-06-07: 33587; 2007-07-07: 33681; 2007-08-07: 33153; 2007-09-07: 33775; 2007-10-01: 35286; 2007-11-01: 35900; 2007-12-01: 36245; 2008-01-01: 37567; 2008-02-01: 38889; 2008-03-01: 41323; 2008-04-01: 46434; 2008-05-01: 46675; 2008-06-01: 48117; 2008-07-01: 49269; 2008-08-01: 49632; 2008-09-01: 50305; 2008-10-01: 50498; 2008-11-01: 50594; 2008-12-01: 50794; 2009-01-01: 50867; 2009-02-01: 49471; 2009-03-01: 49894; 2009-04-01: 49766; 2009-05-01: 49806; 2009-06-01: 46835; 2009-07-01: 47030; 2009-08-01: 47030; 2009-09-01: 47360
| Electrolytic High Grade Zinc | Zn1/Zno | Rs./MT | 2004-01-01: 66100; 2004-02-01: 66100; 2004-03-01: 66100; 2004-04-01: 59400; 2004-05-01: 59400; 2004-06-01: 59400; 2004-07-01: 60100; 2004-08-01: 60100; 2004-09-01: 58600; 2004-10-01: 58600; 2004-11-01: 58600; 2004-12-01: 58600; 2005-01-01: 74300; 2005-02-01: 74300; 2005-03-01: 74300; 2005-04-01: 74300; 2005-05-01: 69900; 2005-06-01: 78100; 2005-07-01: 78100; 2005-08-01: 78100; 2005-09-01: 78100; 2005-10-01: 78100; 2005-11-01: 78100; 2005-12-01: 78100; 2006-01-01: 107100; 2006-02-01: 124500; 2006-03-01: 121500; 2006-04-01: 140200; 2006-05-01: 171900; 2006-06-01: 197900; 2006-07-01: 166200; 2006-08-01: 175300; 2006-09-01: 181600; 2006-10-01: 180500; 2006-11-01: 212300; 2006-12-01: 228800; 2007-01-07: 221500; 2007-02-07: 104200; 2007-03-07: 17800; 2007-04-07: 160400; 2007-05-07: 174000; 2007-06-07: 166300; 2007-07-07: 157800; 2007-08-07: 221500; 2007-09-07: 144500; 2007-10-01: 1,36,700; 2007-11-01: 131100; 2007-12-01: 111100; 2008-01-01: 109800; 2008-02-01: 104200; 2008-03-01: 118300; 2008-04-01: 1,07,300; 2008-05-01: 98000; 2008-06-01: 97700; 2008-07-01: 90300; 2008-08-01: 88700; 2008-09-01: 86400; 2008-10-01: 91200; 2008-11-01: 68700; 2008-12-01: 71400; 2009-01-01: 63400; 2009-02-01: 68900; 2009-03-01: 67900; 2009-04-01: 80700; 2009-05-01: 88400; 2009-06-01: 88200; 2009-07-01: 91000; 2009-08-01: 98900; 2009-09-01: 106900
| Labour-Consumer Price Index | L1/Lo | No. | 2004-01-01: 118.5408; 2004-02-01: 118.5408; 2004-03-01: 118.5408; 2004-04-01: 119.4816; 2004-05-01: 119.4816; 2004-06-01: 119.4816; 2004-07-01: 121.5984; 2004-08-01: 121.5984; 2004-09-01: 122.7744; 2004-10-01: 122.7744; 2004-11-01: 122.7744; 2004-12-01: 122.7744; 2005-01-01: 123.48; 2005-02-01: 123.48; 2005-03-01: 123.48; 2005-04-01: 123.48; 2005-05-01: 123.9504; 2005-06-01: 128.8896; 2005-07-01: 128.8896; 2005-08-01: 128.8896; 2005-09-01: 128.8896; 2005-10-01: 128.8896; 2005-11-01: 128.8896; 2005-12-01: 128.8896; 2006-01-01: 128.8896; 2006-02-01: 130.0656; 2006-03-01: 129.36; 2006-04-01: 129.1248; 2006-05-01: 129.5952; 2006-06-01: 129.5952; 2006-07-01: 130.7712; 2006-08-01: 131.712; 2006-09-01: 133.8288; 2006-10-01: 138.2976; 2006-11-01: 135.0048; 2006-12-01: 136.1808; 2007-01-07: 127; 2007-02-07: 135; 2007-03-07: 138.3; 2007-04-07: 128; 2007-05-07: 139.3889; 2007-06-07: 130; 2007-07-07: 132; 2007-08-07: 133; 2007-09-07: 134; 2007-10-01: 133; 2007-11-01: 134; 2007-12-01: 134; 2008-01-01: 134; 2008-02-01: 135; 2008-03-01: 137; 2008-04-01: 135; 2008-05-01: 137; 2008-06-01: 138; 2008-07-01: 139; 2008-08-01: 140; 2008-09-01: 143; 2008-10-01: 145; 2008-11-01: 145; 2008-12-01: 148; 2009-01-01: 148; 2009-02-01: 147; 2009-03-01: 148; 2009-04-01: 148; 2009-05-01: 148; 2009-06-01: 150; 2009-07-01: 151; 2009-08-01: 162; 2009-09-01: 163
| High Tensile Galv. Steel Wire | W1/Wo | Rs./MT | 2004-01-01: 33150; 2004-02-01: 33150; 2004-03-01: 33150; 2004-04-01: 42500; 2004-05-01: 42500; 2004-06-01: 42500; 2004-07-01: 42850; 2004-08-01: 42850; 2004-09-01: 42850; 2004-10-01: 42850; 2004-11-01: 42850; 2004-12-01: 42850; 2005-01-01: 43350; 2005-02-01: 43350; 2005-03-01: 43350; 2005-04-01: 43350; 2005-05-01: 46033; 2005-06-01: 46033; 2005-07-01: 46033; 2005-08-01: 46033; 2005-09-01: 46033; 2005-10-01: 46033; 2005-11-01: 46033; 2005-12-01: 46033; 2006-01-01: 46033; 2006-02-01: 46033; 2006-03-01: 46033; 2006-04-01: 46033; 2006-05-01: 46033; 2006-06-01: 46033; 2006-07-01: 46033; 2006-08-01: 46033; 2006-09-01: 46033; 2006-10-01: 50500; 2006-11-01: 50500; 2006-12-01: 50500; 2007-01-07: 54500; 2007-02-07: 59500; 2007-03-07: 59500; 2007-04-07: 54500; 2007-05-07: 54500; 2007-06-07: 54500; 2007-07-07: 54500; 2007-08-07: 54500; 2007-10-01: 50725; 2007-11-01: 54500; 2007-12-01: 50725; 2008-01-01: 50975; 2008-02-01: 59500; 2008-03-01: 51125; 2008-04-01: 62500; 2008-05-01: 62000; 2008-06-01: 60875; 2008-07-01: 60875; 2008-08-01: 64875; 2008-09-01: 64875; 2008-10-01: 63875; 2008-11-01: 56875; 2008-12-01: 52875; 2009-01-01: 48375; 2009-02-01: 47375; 2009-03-01: 47875; 2009-04-01: 48625; 2009-05-01: 49125; 2009-06-01: 49625; 2009-07-01: 48875; 2009-08-01: 48475; 2009-09-01: 48725
| Wholesale Prices of Fuel etc.(Base 93-94=100) | F1/Fo | No. | 2004-01-01: 263.3; 2004-02-01: 263.3; 2004-03-01: 263.3; 2004-04-01: 264.3; 2004-05-01: 264.3; 2004-06-01: 264.3; 2004-07-01: 269.9; 2004-08-01: 269.9; 2004-09-01: 281.9; 2004-10-01: 281.9; 2004-11-01: 281.9; 2004-12-01: 281.9; 2005-01-01: 293.4; 2005-02-01: 293.4; 2005-03-01: 293.4; 2005-04-01: 293.4; 2005-05-01: 293.1; 2005-06-01: 312.8; 2005-07-01: 312.8; 2005-08-01: 312.8; 2005-09-01: 312.8; 2005-10-01: 312.8; 2005-11-01: 312.8; 2005-12-01: 312.8; 2006-01-01: 312.8; 2006-02-01: 312.8; 2006-03-01: 312.8; 2006-04-01: 312.8; 2006-05-01: 312.8; 2006-06-01: 312.8; 2006-07-01: 312.8; 2006-08-01: 312.8; 2006-09-01: 312.8; 2006-10-01: 215.4; 2006-11-01: 215.4; 2006-12-01: 215.4; 2007-01-07: 215.4; 2007-02-07: 215.7; 2007-03-07: 215.7; 2007-04-07: 215.4; 2007-05-07: 215.4; 2007-06-07: 215.4; 2007-07-07: 215.4; 2007-08-07: 215.4; 2007-09-07: 215.4; 2007-10-01: 215.4; 2007-11-01: 212.7; 2007-12-01: 207.22; 2008-01-01: 326.5; 2008-02-01: 334.4; 2008-03-01: 334.4; 2008-04-01: 333.6; 2008-05-01: 341; 2008-06-01: 342.7; 2008-07-01: 342.7; 2008-08-01: 374.4; 2008-09-01: 374.4; 2008-10-01: 374.4; 2008-11-01: 370; 2008-12-01: 370.6; 2009-01-01: 350.2; 2009-02-01: 374.4; 2009-03-01: 329.5; 2009-04-01: 323.5; 2009-05-01: 321; 2009-06-01: 322.6; 2009-07-01: 325.2; 2009-08-01: 327.1; 2009-09-01: 343.6
| EC Grade Al Ingots | Al1/Alo | Rs./MT | 2004-01-01: 88350; 2004-02-01: 88350; 2004-03-01: 88350; 2004-04-01: 91190; 2004-05-01: 91190; 2004-06-01: 91190; 2004-07-01: 93900; 2004-08-01: 93900; 2004-09-01: 96500; 2004-10-01: 96500; 2004-11-01: 96500; 2004-12-01: 96500; 2005-01-01: 96183; 2005-02-01: 96183; 2005-03-01: 96183; 2005-04-01: 96183; 2005-05-01: 94533; 2005-06-01: 96500; 2005-07-01: 96500; 2005-08-01: 96500; 2005-09-01: 96500; 2005-10-01: 96500; 2005-11-01: 96500; 2005-12-01: 96500; 2006-01-01: 115617; 2006-02-01: 123617; 2006-03-01: 120983; 2006-04-01: 125150; 2006-05-01: 136167; 2006-06-01: 135700; 2006-07-01: 130833; 2006-08-01: 130817; 2006-09-01: 130817; 2006-10-01: 131150; 2006-11-01: 141667; 2006-12-01: 137667; 2007-01-07: 141983; 2007-02-07: 117267; 2007-03-07: 138600; 2007-04-07: 136600; 2007-05-07: 130017; 2007-06-07: 126100; 2007-07-07: 122433; 2007-08-07: 141983; 2007-09-07: 118117; 2007-10-01: 1,12,467; 2007-11-01: 113433; 2007-12-01: 131417; 2008-01-01: 110250; 2008-02-01: 117263; 2008-03-01: 1235267; 2008-04-01: 1,33,583; 2008-05-01: 1,34,543; 2008-06-01: 1,41,400; 2008-07-01: 1,49,093; 2008-08-01: 1,42,267; 2008-09-01: 134267; 2008-10-01: 1,31,600; 2008-11-01: 114100; 2008-12-01: 110100; 2009-01-01: 99767; 2009-02-01: 92267; 2009-03-01: 96267; 2009-04-01: 96250; 2009-05-01: 96250; 2009-06-01: 96433; 2009-07-01: 98100; 2009-08-01: 105600; 2009-09-01: 115433
| Wholesale prices of Iron and Steel | I1/Io | No. | 2004-01-01: 197.8; 2004-02-01: 197.8; 2004-03-01: 197.8; 2004-04-01: 201.8; 2004-05-01: 201.8; 2004-06-01: 201.8; 2004-07-01: 239.8; 2004-08-01: 239.8; 2004-09-01: 242.9; 2004-10-01: 242.9; 2004-11-01: 242.9; 2004-12-01: 242.9; 2005-01-01: 244.3; 2005-02-01: 244.3; 2005-03-01: 244.3; 2005-04-01: 244.3; 2005-05-01: 258.8; 2005-06-01: 258.5; 2005-07-01: 258.5; 2005-08-01: 258.5; 2005-09-01: 258.5; 2005-10-01: 258.5; 2005-11-01: 258.5; 2005-12-01: 258.5; 2006-01-01: 258.5; 2006-02-01: 258.5; 2006-03-01: 258.5; 2006-04-01: 258.5; 2006-05-01: 258.5; 2006-06-01: 258.5; 2006-07-01: 258.5; 2006-08-01: 258.5; 2006-09-01: 258.5; 2006-10-01: 258.9; 2006-11-01: 258.9; 2006-12-01: 258.9; 2007-01-07: 259.3; 2007-02-07: 280.6; 2007-03-07: 280.6; 2007-04-07: 266.7; 2007-05-07: 266.7; 2007-06-07: 268.7; 2007-07-07: 268.3; 2007-08-07: 217.22; 2007-09-07: 217.22; 2007-10-01: 277.3; 2007-11-01: 277.9; 2007-12-01: 280.1; 2008-01-01: 279.6; 2008-02-01: 280.6; 2008-03-01: 287.4; 2008-04-01: 357.1; 2008-05-01: 354.6; 2008-06-01: 357.9; 2008-07-01: 362.6; 2008-08-01: 362.4; 2008-09-01: 362.4; 2008-10-01: 362.4; 2008-11-01: 360.3; 2008-12-01: 322.7; 2009-01-01: 319.2; 2009-02-01: 322.7; 2009-03-01: 289; 2009-04-01: 286; 2009-05-01: 286.2; 2009-06-01: 286.2; 2009-07-01: 286.2; 2009-08-01: 296.4; 2009-09-01: 288
| Whole Sale Price Index : (HSD) | D1/Do | No. | 2004-01-01: 153.1; 2004-02-01: 153.1; 2004-03-01: 153.1; 2004-04-01: 153.8; 2004-05-01: 153.8; 2004-06-01: 153.8; 2004-07-01: 153.1; 2004-08-01: 153.1; 2004-09-01: 153.1; 2004-10-01: 153.1; 2004-11-01: 153.1; 2004-12-01: 153.1; 2005-01-01: 163.8; 2005-02-01: 163.8; 2005-03-01: 163.8; 2005-04-01: 163.8; 2005-05-01: 163.8; 2005-06-01: 163.8; 2005-07-01: 163.8; 2005-08-01: 163.8; 2005-09-01: 163.8; 2005-10-01: 163.8; 2005-11-01: 163.8; 2005-12-01: 163.8; 2006-01-01: 163.8; 2006-02-01: 163.8; 2006-03-01: 163.8; 2006-04-01: 163.8; 2006-05-01: 163.8; 2006-06-01: 163.8; 2006-07-01: 163.8; 2006-08-01: 163.8; 2006-09-01: 163.8; 2006-10-01: 449.5; 2006-11-01: 449.5; 2006-12-01: 449.5; 2007-01-07: 449.5; 2007-02-07: 449.5; 2007-03-07: 449.5; 2007-04-07: 449.5; 2007-05-07: 449.5; 2007-06-07: 449.5; 2007-07-07: 449.5; 2007-08-07: 449.5; 2007-09-07: 0; 2007-10-01: 449.5; 2007-11-01: 449.5; 2007-12-01: 449.5; 2008-01-01: 449.5; 2008-02-01: 449.5; 2008-03-01: 465.8; 2008-04-01: 465.8; 2008-05-01: 465.8; 2008-06-01: 511.5; 2008-07-01: 511.5; 2008-08-01: 511.5; 2008-09-01: 511.5; 2008-10-01: 511.5; 2008-11-01: 511.3; 2008-12-01: 482.3; 2009-01-01: 482.3; 2009-02-01: 482.3; 2009-03-01: 452.2; 2009-04-01: 452.2; 2009-05-01: 452.2; 2009-06-01: 452.2; 2009-07-01: 452.2; 2009-08-01: 481.4; 2009-09-01: 481.4
| Cement | C1/Co | No. | 2004-01-01: 156.3; 2004-02-01: 156.3; 2004-03-01: 156.3; 2004-04-01: 157.3; 2004-05-01: 157.3; 2004-06-01: 157.3; 2004-07-01: 152.9; 2004-08-01: 152.9; 2004-09-01: 150.8; 2004-10-01: 150.8; 2004-11-01: 150.8; 2004-12-01: 150.8; 2005-01-01: 194; 2005-02-01: 194; 2005-03-01: 194; 2005-04-01: 194; 2005-05-01: 191; 2005-06-01: 165.9; 2005-07-01: 165.9; 2005-08-01: 165.9; 2005-09-01: 165.9; 2005-10-01: 165.9; 2005-11-01: 165.9; 2005-12-01: 165.9; 2006-01-01: 165.9; 2006-02-01: 165.9; 2006-03-01: 165.9; 2006-04-01: 165.9; 2006-05-01: 165.9; 2006-06-01: 165.9; 2006-07-01: 165.9; 2006-08-01: 165.9; 2006-09-01: 165.9; 2006-10-01: 220.2; 2006-11-01: 220.2; 2006-12-01: 220.2; 2007-01-07: 220.2; 2007-02-07: 220.7; 2007-03-07: 220.7; 2007-04-07: 211.6; 2007-05-07: 211.6; 2007-06-07: 211.7; 2007-07-07: 211.7; 2007-08-07: 220.2; 2007-10-01: 220.2; 2007-11-01: 219.5; 2007-12-01: 219.5; 2008-01-01: 221.3; 2008-02-01: 220.9; 2008-03-01: 220.8; 2008-04-01: 221.2; 2008-05-01: 223.3; 2008-06-01: 221.6; 2008-07-01: 221.6; 2008-08-01: 222.1; 2008-09-01: 222.1; 2008-10-01: 222.1; 2008-11-01: 225.1; 2008-12-01: 225.2; 2009-01-01: 221.4; 2009-02-01: 225.2; 2009-03-01: 224.5; 2009-04-01: 227.7; 2009-05-01: 228.1; 2009-06-01: 228.1; 2009-07-01: 228.1; 2009-08-01: 228.1; 2009-09-01: 228.1
| Non Metallic mineral products | M1/Mo | No. | 2004-01-01: 151.4; 2004-02-01: 151.4; 2004-03-01: 151.4; 2004-04-01: 155; 2004-05-01: 155; 2004-06-01: 155; 2004-07-01: 156; 2004-08-01: 156; 2004-09-01: 156.5; 2004-10-01: 156.5; 2004-11-01: 156.5; 2004-12-01: 156.5; 2005-01-01: 168.1; 2005-02-01: 168.1; 2005-03-01: 168.1; 2005-04-01: 168.1; 2005-05-01: 168.4; 2005-06-01: 169.4; 2005-07-01: 169.4; 2005-08-01: 169.4; 2005-09-01: 169.4; 2005-10-01: 169.4; 2005-11-01: 169.4; 2005-12-01: 169.4; 2006-01-01: 169.4; 2006-02-01: 169.4; 2006-03-01: 169.4; 2006-04-01: 169.4; 2006-05-01: 169.4; 2006-06-01: 169.4; 2006-07-01: 169.4; 2006-08-01: 169.4; 2006-09-01: 169.4; 2006-10-01: 195.2; 2006-11-01: 195.2; 2006-12-01: 195.2; 2007-01-07: 211.7; 2007-02-07: 203.5; 2007-03-07: 203.5; 2007-04-07: 203.5; 2007-05-07: 203.5; 2007-06-07: 214.3; 2007-07-07: 220.2; 2007-08-07: 211.7; 2007-10-01: 211.7; 2007-11-01: 211.7; 2007-12-01: 211.7; 2008-01-01: 216; 2008-02-01: 219.5; 2008-03-01: 219.4; 2008-04-01: 219.4; 2008-05-01: 219.4; 2008-06-01: 219.4; 2008-07-01: 219.4; 2008-08-01: 219.4; 2008-09-01: 219.4; 2008-10-01: 219.4; 2008-11-01: 223.1; 2008-12-01: 223.1; 2009-01-01: 223.1; 2009-02-01: 223.1; 2009-03-01: 224; 2009-04-01: 224; 2009-05-01: 227.2; 2009-06-01: 227.2; 2009-07-01: 227.2; 2009-08-01: 227.2; 2009-09-01: 227.2
| Index No. of Insulators (Base 2003= 100) | In1/Ino | No. | 2007-05-07: 144.79; 2007-06-07: 145.39; 2007-07-07: 145.71; 2007-08-07: 146.4; 2007-09-07: 148.13; 2007-10-01: 148.18; 2007-11-01: 148.21; 2007-12-01: 150.71; 2008-01-01: 159.36; 2008-02-01: 160.11; 2008-03-01: 167.71; 2008-04-01: 170.33; 2008-05-01: 171.24; 2008-09-01: 157.02; 2008-12-01: 168.72; 2009-01-01: 161.94; 2009-02-01: 160.905; 2009-03-01: 159.87; 2009-04-01: 150.87; 2009-05-01: 150.64; 2009-06-01: 150.7; 2009-07-01: 153.18; 2009-08-01: 153.63; 2009-09-01: 156.06
| Labour Correction Factor |  | 0.2352
Price Variation Formulas
| Particulars | PGCIL Formulae | bar: 2004-01-01
| Towers | P1=Po[0.15+0.66(S1/So)+(0.08x(Zn1/Zno)+0.11(L1/Lo))-Po
| ACSR | P1=Po[0.15+0.65(Al1/Alo)+0.15x(W1/Wo)+0.05x(L1/Lo)]-Po
| Ground Wire | P1=Po[0.15+0.74(W1/Wo)+0.11x(L1/Lo)]-Po
| Insulator | P1=Po[0.15+0.05(Zn1/Zno)+0.53x(F1/Fo)+0.27x(L1/Lo)]-Po
| H/W Fittings | P1=Po[0.15+0.43(Al1/Alo)+0.05x(Zn1/Znoo)+0.21x(I1/Io)+0.16x(L1/Lo)]-Po
| Cond & GW Accessories | P1=Po[0.15+0.70(Al1/Alo)+0.15x(L1/Lo)]-Po
| GW Clamps | P1=Po[0.15+0.65(I1/Io)+0.05x(Zn1/Zno)+0.15x(L1/Lo)]-Po
| Tower erection | ER1=ERo[0.20+0.22(D1/Do)+0.58x(L1/Lo]-ERo
| Steel Reinforcement | dER=ERo[0.20+0.10x(D1/Do)+ 0.05x(L1/Lo)+0.65x(I1/Io]-ERo
| Concreting | dER=ERo[0.20+0.20x(D1/Do)+ 0.10x(L1/Lo)+0.30x(C1/Co)+0.2X(M1/Mo)]-ERo
| Month and Year Under Consideration | 2009-05-01
|  |  | Units | 2004-01-01: Values
| Structural Steel Heavy Angles | S1/So | Rs./MT | 2004-01-01: 49806
| Electrolytic High Grade Zinc | Zn1/Zno | Rs./MT | 2004-01-01: 88400
| Labour-Consumer Price Index | L1/Lo | No. | 2004-01-01: 148
| High Tensile Galv. Steel Wire | W1/Wo | Rs./MT | 2004-01-01: 49125
| Wholesale Prices of Fuel etc.(Base 93-94=100) | F1/Fo | No. | 2004-01-01: 321
| EC Grade Al Ingots | Al1/Alo | Rs./MT | 2004-01-01: 96250
| Wholesale prices of Iron and Steel | I1/Io | No. | 2004-01-01: 286.2
| Whole Sale Price Index : (HSD) | D1/Do | No. | 2004-01-01: 452.2
| Cement | C1/Co | No. | 2004-01-01: 228.1
| Non Metallic mineral products | M1/Mo | No. | 2004-01-01: 227.2
| Index No. of Insulators (Base 2003= 100) | In1/Ino | No. | 2004-01-01: 150.64

## Escalated Cost
CERC
Capital Cost Benchmarking
Project Cost (Escalated)
| Particulars | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
| Name of the Line | Pichore-Gwalior | Bina-Pichore | Sasaram-Fatepur | Balia-Luknow | Raigarh-Raipur | Muvattupuzha-North | Ranchi-1-Sipat | Gaya-Balia | BINA-GWALIOR | DURGAPUR-MAITHON | Kanpur-Ballabhgrh | Vapi-Navi Mumbai | Edamon-Muvattupuzha(Part-I) | Kaithal-Meerut | Ranchi-Rourkela | Maithon RB TPS -Ranchi | Mejia 'B' TPS-Maithon(PG) | Rourkela-Raigrah | Sasaram-Biharsharif | Ranchi(old)-Ranchi(new)(Line-1) | Ranchi(old)-Ranchi(new)(Line-2) | Maithon RB TPS- Maithon (PG) | Maithon -Jamshedpur(LILO atMejia 'B' TPS) | Edamon- Muvattupuzha(Part II) | Bokaro TPS-Kodarma TPS | Kodarma-Gaya | Pindwara-Kankroli | Madurai-Trivandrum | Bareili-Moradabad and other lines | Agra-Jaipur (Package-A2) | Malerkotla-Jallandhar etc. | Jodhpur-Merta | PPSP-DURGPUR | Thamnar-Raipur(Kumhari) | Nandikur-Hassan | BTPS-HIRIYUR | Bhoopalapally TPP to Warangal
| Voltage class | 765 kV | 765 kV | 765 kV | 765 kV | 400 kV | 400 kV | 765kV | 765kV | 765kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV | 400kV
| DC or SC | SC | SC | SC | SC | DC | DC | S/C | S/C | S/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | D/C | S/C | S/C | D/C | D/C | D/C | D/C | D/C
| Type of Conductor | ACSR Bersimis | ACSR Bersimis | ACSR Bersimis | ACSR Bersimis | ACSR Moose | ACSR, MOOSE | ACSR Bersimis | ACSR Bersimis | ACSR Bersimis | ACSR LAPWING | ACSR Moose | ACSR Moose | ACSR Moose | 0 | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose | ACSR Moose
| No. of Conductors in the bundle | Quad | Quad | Quad | Quad | Twin | Quad | Quad | Quad | Quad | TWIN | Twin | Twin | Quad | Quad Bundle | Twin | Twin | Twin | Twin | Quad | Quad | Quad | TWIN | TWIN | Quad | TWIN | Quad | Twin | Twin | Twin | Twin | Twin | Twin | Twin | Twin | Quad | Twin | Twin
| Wind Zone | 4 | 4 | 4 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 3
| Route length | 117.5 | 122.5 | 168 | 158 | 214 | 77.29 | 292 | 235 | 122.5 | 73 | 132 | 185 | 73.64 | 160 | 143 | 200 | 57 | 210 | 195 | 72 | 72 | 30 | 50 | 8 | 110 | 80 | 114 | 106 | 165 | 110 | 118 | 110 | 185 | 204 | 179 | 151 | 44
| Month and Year of Commissioning | 2007-01-01 | 2007-01-01 | 2008-03-01 | 2007-12-07 | 2007-01-01 | 2007-11-01 | 2008-02-01 | 2007-12-01 | 2007-01-01 | 2007-06-11 | 2007-07-11 | 2007-06-11 | 2007-11-11 | 2007-07-11 | 2007-01-01 | 2007-02-11 | 2008-02-11 | 2007-01-07 | 2008-02-08 | 2008-01-01 | 2008-01-01 | 2008-02-01 | 2008-02-01 | 2007-11-07 | 2008-02-08 | 2008-02-08 | 2006-10-06 | 2005-03-05 | 2004-05-01 | 2004-01-01 | 2004-07-01 | 2008-02-01 | 2007-01-01 | 2005-09-01 | 2008-09-01 | 2008-02-01 | 2008-11-01
I | SUPPLY | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate | Rate
1 | HT Tower parts | 63651.482 | 56712.4409 | 65492.1222 | 57433.9959 | 67683.9618 | 68590.0564 | 62231.5073 | 62121.6235 | 56460.4773 | 71150.1164 | 58294.0359 | 57275.3251 | 60977.2129 | 57974.3861 | 74168.7306 | 63921.8861 | 63921.8861 | 72799.4057 | 76512.1301 | 75072.3686 | 75072.3686 | 57932.1686 | 57932.1686 | 60974.7308 | 60725.7918 | 60725.7918 | 64424.3717 | 0 | 83011.6598 | 74294.2405 | 57075.6905 | 0 |  | 72290.8806 | 69818.6835 | 70217.0081 | 0 |  | 63162.6365 |  | 63439.4325
| MS Tower parts | 58955.1661 | 52040.8561 | 59975.0928 | 51797.4156 | 63780.3444 | 61929.1286 | 58162.9976 | 51898.0245 | 51809.6475 | 65940.9115 | 54450.4731 | 55081.7027 | 54912.0082 | 54450.4731 | 68933.5359 | 59186.9315 | 59186.9315 | 68026.293 | 67516.9003 | 65784.5909 | 65784.5909 | 52760.4145 | 52760.4145 | 54908.2849 | 56227.585 | 56227.585 | 60856.2648 | 0 | 73675.0231 | 70088.9062 | 66720.3611 | 75084.5413 |  | 65841.8785 | 60721.4123 | 65654.8794 | 76987.0086 |  | 68 |  | 59392.1826
| Stubs-HT | 63651.482 | 56712.4409 | 65492.1189 | 57433.9959 | 67683.9618 | 68590.0564 | 62231.5073 | 62121.6235 | 56460.4773 | 71150.1164 | 58294.0359 | 57275.3251 | 60982.1773 | 11530.6884 | 74168.7306 | 63921.8861 | 63921.8861 | 72799.4057 | 76512.1301 | 75072.3686 | 75072.3686 | 57932.1686 | 57932.1686 | 60975.9718 | 60725.7918 | 60725.7918 | 64424.3717 | 0 | 83011.6598 | 74294.2405 | 57075.6905 | 0 |  | 72290.8806 | 0 | 0 | 0
| Stubs-MS | 58957.7693 | 52043.4594 | 59975.0928 | 51797.4156 | 63780.3444 | 61929.1286 | 58162.9976 | 51898.0245 | 51812.2392 | 65940.9115 | 54450.4731 | 55081.7027 | 54916.9725 | 11530.6884 | 68933.5359 | 59186.9315 | 59186.9315 | 68026.293 | 67516.9003 | 65784.5909 | 65784.5909 | 52760.4145 | 52760.4145 | 54918.2136 | 56227.585 | 56227.585 | 60856.2648 | 0 | 73675.0231 | 70088.9062 | 66720.3611 | 0 |  | 65841.8785 | 0 | 0 | 0
2 | Bolts and Nuts
| Hex. Bolts and Nuts | 98751.4977 | 76611.9083 | 102718.0613 | 92640.8864 | 81157.2341 | 85028.2878 | 104395.0936 | 91688.2074 | 76272.8306 | 96560.8723 | 102495.0082 | 87453.1907 | 72670.7589 | 102495.0082 | 100500.9014 | 91959.9193 | 91959.9193 | 87087.5045 | 104620.0039 | 106302.0671 | 106302.0671 | 100234.2523 | 100234.2523 | 72670.7589 | 87362.2784 | 87362.2784 | 95232.3137 | 0 | 103136.4848 | 105133.3592 | 0 | 121030.1726 |  | 93694.8082 | 74841.4163 | 0 | 0
| Anti theft Bolts and Nuts | 172529.7364 | 110839.8254 | 210678.9276 | 171144.3649 | 136994.9731 | 141713.813 | 223680.4354 | 165039.5187 | 110347.3831 | 158817.2242 | 166554.3884 | 134415.1197 | 134356.634 | 166554.3884 | 172521.9266 | 183921.0223 | 183921.0223 | 164343.7244 | 197235.7144 | 194887.1229 | 194887.1229 | 184696.3711 | 184696.3711 | 134356.634 | 174724.5568 | 174724.5568 | 266564.5282 | 0 | 205663.959 | 157700.0388 | 144515.1888 | 0 |  | 200771.2593 | 0 | 94255.1885 | 0
3 | Earthing Pipe type | 2479 | 1845 | 1782 | 1793 | 1319 | 1713 | 2945 | 1544 | 1845 | 1470 | 1485 | 1794 | 1624 | 1485 | 2477 | 1549 | 1549 | 1864 | 1697 | 2107 | 2107 | 2043 | 2043 | 1624 | 1472 | 1472 | 2372 | 1763 | 2304 | 1500 | 2418 | 2989 |  | 5743 | 1728 | 2266 | 3145
| Earthing Counterpoise | 6065 | 6365 | 0 | 0 | 4344 | 5709 | 6639 | 0 | 6365 | 0 | 0 | 7537 | 4868 | 0 | 5995 | 7000 | 7000 | 6500 | 0 | 6500 | 6500 | 6500 | 6500 | 4868 | 0 | 6542 | 5993 | 6818 | 0 | 3500 | 0 | 7526 |  | 6890 | 3024 | 6646 | 0
| River Crossing locations (MT) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71897 | 0 | 0 | 67499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
4 | Tower Accessories
| Danger Plate | 280 | 212 | 283 | 291 | 113 | 171 | 211 | 144 | 212 | 147 | 149 | 149 | 217 | 147 | 279 | 132 | 132 | 144 | 178 | 157 | 157 | 330 | 330 | 217 | 125 | 125 | 265 | 142 | 308 | 150 | 167.5 | 201 |  | 172 | 130 | 308 | 332
| Number Plate | 280 | 212 | 283 | 291 | 113 | 171 | 211 | 144 | 212 | 147 | 149 | 149 | 217 | 147 | 279 | 126 | 126 | 144 | 178 | 157 | 157 | 330 | 330 | 217 | 120 | 120 | 265 | 142 | 308 | 150 | 167.5 | 201 |  | 172 | 0 | 308 | 332
| Circuit plates | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 147 | 0 | 149 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 308 | 150 | 66 | 0 |  | 345 | 86 | 308 | 332
| Phase Plate (Set of three) | 280 | 530 | 283 | 291 | 107 | 171 | 58 | 144 | 530 | 147 | 149 | 149 | 217 | 147 | 279 | 131 | 131 | 144 | 178 | 157 | 157 | 330 | 330 | 217 | 124 | 124 | 265 | 142 | 308 | 150 | 167.5 | 201 |  | 345 | 207 | 599 | 332
| Anti climbing device | 6375 | 5304 | 6059 | 6223 | 5214 | 3426 | 7087 | 5839 | 606 | 2940 | 3465 | 5503 | 5411 | 3465 | 6372 | 6552 | 6552 | 4388 | 7215 | 6224 | 6224 | 7057 | 7057 | 5411 | 6224 | 6224 | 6556 | 6622 | 4712 | 3000 | 7576.4 | 58832.0179 |  | 5743 | 2851 |  | 6000
| Bird guard | 928 | 606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 149 | 0 | 207 | 207 | 0 | 2659 | 2261 | 2261 | 1257 | 1257 | 0 | 197 | 197 | 795 | 0 | 232 | 0 | 0 | 201 |  | 0 | 0 | 0 | 0
5 | ACSR Moose Conductor | 244041.6415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Bersimis Conductor | 262609.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | GSS Ground wire | 36346.0573 | 27933.7121 | 45225.5413 | 37589.2637 | 24024.3346 | 30022.9632 | 45814.6201 | 37500.3301 | 27762.8082 | 41543.7636 | 41734.6883 | 33512.0321 | 29518.9829 | 41186.4633 | 36162.687 | 35934.1071 | 35934.1071 | 33126.6811 | 43934.2548 | 45508.9022 | 45508.9022 | 43465.2655 | 43465.2655 | 29603.4489 | 34137.4899 | 34137.4899 | 39150.1836 | 48255.564 | 52130.3982 | 40826.319 | 47073.3846 | 48089.0423 | 24068.7593 | 36637.8647 | 29552.2633 | 37557.0572 | 48195.5269
7 | Hardware fittings
| Single 'V' suspension | 29273.5535 | 23998.0329 | 13503.5584 | 16789.3676 | 0 | 0 | 23724.6809 | 17954.1759 | 24993.4821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16067.3356 | 8956.1574 | 0 | 10808.2079 | 0 | 0
| Double 'V' Suspension | 56566.0378 | 44707.7723 | 26569.4568 | 34298.2283 | 0 | 0 | 47717.6962 | 36678.9173 | 46562.2708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32006.4453 | 0 | 0 | 25894.7296 | 0 | 0 | 0 | 0 | 0
| Single 'I' Pilot | 34335.3087 | 27197.4774 | 17038.5971 | 30411.3526 | 3632.2536 | 26918.4343 | 31515.7259 | 32523.2397 | 0 | 7526.2827 | 5390.7737 | 4194.3204 | 24749.066 | 0 | 5785.7428 | 4502.7228 | 0 | 5584.293 | 30478.8521 | 23278.3228 | 23278.3228 | 0 | 0 | 24749.066 | 4277.4548 | 23225.4108 | 5616.994 | 6686.3667 | 6092.216 | 4993.5167 | 7173.097 | 7044.0097 | 3809.0719 | 6467.9928 | 0 | 0 | 5766.0939
| Single 'V' Pilot | 15045.3943 | 12664.9443 | 8856.2847 | 11987.6694 | 0 | 0 | 13780.4166 | 12819.1633 | 13190.2918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88344.1644 | 7 | 12873.0068
| Double 'I' suspension | 25416.0985 | 21331.6825 | 12548.0611 | 17092.2177 | 0 | 14318.3963 | 22434.4323 | 18279.4262 | 22216.5303 | 0 | 0 | 0 | 13164.9777 | 0 | 0 | 0 | 0 | 0 | 20184.9118 | 19784.0854 | 19784.0854 | 0 | 0 | 13164.9777 | 0 | 14856.5588 | 0 | 0 | 0 | 0 | 0 | 14469.4842 | 0 | 13570.1644 | 0 | 0 | 0
| Quad Tension string | 71501.4704 | 59283.4104 | 32508.6112 | 47680.0836 | 0 | 31312.7235 | 57786.3105 | 50989.0352 | 61742.5129 | 0 | 0 | 0 | 28790.2678 | 0 | 0 | 0 | 0 | 0 | 41492.7139 | 39833.3498 | 39833.3498 | 0 | 0 | 28790.2678 | 0 | 30960.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22421.9442 | 0 | 0
| Standard Insulators 120 kN | 1: 608.4354
| Standard Insulators 160 kN | 1: 729.7463
| Standard Insulators 210 kN | 1: 799.3355
| Antifog Insulator 120 kN | 1: 937.5735
| Antifog Insulator 160 kN | 1: 1058.8845
| Antifog Insulator 210 kN | 1: 1269.5329
| Polymer Insulator - 120 kN String | 1: 19888.4081
| Polymer Insulator - 160 kN String | 1: 22097.3954
| Single 'I' suspension | 0 | 0 | 0 | 0 | 6625.8498 | 0 | 0 | 0 | 28325.641 | 12504.6478 | 8029.614 | 7087.3634 | 0 | 0 | 8608.6785 | 6415.6321 | 6415.7147 | 7817.8342 | 0 | 0 | 0 | 7369.3767 | 7369.3767 | 0 | 6095.0225 | 0 | 8259.7598 | 10519.3089 | 9100.7467 | 7609.1683 | 11147.8111 | 10011.5816 | 0 | 9512.6821 | 0 | 0 | 9203.4334
| Single tension string | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9001.4796 | 6874.2781 | 0 | 0 | 9653.7541 | 8098.5434 | 0 | 8749.4294 | 18301.8967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7728.0616 | 0 | 11624.3924 | 6150.8155 | 0 | 0 | 0 | 0
| Double tension string | 0 | 0 | 0 | 0 | 9993.3157 | 0 | 0 | 0 | 0 | 21881.3125 | 13601.5207 | 12660.364 | 0 | 0 | 14583.5553 | 11718.6728 | 11718.8237 | 13496.2544 | 0 | 0 | 0 | 13233.4634 | 13233.4634 | 0 | 11132.602 | 0 | 14423.533 | 16809.1272 | 14988.6362 | 11116.5194 | 17394.3152 | 19049.8669 | 9015.9765 | 15979.6232 | 0 | 0 | 17631.2201
8 | Conductor and GW Accessories
| MSC joints for conductors | 1332.4861 | 1114.2685 | 537.7826 | 925.2699 | 617.8835 | 658.5754 | 1220.6074 | 989.0531 | 1103.2756 | 1731.5115 | 922.3287 | 787.5171 | 605.8166 | 0 | 951.2048 | 783.1984 | 783.2157 | 888.0576 | 940.57 | 815.5688 | 815.5688 | 853.4473 | 853.4473 | 605.8166 | 744.0994 | 746.7664 | 914.9154 | 0 | 0 | 736.9124 | 0 | 1129.0397 | 619.4821 | 1132.6739 | 555.2459 | 846.3352 | 1000.8256 | 29262.7677 | 33 | 904.4855
| MSC joints for GW | 296.5521 | 242.1975 | 119.1407 | 181.4092 | 202.2309 | 165.5535 | 198.2487 | 194.6629 | 239.8081 | 312.0996 | 261.4133 | 210.3466 | 152.8186 | 0 | 270.1741 | 207.1342 | 207.1388 | 253.3882 | 244.4771 | 224.2814 | 224.2814 | 196.4707 | 196.4707 | 152.8186 | 196.4707 | 196.4707 | 324.7538 | 297.7491 | 260.064 | 241.9712 | 220.0562 | 304.9296 | 132.6891 | 325.5162 | 146.0749 | 264.0353 | 330.6299
| Flexible copper earth bonds | 418.8499 | 363.696 | 166.7969 | 421.6315 | 205.4283 | 322.0106 | 504.9563 | 451.4522 | 360.1079 | 424.9685 | 376.9215 | 342.882 | 295.6312 | 0 | 369.2913 | 460.4958 | 460.5059 | 380.4819 | 540.5166 | 334.5686 | 334.5686 | 499.6223 | 499.6223 | 295.6312 | 437.3917 | 437.3917 | 390.6936 | 338.9601 | 307.3484 | 318.9621 | 388.0701 | 0 | 171.057 | 454.09 | 0 | 0 | 501.3064
| Vibration dampers for GW | 346.1107 | 282.9635 | 146.2681 | 284.9533 | 244.5955 | 285.6253 | 285.3714 | 305.6621 | 280.1719 | 376.2297 | 306.5744 | 275.3317 | 261.9748 | 0 | 326.9267 | 264.0294 | 264.0353 | 306.1441 | 322.7098 | 279.8884 | 279.8884 | 284.4824 | 284.4824 | 261.9748 | 250.7001 | 250.7001 | 330.5235 | 403.8673 | 341.737 | 274.9673 | 394.4126 | 407.1655 | 191.8396 | 393.8848 | 255.8328 | 363.6041 | 445.0099
| Quad spacer damper for conductor | 2225.3397 | 1816.8812 | 835.451 | 1601.2057 | 0 | 1660.0831 | 2045.6065 | 1712.2049 | 1798.9566 | 0 | 0 | 0 | 1526.3669 | 0 | 0 | 0 | 0 | 0 | 2021.6033 | 1694.1589 | 1694.1589 | 0 | 0 | 1526.3669 | 0 | 1533.5381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1083.0523 | 811.6639 | 0
| Quad rigid spacer for conductor | 1014.352 | 848.8904 | 370.6191 | 743.0323 | 0 | 742.2618 | 985.9094 | 0 | 840.5156 | 0 | 0 | 0 | 683.1356 | 0 | 0 | 0 | 0 | 0 | 965.4623 | 874.8829 | 874.8829 | 0 | 0 | 683.1356 | 0 | 727.2082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.1754 | 433.8357 | 0
| Vibration damper for conductor | 0 | 0 | 0 | 0 | 493.987 | 0 | 0 | 0 | 0 | 831.9806 | 693.0493 | 639.5904 | 0 | 0 | 714.6026 | 679.1868 | 679.2018 | 655.4521 | 0 | 0 | 0 | 731.6533 | 731.6533 | 0 | 645.4195 | 0 | 691.5442 | 864.3997 | 804.9088 | 604.9281 | 914.0796 | 984.1314 | 396.4686 | 837.7705 | 499.5599 | 815.22 | 886.4455
| Rigid spacer for jumpers | 0 | 0 | 0 | 0 | 328.5254 | 0 | 0 | 795.2185 | 0 | 477.9827 | 390.8173 | 296.7084 | 0 | 0 | 404.4619 | 298.7 | 298.7066 | 372.4886 | 0 | 0 | 0 | 306.7076 | 306.7076 | 0 | 283.5934 | 0 | 406.3543 | 403.8673 | 380.4242 | 604.9281 | 480.7403 | 420.5006 | 234.2042 | 0 | 0 | 0 | 536.1565
| Earthwire suspension clamps | 284.4681 | 227.7129 | 235.6014 | 178.4356 | 124.5846 | 142.1657 | 256.6497 | 201.2754 | 227.7129 | 291.2672 | 241.3117 | 171.2721 | 130.5818 | 96.6638 | 268.5489 | 231.9167 | 231.9167 | 249.1691 | 275.2891 | 228.1577 | 228.1577 | 254.8575 | 254.8575 | 130.5818 | 220.4463 | 220.1847 | 254.9377 | 328.2243 | 252.7114 | 182.8131 | 323.6589 | 595.3843 | 160.9217 | 275.2912 | 152.4176 | 219.7294 | 242.8491
| Earthwire tension clamps | 289.313 | 227.7129 | 235.2519 | 188.0711 | 167.8431 | 172.0029 | 279.232 | 191.6398 | 227.7129 | 289.1742 | 251.7431 | 208.2473 | 158.3129 | 221.1445 | 266.8186 | 269.1954 | 269.1954 | 248.8231 | 322.2459 | 237.0981 | 237.0981 | 277.7982 | 277.7982 | 158.3129 | 255.5744 | 255.2159 | 246.9292 | 314.5319 | 254.3604 | 170.6255 | 324.32 | 636.2475 | 167.8431 | 266.5336 | 167.0868 | 209.3344 | 245.8017
| Repair sleeve for conductor | 0 | 0 | 336.5266 | 489.5564 | 0 | 238.3243 | 710.3171 | 523.5189 | 0 | 928.6032 | 529.7745 | 275.3317 | 219.2219 | 0 | 609.0908 | 288.0321 | 288.0385 | 338.1173 | 335.1559 | 313.2526 | 313.2526 | 313.8197 | 313.8197 | 219.2219 | 273.8143 | 274.7034 | 0 | 0 | 0 | 538.9359 | 0 | 420.5006 | 237.4015 | 454.09 | 182.3918 | 358.2701 | 424.4573
| T-Connector for ACSR Moose Conductor. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1345.2799 | 895.2556 | 0 | 0 | 1319.6968 | 1173.4642 | 1173.49 | 1067.1079 | 1404.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1209.8562 | 0 | 0 | 875.2683 | 0 | 0 | 0 | 0
| Bundle spacer for line | 0 | 0 | 0 | 0 | 473.2044 | 0 | 0 | 0 | 0 | 961.0958 | 793.7933 | 619.9239 | 0 | 0 | 819.3151 | 712.9684 | 712.9841 | 748.9739 | 0 | 0 | 0 | 731.6533 | 731.6533 | 0 | 677.4238 | 0 | 833.3149 | 1010.6986 | 917.7465 | 659.9216 | 1081.6629 | 969.9073 | 608.2915 | 958.1809 | 0 | 0 | 875.7224
| Repair Sleeves for Ground wire | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1227 | 0 | 0 | 146.0749 | 0 | 0
9 | Aviation Requirements
Span markers
Obstruction lights
Wind measuring equipments
II | ERECTION
1 | Detailed survey | 11143.4372 | 9875.0428 | 13906.7518 | 7515.1971 | 20693.7008 | 10621.3087 | 10191.1508 | 16037.0929 | 9600.615 | 0 | 6309.0551 | 7646.5748 | 14904.0259 | 6365.4495 | 9297.9014 | 21799.971 | 21799.971 | 9870.6539 | 10439.5865 | 10353.7052 | 10353.7052 | 13363.7279 | 13363.7279 | 15924.5296 | 21281.9561 | 21281.9561 | 17512.0524 | 9338.185 | 15095.5317 | 16397.2692 | 20224.4622 | 21143.4664 | 21944.5396 | 11129.6614 | 0 | 0 | 12425.858
2 | Check survey | 10037.4324 | 5846.0254 | 11955.438 | 6142.1365 | 6898.266 | 7964.3886 | 6486.8155 | 10691.3953 | 5683.5641 | 8479.9726 | 3606.5851 | 4438.2831 | 14143.6923 | 3182.7248 | 9428.4714 | 9395.0993 | 9395.0993 | 3619.7518 | 8351.6692 | 7765.8099 | 7765.8099 | 10690.1366 | 10690.1366 | 15037.8276 | 9932.1433 | 9932.1433 | 14755.9308 | 4289.7053 | 14358.2862 | 10150.3157 | 0 | 0 | 16458.4047 | 7321.06 | 4893.295 | 27907.2613 | 2782.1294
3 | Soil Investigation
| All kinds except FR and HR | 8434.3838 | 8903.9969 | 7207.1715 | 6148.508 | 13797.6293 | 0 | 9499.7595 | 6950.2565 | 8656.5545 | 10599.9658 | 3606.5851 | 8481.5646 | 0 | 4243.633 | 13036.1538 | 7476.3297 | 7476.3297 | 11516.4944 | 9499.7595 | 6730.4393 | 6730.4393 | 8908.7996 | 8908.7996 | 0 | 7102.0904 | 7102.0904 | 11025.5281 | 0 | 21979.6201 | 27799.431 | 10112.2311 | 0 | 6583.3619 | 5082.3975 | 0 | 0 | 0
| Fissured rock | 24602.0233 | 21916.0117 | 0 | 0 | 25867.1261 | 0 | 11874.1707 | 6950.2565 | 21306.9649 | 12719.9589 | 0 | 20876.9378 | 0 | 0 | 52142.4205 | 18689.7671 | 18689.7671 | 13161.2376 | 9499.7595 | 6730.4393 | 6730.4393 | 26726.3987 | 26726.3987 | 0 | 17755.2259 | 17755.2259 | 27563.2993 | 0 | 0 | 0 | 0 | 0 | 0 | 5082.3975 | 0 | 0 | 0
| Hard rock | 24602.0233 | 34245.5513 | 0 | 0 | 0 | 0 | 13457.8164 | 53455.9145 | 33293.8662 | 19079.9384 | 0 | 0 | 0 | 0 | 0 | 31149.6119 | 0 | 0 | 9499.7595 | 8282.9642 | 8282.9642 | 106906.652 | 0 | 0 | 29592.3956 | 29592.3956 | 27563.2993 | 0 | 0 | 0 | 0 | 0 | 0 | 5085.2536 | 0 | 0 | 0
| River Crossing locations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26099.4949 | 0 | 0 | 106906.652 | 0 | 0 | 0 | 0 | 0 | 0 | 109901.231 | 0 | 20224.4622 | 0 | 0 | 0 | 0 | 0 | 0
4 | Benching
| All kinds except FR and HR | 105.3338 | 109.7227 | 115.4562 | 0 | 86.6809 | 174.1546 | 187.1197 | 79.6439 | 0 | 63.8161 | 27.4307 | 140.4451 | 76.4581 | 32.1487 | 98.7504 | 100.4315 | 0 | 131.6672 | 78.2308 | 82.8296 | 82.8296 | 0 | 0 | 76.4581 | 75.0593 | 75.0593 | 96.9071 | 0 | 0 | 144.8397 | 303.3669 | 116.2891 | 0 | 685.1062 | 93.5088 | 153.2901 | 82.8719
| Fissured rock | 280.8901 | 342.3348 | 0 | 0 | 0 | 232.5601 | 445.07 | 0 | 106.6735 | 211.9993 | 0 | 210.6676 | 175.2165 | 0 | 294.0568 | 259.0075 | 0 | 148.1256 | 0 | 311.1421 | 311.1421 | 0 | 0 | 177.3404 | 246.3214 | 246.3214 | 448.0651 | 0 | 0 | 0 | 0 | 380.5824 | 0 | 0 | 267.5943 | 510.6147 | 0
| Hard rock | 490.4605 | 547.5163 | 0 | 0 | 0 | 406.7148 | 1019.1151 | 0 | 332.8213 | 529.9983 | 0 | 0 | 584.0552 | 0 | 456.4464 | 741.0785 | 0 | 658.3362 | 0 | 362.1142 | 362.1142 | 0 | 0 | 590.4267 | 621.6179 | 621.6179 | 827.3575 | 0 | 0 | 0 | 0 | 422.8693 | 0 | 0 | 3979.0974 | 0 | 0
5 | Excavation
| Dry soil | 114.1116 | 170.0702 | 112.3358 | 108.3157 | 128.3756 | 174.1546 | 187.1197 | 107.2538 | 165.3439 | 63.8161 | 113.0144 | 111.9172 | 136.9875 | 106.0908 | 110.8199 | 103.603 | 103.603 | 131.6672 | 104.6602 | 113.6253 | 113.6253 | 160.6903 | 160.6903 | 145.4828 | 103.603 | 103.603 | 165.6799 | 177.2978 | 206.6166 | 289.6043 | 303.3669 | 158.576 | 274.3067 | 213.6353 | 1492.1615 | 163.8619 | 179.5559
| Wet soil | 126.1811 | 170.0702 | 115.4562 | 112.5634 | 172.2646 | 203.8883 | 206.1488 | 107.2538 | 165.3439 | 63.8161 | 113.0144 | 139.3478 | 150.7924 | 106.0908 | 123.9866 | 127.918 | 127.918 | 148.1256 | 156.4617 | 113.6253 | 113.6253 | 178.6623 | 178.6623 | 160.3497 | 126.8608 | 126.8608 | 192.7722 | 205.8458 | 247.3138 | 289.6043 | 444.9382 | 158.576 | 274.3067 | 291.7227 | 2984.323 | 190.2912 | 11.0003
| Dry Fissured Rock | 386.2239 | 352.2099 | 0 | 0 | 604.5721 | 465.1203 | 445.07 | 347.2473 | 342.4219 | 243.3666 | 0 | 185.4314 | 477.8633 | 0 | 378.5433 | 311.8661 | 311.8661 | 452.0575 | 417.5835 | 414.1482 | 414.1482 | 489.4712 | 489.4712 | 510.7828 | 312.9233 | 312.9233 | 654.3835 | 479.3051 | 0 | 859.3693 | 0 | 634.304 | 438.8908 | 724.8866 | 2984.323 | 715.7063 | 270.3204
| Wet Fissured Rock | 386.2239 | 352.2099 | 0 | 0 | 646.2667 | 465.1203 | 500.043 | 0 | 342.4219 | 264.9991 | 0 | 185.4314 | 0 | 0 | 390.6128 | 344.6385 | 344.6385 | 468.5159 | 0 | 414.1482 | 414.1482 | 0 | 507.4432 | 0 | 363.6676 | 363.6676 | 723.1563 | 0 | 0 | 0 | 0 | 0 | 438.8908 | 792.6606 | 149.2162 | 1012.772 | 98.6571
| Hard Rock | 633.1 | 1369.3393 | 0 | 0 | 1033.5878 | 581.9313 | 1019.1151 | 0 | 1331.2853 | 635.9979 | 0 | 0 | 887.7639 | 0 | 977.6292 | 1059.2877 | 1059.2877 | 0 | 0 | 932.3644 | 932.3644 | 0 | 801.3374 | 0 | 888.0256 | 888.0256 | 1171.2214 | 0 | 0 | 0 | 0 | 740.0213 | 877.7816 | 1669.3019 | 0 | 1431.4127 | 587.0096
6 | 1:1½:3 Concreting | 5550.5643 | 6045.0141 | 5555.7604 | 5380.1947 | 5257.2499 | 4963.9381 | 6176.0268 | 5536.9397 | 6014.5484 | 3704.5038 | 4111.1939 | 4847.2597 | 5739.3588 | 4182.1126 | 5809.2638 | 6079.2291 | 5982.8333 | 5781.0989 | 4566.7659 | 5530.5279 | 5530.5279 | 6870.7014 | 6870.7014 | 7680.5057 | 5848.2144 | 5848.2144 | 6292.7205 | 8103.1247 | 0 | 0 | 6869.2691 | 5446.413 | 0 | 7656.9831 | 6661.0548 | 8748.1724 | 6522.5787
7 | 1:3:6 Concreting | 4289.4043 | 4983.0945 | 4515.1382 | 4443.8768 | 4069.3011 | 3794.0598 | 4210.18 | 4494.7411 | 4983.0945 | 2675.1832 | 3255.6495 | 3875.2765 | 5739.3588 | 3200.7241 | 4571.0529 | 5062.1956 | 4981.9264 | 3705.2442 | 4566.7659 | 4525.0711 | 4525.0711 | 5430.9986 | 5430.9986 | 6142.1208 | 5139.1531 | 5139.1531 | 4906.4919 | 6790.4783 | 0 | 8368.4675 | 6117.9428 | 4418.7879 | 7302.0015 | 6446.0953 | 5244.4234 | 6700.1156 | 4090.5478
8 | Reinforcements | 45574.8443 | 50916.5208 | 70174.1969 | 50852.1332 | 58918.8108 | 40534.835 | 76764.0269 | 42618.853 | 57366.9574 | 29169.7246 | 42451.4219 | 41284.7127 | 51908.8255 | 38670.391 | 40775.6229 | 57406.5138 | 57406.5138 | 52876.463 | 60339.4703 | 49781.9349 | 49781.9349 | 70415.3981 | 70415.3981 | 55442.8209 | 55206.7964 | 55206.7964 | 47998.8725 | 48371.3107 | 0 | 49801.4526 | 53679.1989 | 0 | 37670.4976 | 46684.2425 | 0 | 64842.7807 | 64600.5749
9 | Installation of stubs | 5623.2883 | 25613.6666 | 4322.8467 | 3074.254 | 10345.7532 | 2336.2207 | 2304.6378 | 2844.8796 | 24901.8619 | 2420.0068 | 313.8069 | 3519.9042 | 5464.6325 | 2652.2706 | 3993.9062 | 6234.1511 | 6234.1511 | 3784.3359 | 20879.1731 | 20707.4104 | 3177.2601 | 6236.2654 | 6236.2654 | 5837.3659 | 7665.5637 | 7665.5637 | 6890.8248 | 5048.4797 | 13738.4365 | 15616.5968 | 3033.6693 | 2642.9333 | 8777.8158 | 40941.3596 | 48743.9429 | 0 | 10862.1434
10 | Erection of towers | 3322.4033 | 4987.9939 | 3355.5109 | 3269.647 | 3708.6272 | 3025.4058 | 2304.6378 | 2844.8796 | 4892.0467 | 1728.5763 | 2343.6768 | 2593.8446 | 4994.2026 | 2428.3011 | 3412.3759 | 2987.5718 | 2987.5718 | 3697.6549 | 5534.3023 | 5176.8526 | 3068.9444 | 4047.9166 | 4047.9166 | 5344.6357 | 2960.0853 | 2961.1425 | 3649.1257 | 4790.0457 | 6417.6358 | 5777.9205 | 4853.8709 | 2453.4708 |  | 4722.0763 | 3960.1967 | 5660.032 | 5801.0357
11 | Installation of earthing of towers
| Earthing Pipe type | 1968.4252 | 1644.7432 | 1585.1825 | 1229.7016 | 2413.8994 | 1592.8777 | 106.7745 | 3314.2476 | 1599.0358 | 950.7169 | 1352.8809 | 1566.8401 | 2732.3163 | 1591.3624 | 1303.5057 | 2254.9507 | 2254.9507 | 1892.7165 | 5220.3219 | 2070.741 | 2070.741 | 2137.6045 | 2137.6045 | 2919.2139 | 2286.6659 | 2286.6659 | 2756.1215 | 2521.2348 | 3296.4734 | 4372.3953 | 10112.2311 | 2114.3466 | 1795063.3395 | 1963.9712 | 1830.3848 | 3680.0203 | 3009.0406
| Earthing River Crossing Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3314.2476 | 0 | 0 | 0 | 0 | 0 | 42436.3301 | 0 | 0 | 24919.6895 | 0 | 76007.5902 | 0 | 0 | 26726.3987 | 0 | 0 | 3551.0452 | 0 | 0 | 0 | 68689.052 | 7027.6259 | 30336.6933 | 0 | 0 | 0 | 0 | 0 | 0
| Earthing Counterpoise | 3373.973 | 3015.1797 | 0 | 0 | 3794.2109 | 8495.3479 | 5285.8666 | 4247.6739 | 2931.3878 | 4409.6333 | 0 | 2871.443 | 4782.8808 | 15920.0536 | 2743.0675 | 3805.824 | 4228.6933 | 4937.5214 | 5814.4533 | 3716.7147 | 3716.7147 | 4228.6933 | 3700.1066 | 5107.8279 | 0 | 3551.0452 | 5168.3791 | 5048.4797 | 0 | 0 | 0 | 6343.0399 | 0 | 3924.9957 | 2438.1919 | 4906.3414 | 2594.6809
12 | Installation of tower accessories | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344309.8264 | 0 | 0 | 0 | 0
13 | River Crossing Location -Pile Foundation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211818.4179 | 0 | 0 | 0 | 0 | 0 | 106906.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27268284.9097 | 0 | 0 | 0 | 0
14 | Protection to tower footing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Random rubble masonry | 3011.8881 | 4109.115 | 2789.6715 | 3358.8482 | 2244.9264 | 2444.5363 | 2780.3658 | 1603.4969 | 3994.9226 | 1166.789 | 1622.7987 | 1304.6029 | 2076.0506 | 1591.3624 | 2767.2064 | 3571.1315 | 3571.1315 | 2793.5399 | 1565.6737 | 2588.9573 | 2588.9573 | 3119.7185 | 3119.7185 | 2165.9261 | 3136.6332 | 3136.6332 | 2661.2984 | 3847.9633 | 4324.8604 | 4997.248 | 2831.4247 | 2642.9333 | 4937.5214 | 5888.967 | 5272.304 | 4502.5012 | 2856.1222
| Stone bound wire netting | 2954.4665 | 4124.842 | 2882.2445 | 1912.5152 | 3794.2109 | 7215.7361 | 2780.3658 | 1603.4969 | 3995.9893 | 1037.1458 | 991.8932 | 1304.6029 | 1784.0231 | 1060.9083 | 0 | 0 | 3115.4898 | 2467.6635 | 0 | 2588.9573 | 2588.9573 | 0 | 0 | 170.0702 | 0 | 0 | 2661.2984 | 0 | 4121.3744 | 0 | 4044.8924 | 0 | 0 | 0 | 0 | 0 | 140.093
| Back filling | 97.6532 | 87.7782 | 136.2591 | 95.5727 | 120.695 | 174.1546 | 445.07 | 97.6965 | 85.3388 | 0 | 53.7641 | 58.153 | 79.6439 | 53.5812 | 91.0698 | 0 | 0 | 164.584 | 78.2308 | 129.5541 | 129.5541 | 124.7465 | 124.7465 | 85.5837 | 75.0593 | 75.0593 | 103.1592 | 177.2978 | 164.3541 | 221.925 | 182.0202 | 116.2891 | 219.4454 | 0 | 0 | 0 | 345.2997
| M15 concrete for top seal cover of revetments | 4709.2982 | 5453.2181 | 5055.1095 | 3647.69 | 4937.5214 | 4416.519 | 5294.324 | 5132.252 | 5301.673 | 2765.722 | 3786.5303 | 3210.4861 | 7592.7172 | 1591.3624 | 5454.3153 | 4667.4202 | 4667.4202 | 4304.4214 | 5220.3219 | 5176.8526 | 5176.8526 | 5505.7587 | 5505.7587 | 7924.1733 | 4453.8712 | 4453.8712 | 4438.9708 | 0 | 7388.1076 | 0 | 5662.8494 | 0 | 0 | 0 | 0 | 0 | 0
15 | Installation of Insulators and stringing | 175551.9279 | 155720.6475 | 223588.7409 | 168794.0667 | 137959.8343 | 375159.8713 | 260328.9301 | 106917.1386 | 151393.165 | 116599.6235 | 126222.7973 | 106957.686 | 370233.6315 | 182176.1648 | 121300.6371 | 137059.3494 | 137059.3494 | 222100.6853 | 0 | 206038.7337 | 206038.7337 | 182769.4095 | 182769.4095 | 453490.4942 | 136124.8082 | 179921.3845 | 359412.8359 | 265335.1739 | 0 | 287345.6952 | 151683.4663 | 174433.5978 | 0 | 280643.0895 | 159108.1877 | 220467.1529 | 242158.7117
| Stringing across river crossing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213833.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264293.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Aviation requirement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10590.2311 | 0 | 0 | 109307.5172 | 2652.2706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120632.4259 | 0 | 0 | 0 | 0 | 0 | 0 | 7078.5618 | 0 | 0 | 0 | 0 | 0 | 0
| Painting of towers (MT) etc. | 10543.2541 | 0 | 6485.3102 | 8198.0107 | 0 | 0 | 7597.9047 | 3742.2007 | 0 | 0 | 2253.7042 | 0 | 0 | 0 | 0 | 0 | 5233.0079 | 0 | 5114.6045 | 5176.8526 | 5176.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Transportation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Aviation requirment materials | 0 | 0 | 0 | 0 | 0 | 21238.3697 | 0 | 10691.3953 | 0 | 10590.2311 | 4492.0473 | 6525.2089 | 0 | 0 | 78219.117 | 6229.9224 | 0 | 65807.2854 | 0 | 0 | 0 | 53452.7974 | 53452.7974 | 0 | 5918.0562 | 5918.0562 | 82688.856 | 20175.8887 | 0 | 0 | 18202.016 | 26429.333 | 0 | 0 | 0 | 0 | 0
| Painting of towers (MT) etc. | 10543.2541 | 0 | 6485.3102 | 8198.0107 | 0 | 0 | 7597.9047 | 3742.2007 | 0 | 0 | 2253.7042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Average Rates
CERC
Capital Cost Benchmarking
| Detailed BoQ for Transmission line | Final Rates Including Transportation Charges (INR) | Average Unit Rates (Including Taxes and Duties) | Avearge Unit Rates (Excluding Dates and Duties) | Excise Duty (INR) | Cess on Excise Duty (INR) | Central Sales Tax (INR)
I | Statutory clearances and charges. (% of total cost) | 0.5 | 0.5 | 0.5
II | Detailed survey (Rs. Per kM) | 14097.2947 | 14097.2947 | 14097.2947
III | Check Survey | 10109.2063 | 10109.2063 | 10109.2063
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 | 0.5 | 0.5
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 68832.5508 | 62345.6143 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 68832.5508 | 62345.6143 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 68832.5508 | 62345.6143 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 68832.5508 | 62345.6143 | 0 | 0 | 0
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 | 68832.5508 | 62345.6143 | 0 | 0 | 0
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 | 93768.8626 | 84931.8713 | 0 | 0 | 0
3 | Supply of Tower accessories
| a) Danger plate (one per tower) | 184.967 | 200.2083 | 181.3402 | 0 | 0 | 0
| b) Number plate (one per tower) | 186.2396 | 201.5857 | 182.5878 | 0 | 0 | 0
| c) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 193.6667 | 175.4151 | 0 | 0 | 0
| d) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 228.375 | 206.8524 | 0 | 0 | 0
| f) Anti climbing device (one set per tower) | 6448.8813 | 6980.2691 | 6322.4326 | 0 | 0 | 0
| g) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2037.6389 | 1845.6072 | 0 | 0 | 0
| f) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 6087.76 | 5514.0356 | 0 | 0 | 0
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 244041.6415 | 221042.6009 | 0 | 0 | 0
(=Route km x 3 x No. of Ckts x No. of Sub Condrs x 1.015)
5 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 262609.514 | 237860.5948 | 0 | 0 | 0
(=Route km x 3 x No. of Ckts x No. of Sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 38166.7709 | 34569.8475 | 0 | 0 | 0
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| Single 'V' suspension Insulator strings | 17611.7014 | 18606.8552 | 16853.3028 | 0 | 0 | 0
| I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 9401.4622 | 8515.447 | 0 | 0 | 0
| Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 14808.0793 | 13412.5321 | 0 | 0 | 0
| Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 14183.1083 | 12846.4598 | 0 | 0 | 0
| Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 17663.5056 | 15998.8566 | 0 | 0 | 0
| Quad Tension String | 39722.001 | 42995.0939 | 38943.1383 | 0 | 0 | 0
| Standard Insulators 120 kN | 575.8943 | 608.4354 | 551.0951 | 0 | 0 | 0
| Standard Insulators 160 kN | 690.7172 | 729.7463 | 660.9734 | 0 | 0 | 0
| Standard Insulators 210 kN | 756.5845 | 799.3355 | 724.0043 | 0 | 0 | 0
| Antifog Insulator 120 kN | 887.4291 | 937.5735 | 849.2145 | 0 | 0 | 0
| Antifog Insulator 160 kN | 1002.252 | 1058.8845 | 959.0928 | 0 | 0 | 0
| Antifog Insulator 210 kN | 1201.6342 | 1269.5329 | 1149.8892 | 0 | 0 | 0
| Polymer Insulator - 120 kN String | 18824.7128 | 19888.4081 | 18014.0792 | 0 | 0 | 0
| Polymer Insulator - 160 kN String | 20915.5563 | 22097.3954 | 20014.8864 | 0 | 0 | 0
7 | Supply of Conductor and GW Accessories | 0
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 1651.7506 | 1496.0858 | 0 | 0 | 0
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 227.6258 | 206.1738 | 0 | 0 | 0
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 381.0881 | 345.1735 | 0 | 0 | 0
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 301.6844 | 273.253 | 0 | 0 | 0
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 794.9218 | 720.0065 | 0 | 0 | 0
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 755.6866 | 684.469 | 0 | 0 | 0
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 301.6844 | 273.253 | 0 | 0 | 0
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 232.2358 | 210.3494 | 0 | 0 | 0
| i) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 248.2754 | 224.8774 | 0 | 0 | 0
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 717.9651 | 650.3025 | 0 | 0 | 0
| h) Quad Bundle Spacer for Jumper | 698.1584 | 755.6866 | 684.469 | 0 | 0 | 0
| j) Spacer Damper for Quad Conductor | 1477.425 | 1599.1649 | 1448.4559 | 0 | 0 | 0
V | ERECTION
| Stringing of Conductor- 765 kV Quad (Route kM) | 163660.9478 | 163660.9478 | 163660.9478
| Stringing of Conductor-400 kV Twin/Tripple (Route kM) | 190630.2522 | 190630.2522 | 190630.2522
| Stringing of Conductor- 400 kV Quad (Route kM) | 266273.3924 | 266273.3924 | 266273.3924
| Stringing of GW (Route kM) | 25000 | 25000 | 25000
| Erection of Tower parts (Rate x total tonnage) | 3892.0037 | 3892.0037 | 3892.0037
VI | CIVIL WORKS
1 | Excavations (9 times M20 concrete) | 294 | 294 | 294
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 | 5934.2225 | 5934.2225
3 | 1:3:6 Concrete (M20 Concrete) in Cu.M | 4948.1718 | 4948.1718 | 4948.1718
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 | 52526.7896 | 52526.7896
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 126.7554 | 126.7554
| b) Fissured rock | 752.9865 | 752.9865 | 752.9865
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3053.7228 | 3053.7228
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 4927.4272 | 4927.4272
| c) Back filling and levelling (Included above) | 135.269 | 135.269 | 135.269

## Moose-Antifog-Hilly
CERC
Capital Cost Benchmarking
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1707137.4496 | 1705764.3305 | 1702374.965 | 1716391.5702 | 1714529.8341 | 1709858.4007 | 1724885.84 | 1722628.4862 | 1716911.8601 | 1730236.1354 | 1727745.8111 | 1721414.3842 | 1735741.7211 | 1733020.5109 | 1726081.3534 | 1745209.9323 | 1742105.7898 | 1734162.9347
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1707137.4496 | 1705764.3305 | 1702374.965 | 1716391.5702 | 1714529.8341 | 1709858.4007 | 1724885.84 | 1722628.4862 | 1716911.8601 | 1730236.1354 | 1727745.8111 | 1721414.3842 | 1735741.7211 | 1733020.5109 | 1726081.3534 | 1745209.9323 | 1742105.7898 | 1734162.9347
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 10366.8386 | 11627.9013 | 12386.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 16898.4575 | 18612.4108 | 19653.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 20290.3432 | 22180.6901 | 23333.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 25560.0611 | 27781.5378 | 29139.1942 | 6713449.1742 | 6598109.0913 | 6309276.5083 | 7467581.5258 | 7318955.0922 | 6939279.0957 | 8127742.3112 | 7955060.3041 | 7508853.8293 | 8529587.207 | 8343816.2595 | 7861380.4186 | 8932824.5617 | 8734772.7986 | 8218426.5393 | 9604040.2607 | 9386927.1116 | 8818212.4665
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 10224.0244 | 11112.6151 | 11655.6777 | 1007017.3761 | 989716.3637 | 946391.4763 | 1120137.2289 | 1097843.2638 | 1040891.8644 | 1219161.3467 | 1193259.0456 | 1126328.0744 | 1279438.0811 | 1251572.4389 | 1179207.0628 | 1339923.6842 | 1310215.9198 | 1232763.9809 | 1440606.0391 | 1408039.0667 | 1322731.87
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 315521.9552 | 310101.1458 | 296526.4514 | 350965.0349 | 343979.8174 | 326135.6199 | 381991.5932 | 373875.8001 | 352904.7708 | 400877.6954 | 392146.7419 | 369472.9872 | 419829.241 | 410521.1078 | 386253.6147 | 451375.3635 | 441171.3739 | 414442.6459
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
| Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
| Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 419748.923 | 412537.4473 | 394478.5982 | 466899.9826 | 457607.3249 | 433868.6197 | 508175.6029 | 497378.9044 | 469480.4751 | 533300.3871 | 521685.3211 | 491521.7019 | 558512.2329 | 546129.3263 | 513845.5061 | 600479.046 | 586904.3532 | 551346.2736
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 12823124.772 | 2915.0868 | 3206.9634 | 635297.8298 | 613655.9432 | 561106.2203 | 786042.2794 | 755064.6285 | 678757.5465 | 931163.2189 | 892016.5529 | 794754.9867 | 1025514.933 | 981330.7887 | 871131.2359 | 1124769.6014 | 1075447.4324 | 952057.8016 | 1300151.3314 | 1242032.192 | 1096092.1771
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 323.8985 | 356.3293 | 1424791.6413 | 1376255.0689 | 1258401.0446 | 1762868.401 | 1693394.3749 | 1522259.3773 | 2088333.2333 | 2000538.4386 | 1782408.5159 | 2299937.1887 | 2200844.7686 | 1953698.6359 | 2522537.0707 | 2411921.528 | 2135193.8165 | 2915868.2158 | 2785523.5803 | 2458221.7959
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 213718.7462 | 48.5848 | 53.4494 | 178206.5093 | 172135.7738 | 157395.1243 | 220491.6249 | 211802.1272 | 190397.3339 | 261199.2975 | 250218.3207 | 222935.6143 | 287665.7654 | 275271.7326 | 244359.8095 | 315507.5542 | 301672.2612 | 267060.4078 | 364703.6389 | 348400.7201 | 307463.2898
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 136779.9976 | 31.0943 | 34.2076 | 1558787.3073 | 1505686.0742 | 1376748.3742 | 1928658.7654 | 1852650.9991 | 1665421.4742 | 2284732.1974 | 2188680.6712 | 1950036.546 | 2516236.6154 | 2407824.9696 | 2137435.7818 | 2759771.0808 | 2638752.6113 | 2335999.8215 | 3190093.3671 | 3047490.3664 | 2689407.2247
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 341427489.9176 | 341152866.1095 | 340474992.9989 | 343278314.0443 | 342905966.8294 | 341971680.133 | 344977168.0023 | 344525697.2389 | 343382372.0138 | 346047227.0745 | 345549162.2224 | 344282876.8349 | 347148344.2283 | 346604102.1868 | 345216270.6897 | 349041986.464 | 348421157.9656 | 346832586.945
| Survey, Design, Supervision etc. | [5 empty] | 5834924.9922 | 5832178.7541 | 5825400.023 | 5853433.2334 | 5849709.7613 | 5840366.8943 | 5870421.773 | 5865907.0654 | 5854473.8131 | 5881122.3637 | 5876141.7152 | 5863478.8613 | 5892133.5353 | 5886691.1149 | 5872812.7999 | 5911069.9576 | 5904861.6726 | 5888975.9624
| TOTAL COST | [5 empty] | 347262414.9098 | 346985044.8636 | 346300393.0219 | 349131747.2777 | 348755676.5907 | 347812047.0273 | 350847589.7753 | 350391604.3043 | 349236845.8269 | 351928349.4382 | 351425303.9376 | 350146355.6963 | 353040477.7636 | 352490793.3016 | 351089083.4896 | 354953056.4217 | 354326019.6382 | 352721562.9074
| TOTAL COST IN RS. LAKHS | [5 empty] | 3472.6241 | 3469.8504 | 3463.0039 | 3491.3175 | 3487.5568 | 3478.1205 | 3508.4759 | 3503.916 | 3492.3685 | 3519.2835 | 3514.253 | 3501.4636 | 3530.4048 | 3524.9079 | 3510.8908 | 3549.5306 | 3543.2602 | 3527.2156
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 34.7262 | 34.6985 | 34.63 | 34.9132 | 34.8756 | 34.7812 | 35.0848 | 35.0392 | 34.9237 | 35.1928 | 35.1425 | 35.0146 | 35.304 | 35.2491 | 35.1089 | 35.4953 | 35.4326 | 35.2722
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2405821.885 | 2404004.5313 | 2399554.9504 | 2418013.534 | 2415533.4462 | 2409359.47 | 2429267.2124 | 2426246.0239 | 2418654.2187 | 2436380.6503 | 2433039.2498 | 2424609.2398 | 2443718.0344 | 2440058.3064 | 2430797.0978 | 2456372.8995 | 2452183.3831 | 2441544.5063
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2405821.885 | 2404004.5313 | 2399554.9504 | 2418013.534 | 2415533.4462 | 2409359.47 | 2429267.2124 | 2426246.0239 | 2418654.2187 | 2436380.6503 | 2433039.2498 | 2424609.2398 | 2443718.0344 | 2440058.3064 | 2430797.0978 | 2456372.8995 | 2452183.3831 | 2441544.5063
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 39.6672 | 47.4027 | 52.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5.9501 | 7.1104 | 7.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4760.065 | 5688.3225 | 6294.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8071596.8224 | 7932218.9887 | 7585524.2727 | 8976104.3948 | 8796179.1737 | 8339381.5223 | 9768964.9637 | 9559735.8178 | 9022265.8025 | 10251848.7038 | 10026682.7192 | 9445301.6091 | 10736524.8785 | 10496412.8929 | 9873953.1559 | 11543450.8439 | 11280154.7492 | 10594306.1139
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1210739.5234 | 1189832.8483 | 1137828.6409 | 1346415.6592 | 1319426.8761 | 1250907.2283 | 1465344.7446 | 1433960.3727 | 1353339.8704 | 1537777.3056 | 1504002.4079 | 1416795.2414 | 1610478.7318 | 1574461.9339 | 1481092.9734 | 1731517.6266 | 1692023.2124 | 1589145.9171
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 379352.8401 | 372802.2928 | 356508.1656 | 421863.3277 | 413407.1145 | 391938.3159 | 459126.575 | 449293.1217 | 424032.844 | 481821.3803 | 471238.9197 | 443914.887 | 504600.4273 | 493315.5272 | 464060.8612 | 542524.727 | 530150.2089 | 497916.3605
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1827 |  |  |  | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'v'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 609 |  |  |  | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 288 |  |  |  | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 504665.1855 | 495950.7834 | 474274.1862 | 561218.2433 | 549968.6731 | 521408.0455 | 610790.73 | 597708.9733 | 564104.4201 | 640982.3535 | 626904.1685 | 590554.1361 | 671286.0465 | 656273.3839 | 617354.9684 | 721737.9522 | 705275.7359 | 662394.0192
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 18536228.6849 | 154.5809 | 171.1442 | 918342.9207 | 886901.4237 | 811067.8111 | 1135695.0972 | 1090621.6016 | 980287.9116 | 1345188.2499 | 1288183.5312 | 1147406.2106 | 1481461.391 | 1417100.0263 | 1257527.879 | 1624850.5834 | 1552986.8315 | 1374257.406 | 1878266.7778 | 1793560.6884 | 1582089.3092
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17.1757 | 19.016 | 2059580.965 | 1989066.6644 | 1818993.5233 | 2547039.8382 | 2445952.857 | 2198505.8929 | 3016873.165 | 2889027.8571 | 2573304.5217 | 3322494.9117 | 3178150.7472 | 2820275.9819 | 3644075.9295 | 3482906.0526 | 3082066.9824 | 4212416.098 | 4022444.5248 | 3548174.6007
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 308937.1447 | 2.5763 | 2.8524 | 257603.0935 | 248783.483 | 227511.5019 | 318572.2498 | 305928.7463 | 274979.1966 | 377336.8822 | 361346.568 | 321857.3179 | 415562.6712 | 397508.7544 | 352747.3937 | 455784.5738 | 435626.1729 | 385491.0307 | 526869.9975 | 503109.2104 | 443789.6684
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 197719.7726 | 1.6489 | 1.8255 | 2253275.899 | 2176130.0249 | 1990062.2196 | 2786578.2307 | 2675984.4437 | 2405266.1325 | 3300597.4073 | 3160728.7855 | 2815312.9973 | 3634961.5948 | 3477042.4683 | 3085511.0853 | 3986785.9558 | 3810458.7294 | 3371922.4292 | 4608576.1287 | 4400738.5274 | 3881865.5101
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 481164377.006 | 480800906.2656 | 479910990.0777 | 483602706.7974 | 483106689.2425 | 481871894.0021 | 485853442.4741 | 485249204.7836 | 483730843.7408 | 487276130.0683 | 486607849.9678 | 484921847.9698 | 488743606.8829 | 488011661.2808 | 486159419.5636 | 491274579.908 | 490436676.6137 | 488308901.2554
| Survey, Design, Supervision etc. | [5 empty] | 7232293.863 | 7228659.1556 | 7219759.9938 | 7256677.161 | 7251716.9854 | 7239369.033 | 7279184.5177 | 7273142.1408 | 7257958.5304 | 7293411.3937 | 7286728.5927 | 7269868.5727 | 7308086.1618 | 7300766.7058 | 7282244.2886 | 7333395.8921 | 7325016.8591 | 7303739.1055
| TOTAL COST | [5 empty] | 488396670.869 | 488029565.4212 | 487130750.0714 | 490859383.9583 | 490358406.2279 | 489111263.0351 | 493132626.9918 | 492522346.9245 | 490988802.2711 | 494569541.462 | 493894578.5605 | 492191716.5425 | 496051693.0447 | 495312427.9866 | 493441663.8522 | 498607975.8001 | 497761693.4728 | 495612640.3609
| TOTAL COST IN RS. LAKHS | [5 empty] | 4883.9667 | 4880.2957 | 4871.3075 | 4908.5938 | 4903.5841 | 4891.1126 | 4931.3263 | 4925.2235 | 4909.888 | 4945.6954 | 4938.9458 | 4921.9172 | 4960.5169 | 4953.1243 | 4934.4166 | 4986.0798 | 4977.6169 | 4956.1264
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 48.8397 | 48.803 | 48.7131 | 49.0859 | 49.0358 | 48.9111 | 49.3133 | 49.2522 | 49.0989 | 49.457 | 49.3895 | 49.2192 | 49.6052 | 49.5312 | 49.3442 | 49.8608 | 49.7762 | 49.5613
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 3137206.9623 | 3135034.9854 | 3129744.1873 | 3151765.9658 | 3148783.7477 | 3141397.5631 | 3165277.4652 | 3161627.8962 | 3152503.5741 | 3173848.1154 | 3169801.5397 | 3159644.0594 | 3182710.0315 | 3178267.4726 | 3167081.9047 | 3198039.7379 | 3192935.6915 | 3180039.4168
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 3137206.9623 | 3135034.9854 | 3129744.1873 | 3151765.9658 | 3148783.7477 | 3141397.5631 | 3165277.4652 | 3161627.8962 | 3152503.5741 | 3173848.1154 | 3169801.5397 | 3159644.0594 | 3182710.0315 | 3178267.4726 | 3167081.9047 | 3198039.7379 | 3192935.6915 | 3180039.4168
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 4795.5834 | 6031.7 | 6844.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8616590.2871 | 8467404.143 | 8097622.1029 | 9580934.9506 | 9388165.7809 | 8900348.7823 | 10426848.0245 | 10202580.5495 | 9628258.4602 | 10942191.8119 | 10700798.4613 | 10079401.2181 | 11459515.8602 | 11202065.2527 | 10536641.663 | 12320881.171 | 12038530.5157 | 11305197.1335
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1292488.5431 | 1270110.6215 | 1214643.3154 | 1437140.2426 | 1408224.8671 | 1335052.3173 | 1564027.2037 | 1530387.0824 | 1444238.769 | 1641328.7718 | 1605119.7692 | 1511910.1827 | 1718927.379 | 1680309.7879 | 1580496.2495 | 1848132.1756 | 1805779.5774 | 1695779.57
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 404966.7085 | 397955.1854 | 380575.9889 | 450289.4489 | 441229.5895 | 418302.9285 | 490046.0837 | 479505.8516 | 452513.5822 | 514266.4621 | 502921.3398 | 473716.6094 | 538579.9097 | 526480.1206 | 495206.2186 | 579062.7763 | 565792.7226 | 531327.163
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 2436 |  |  |  | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 812 |  |  |  | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 384 |  |  |  | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 538740.1318 | 529412.4789 | 506292.3794 | 599034.4192 | 586981.7992 | 556481.7307 | 651923.9388 | 637901.9318 | 601993.2547 | 684145.0808 | 669052.3027 | 630200.3182 | 716490.0359 | 700393.3005 | 658788.6309 | 770345.6848 | 752692.1091 | 706841.4756
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 24249332.5977 | 85.5822 | 93.9493 | 1201388.0117 | 1160146.9043 | 1061029.4018 | 1485347.9151 | 1426178.5747 | 1281818.2767 | 1759213.2809 | 1684350.5096 | 1500057.4344 | 1937407.849 | 1852869.2639 | 1643924.522 | 2124931.5653 | 2030526.2306 | 1796457.0105 | 2456382.2242 | 2345089.1848 | 2068086.4412
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 9.5091 | 10.4388 | 2694370.2886 | 2601878.26 | 2379586.0021 | 3331211.2754 | 3198511.3392 | 2874752.4085 | 3945413.0966 | 3777517.2756 | 3364200.5275 | 4345052.6346 | 4155456.7258 | 3686853.3279 | 4765614.7882 | 4553890.5772 | 4028940.1482 | 5508963.9801 | 5259365.4692 | 4638127.4055
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 404155.5433 | 1.4264 | 1.5658 | 336999.6777 | 325431.1921 | 297627.8795 | 416652.8746 | 400055.3654 | 359561.0593 | 493474.4669 | 472474.8153 | 420779.0214 | 543459.577 | 519745.7763 | 461134.9778 | 596061.5935 | 569580.0845 | 503921.6536 | 689036.3561 | 657817.7007 | 580116.0469
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 258659.5477 | 0.91288 | 1.0021 | 2947764.4908 | 2846573.9755 | 2603376.065 | 3644497.6959 | 3499317.8884 | 3145110.7909 | 4316462.6172 | 4132776.8998 | 3680589.4485 | 4753686.5742 | 4546259.9669 | 4033586.3888 | 5213800.8308 | 4982164.8475 | 4407845.0369 | 6027058.8902 | 5753986.6883 | 5074323.7955
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 627441392.4673 | 627006997.0889 | 625948837.4631 | 630353193.1503 | 629756749.5326 | 628279512.6223 | 633055493.0403 | 632325579.2436 | 630500714.8262 | 634769623.0895 | 633960307.9339 | 631928811.873 | 636542006.2909 | 635653494.5298 | 633416380.9393 | 639607947.5864 | 638587138.2959 | 636007883.3594
| Survey, Design, Supervision etc. | [5 empty] | 8695064.0177 | 8690720.0639 | 8680138.4676 | 8724182.0245 | 8718217.5883 | 8703445.2192 | 8751205.0234 | 8743905.8854 | 8725657.2413 | 8768346.3239 | 8760253.1723 | 8739938.2117 | 8786070.1559 | 8777185.0383 | 8754813.9024 | 8816729.5689 | 8806521.4759 | 8780728.9266
| TOTAL COST | [5 empty] | 636136456.485 | 635697717.1528 | 634628975.9308 | 639077375.1748 | 638474967.1209 | 636982957.8415 | 641806698.0637 | 641069485.129 | 639226372.0675 | 643537969.4134 | 642720561.1062 | 640668750.0847 | 645328076.4468 | 644430679.568 | 642171194.8416 | 648424677.1553 | 647393659.7719 | 644788612.286
| TOTAL COST IN RS. LAKHS | [5 empty] | 6361.3646 | 6356.9772 | 6346.2898 | 6390.7738 | 6384.7497 | 6369.8296 | 6418.067 | 6410.6949 | 6392.2637 | 6435.3797 | 6427.2056 | 6406.6875 | 6453.2808 | 6444.3068 | 6421.7119 | 6484.2468 | 6473.9366 | 6447.8861
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 63.6136 | 63.5698 | 63.4629 | 63.9077 | 63.8475 | 63.6983 | 64.1807 | 64.1069 | 63.9226 | 64.3538 | 64.2721 | 64.0669 | 64.5328 | 64.4431 | 64.2171 | 64.8425 | 64.7394 | 64.4789
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 984895.8517 | 984101.9845 | 982604.87 | 988819.9046 | 987740.8277 | 985666.8778 | 992416.8343 | 991108.6525 | 988565.9221 | 994678.2414 | 993236.2818 | 990419.6308 | 997001.2118 | 995427.5574 | 992341.8105 | 1000985.6261 | 999195.4065 | 995669.0481
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 984895.8517 | 984101.9845 | 982604.87 | 988819.9046 | 987740.8277 | 985666.8778 | 992416.8343 | 991108.6525 | 988565.9221 | 994678.2414 | 993236.2818 | 990419.6308 | 997001.2118 | 995427.5574 | 992341.8105 | 1000985.6261 | 999195.4065 | 995669.0481
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 12.9621 | 15.239 | 16.7289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 1.9443 | 2.2858 | 2.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 1555.4579 | 1828.6799 | 2007.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 3314103.665 | 3239069.4172 | 3095630.46 | 3675264.3961 | 3577497.4891 | 3386322.1819 | 3993323.9735 | 3878993.5738 | 3652354.5296 | 4187540.3708 | 4064191.1802 | 3818167.0535 | 4382776.6055 | 4250976.547 | 3986807.2955 | 4708338.0976 | 4563459.2572 | 4271326.5244
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 497115.5497 | 485860.4126 | 464344.569 | 551289.6594 | 536624.6234 | 507948.3273 | 598998.596 | 581849.0361 | 547853.1794 | 628131.0556 | 609628.677 | 572725.058 | 657416.4908 | 637646.482 | 598021.0943 | 706250.7146 | 684518.8886 | 640698.9787
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 155757.8588 | 152231.3626 | 145489.9486 | 172731.8668 | 168136.97 | 159152.0198 | 187680.1857 | 182306.8299 | 171655.1377 | 196808.0626 | 191010.8373 | 179448.0755 | 205983.8703 | 199789.4669 | 187373.9117 | 221284.7679 | 214475.6816 | 200745.8851
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 609 |  |  |  | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 1152 |  |  |  | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 96 |  |  |  | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 207209.6486 | 202518.2382 | 193549.9201 | 229790.7129 | 223677.9752 | 211725.0093 | 249676.9386 | 242528.5919 | 228358.3059 | 261820.0444 | 254107.8105 | 238725.4996 | 274026.914 | 265786.3016 | 249269.4925 | 294382.1863 | 285323.8415 | 267058.6552
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 4847825.7959 | 0 | 0 | 240176.4985 | 229423.9972 | 209554.2888 | 295376.2046 | 279870.4243 | 250758.0488 | 348712.4248 | 329030.7226 | 291705.2098 | 383456.7128 | 361199.0414 | 318792.564 | 420046.1424 | 395162.5223 | 347575.2306 | 484767.6311 | 455393.3516 | 398954.9668
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 538647.3107 | 514532.5204 | 469970.4376 | 662444.4908 | 627669.4528 | 562378.7068 | 782062.4041 | 737921.9656 | 654211.4977 | 859983.9218 | 810066.3199 | 714960.699 | 942043.5653 | 886236.7103 | 779512.0023 | 1087195.3852 | 1021317.2633 | 894742.0806
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 80797.0966 | 0 | 0 | 67371.575 | 64355.4059 | 58781.7817 | 82855.5677 | 78506.0629 | 70339.791 | 97816.8365 | 92295.9497 | 81825.8221 | 107562.9084 | 101319.44 | 89424.0581 | 117826.5583 | 110846.4887 | 97497.8438 | 135981.4929 | 127741.7547 | 111910.302
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 51710.1418 | 0 | 0 | 589304.8265 | 562922.1415 | 514169.1821 | 724744.6111 | 686699.127 | 615268.0607 | 855612.0865 | 807320.4252 | 715737.3396 | 940861.7954 | 886249.6529 | 782199.7481 | 1030638.8036 | 969583.5484 | 852821.8301 | 1189441.5421 | 1117367.8596 | 978888.8129
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 196979170.3391 | 196820396.902 | 196520973.9943 | 197763980.9159 | 197548165.5312 | 197133375.5519 | 198483366.8523 | 198221730.5011 | 197713184.4284 | 198935648.2783 | 198647256.3656 | 198083926.1623 | 199400242.3567 | 199085511.4737 | 198468362.1073 | 200197125.2242 | 199839081.3046 | 199133809.6122
| Survey, Design, Supervision etc. | [5 empty] | 4390441.7964 | 4388854.062 | 4385859.8329 | 4398289.9021 | 4396131.7483 | 4391983.8485 | 4405483.7615 | 4402867.398 | 4397781.9373 | 4410006.5758 | 4407122.6566 | 4401489.3546 | 4414652.5166 | 4411505.2077 | 4405333.7141 | 4422621.3452 | 4419040.906 | 4411988.1891
| TOTAL COST | [5 empty] | 201369612.1355 | 201209250.964 | 200906833.8273 | 202162270.8181 | 201944297.2795 | 201525359.4004 | 202888850.6138 | 202624597.8991 | 202110966.3656 | 203345654.8541 | 203054379.0222 | 202485415.5169 | 203814894.8732 | 203497016.6814 | 202873695.8214 | 204619746.5694 | 204258122.2106 | 203545797.8013
| TOTAL COST IN RS. LAKHS | [5 empty] | 2013.6961 | 2012.0925 | 2009.0683 | 2021.6227 | 2019.443 | 2015.2536 | 2028.8885 | 2026.246 | 2021.1097 | 2033.4565 | 2030.5438 | 2024.8542 | 2038.1489 | 2034.9702 | 2028.737 | 2046.1975 | 2042.5812 | 2035.458
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 20.137 | 20.1209 | 20.0907 | 20.2162 | 20.1944 | 20.1525 | 20.2889 | 20.2625 | 20.2111 | 20.3346 | 20.3054 | 20.2485 | 20.3815 | 20.3497 | 20.2874 | 20.462 | 20.4258 | 20.3546
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1332556.9512 | 1331534.459 | 1329634.3617 | 1337560.534 | 1336160.6386 | 1333507.7353 | 1342175.7098 | 1340470.0888 | 1337199.9244 | 1345088.3146 | 1343203.3135 | 1339570.6657 | 1348087.7193 | 1346025.5989 | 1342035.7624 | 1353247.73 | 1350893.3561 | 1346316.6768
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1332556.9512 | 1331534.459 | 1329634.3617 | 1337560.534 | 1336160.6386 | 1333507.7353 | 1342175.7098 | 1340470.0888 | 1337199.9244 | 1345088.3146 | 1343203.3135 | 1339570.6657 | 1348087.7193 | 1346025.5989 | 1342035.7624 | 1353247.73 | 1350893.3561 | 1346316.6768
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 26.1911 | 31.6347 | 35.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3.9287 | 4.7452 | 5.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 3142.9283 | 3796.1589 | 4225.0539 | 3932659.3307 | 3842800.086 | 3673289.6566 | 4359709.4552 | 4242258.0967 | 4015396.5614 | 4736703.0264 | 4599136.5048 | 4329598.4627 | 4967148.6419 | 4818636.2898 | 4525778.1752 | 5198922.7469 | 5040161.1033 | 4725490.2715 | 5585579.1548 | 5410971.3232 | 5062725.6683
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 1257.1713 | 1518.4636 | 1690.0215 | 589898.8996 | 576420.0129 | 550993.4485 | 653956.4183 | 636338.7145 | 602309.4842 | 710505.454 | 689870.4757 | 649439.7694 | 745072.2963 | 722795.4435 | 678866.7263 | 779838.412 | 756024.1655 | 708823.5407 | 837836.8732 | 811645.6985 | 759408.8502
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 184829.0393 | 180605.7907 | 172639.057 | 204899.7491 | 199379.713 | 188717.564 | 222617.8767 | 216152.4583 | 203484.578 | 233448.472 | 226468.6161 | 212704.7277 | 244341.5043 | 236879.9472 | 222090.8941 | 262513.7705 | 254307.4666 | 237940.4476
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 913.5 |  |  |  | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'v'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 1152 |  |  |  | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 144 |  |  |  | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 245883.9675 | 240265.6452 | 229667.2451 | 272584.6731 | 265241.1928 | 251056.9959 | 296155.6634 | 287554.511 | 270702.0258 | 310563.9499 | 301278.4249 | 282967.8851 | 325055.2983 | 315128.9508 | 295454.6017 | 349230.4438 | 338313.3359 | 316539.7684
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 6826333.1759 | 21028.6958 | 23851.7409 | 338197.961 | 322919.2346 | 295058.8754 | 415636.2578 | 393543.2841 | 352578.0053 | 490626.0967 | 462541.741 | 409914.7751 | 539526.3298 | 507746.1336 | 447903.9151 | 591051.1398 | 555503.971 | 488306.0193 | 682236.1885 | 640248.833 | 560489.0355
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 2336.5218 | 2650.1934 | 758481.464 | 724215.6431 | 661732.812 | 932153.4533 | 882605.2213 | 790731.7975 | 1100334.2508 | 1037349.0596 | 919321.8012 | 1210003.5117 | 1138729.6056 | 1004520.5955 | 1325558.9491 | 1245836.7989 | 1095130.9796 | 1530060.978 | 1435895.328 | 1257016.8752
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 113772.2196 | 350.4783 | 397.529 | 94867.439 | 90581.6247 | 82766.5541 | 116589.5477 | 110392.2784 | 98901.1652 | 137624.843 | 129746.9395 | 114984.6226 | 151341.7793 | 142427.1607 | 125640.9033 | 165794.9319 | 155823.6451 | 136974.0413 | 191373.1229 | 179595.3083 | 157221.9986
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 72814.2205 | 224.3061 | 254.4186 | 829813.458 | 792325.0807 | 723966.0019 | 1019818.568 | 965610.5331 | 865096.7999 | 1203816.0628 | 1134907.379 | 1005780.153 | 1323799.2568 | 1245822.3393 | 1098991.5358 | 1450222.1974 | 1363002.514 | 1198123.4458 | 1673956.7827 | 1570935.249 | 1375234.0295
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 266511390.2432 | 266306891.8019 | 265926872.3346 | 267512106.8065 | 267232127.7179 | 266701547.0574 | 268435141.9576 | 268094017.7527 | 267439984.8717 | 269017662.9216 | 268640662.6974 | 267914133.1479 | 269617543.8636 | 269205119.7799 | 268407152.4779 | 270649545.9985 | 270178671.2264 | 269263335.3573
| Survey, Design, Supervision etc. | [5 empty] | 5085763.9954 | 5083719.011 | 5079918.8163 | 5095771.1611 | 5092971.3702 | 5087665.5636 | 5105001.5126 | 5101590.2705 | 5095049.9417 | 5110826.7222 | 5107056.72 | 5099791.4245 | 5116825.5316 | 5112701.2908 | 5104721.6178 | 5127145.553 | 5122436.8053 | 5113283.4466
| TOTAL COST | [5 empty] | 271597154.2386 | 271390610.8129 | 271006791.1509 | 272607877.9675 | 272325099.0881 | 271789212.6209 | 273540143.4702 | 273195608.0232 | 272535034.8134 | 274128489.6438 | 273747719.4174 | 273013924.5724 | 274734369.3952 | 274317821.0706 | 273511874.0957 | 275776691.5515 | 275301108.0317 | 274376618.8039
| TOTAL COST IN RS. LAKHS | [5 empty] | 2715.9715 | 2713.9061 | 2710.0679 | 2726.0788 | 2723.251 | 2717.8921 | 2735.4014 | 2731.9561 | 2725.3503 | 2741.2849 | 2737.4772 | 2730.1392 | 2747.3437 | 2743.1782 | 2735.1187 | 2757.7669 | 2753.0111 | 2743.7662
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 27.1597 | 27.1391 | 27.1007 | 27.2608 | 27.2325 | 27.1789 | 27.354 | 27.3196 | 27.2535 | 27.4128 | 27.3748 | 27.3014 | 27.4734 | 27.4318 | 27.3512 | 27.5777 | 27.5301 | 27.4377
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1717505.2118 | 1716267.4282 | 1713986.4243 | 1723532.3707 | 1721829.5798 | 1718628.5573 | 1729115.1504 | 1727033.374 | 1723073.2182 | 1732647.6651 | 1730342.7265 | 1725935.1253 | 1736291.874 | 1733766.0868 | 1728916.5507 | 1742574.4859 | 1739683.3571 | 1734105.8442
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1717505.2118 | 1716267.4282 | 1713986.4243 | 1723532.3707 | 1721829.5798 | 1718628.5573 | 1729115.1504 | 1727033.374 | 1723073.2182 | 1732647.6651 | 1730342.7265 | 1725935.1253 | 1736291.874 | 1733766.0868 | 1728916.5507 | 1742574.4859 | 1739683.3571 | 1734105.8442
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 6.3189 | 7.4431 | 8.1777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5055.1374 | 5954.461 | 6542.1879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 4466355.9779 | 4363788.9858 | 4171712.5808 | 4950410.5574 | 4816120.7661 | 4558469.1697 | 5378296.6414 | 5220873.6849 | 4914382.1674 | 5640003.2716 | 5469996.4751 | 5136821.6372 | 5903292.6983 | 5721507.3444 | 5363383.6521 | 6342628.8988 | 6142642.8294 | 5746142.3674
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 669953.3967 | 654568.3479 | 625756.8871 | 742561.5836 | 722418.1149 | 683770.3754 | 806744.4962 | 783131.0527 | 737157.3251 | 846000.4907 | 820499.4713 | 770523.2456 | 885493.9047 | 858226.1017 | 804507.5478 | 951394.3348 | 921396.4244 | 861921.3551
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 209911.9744 | 205091.4809 | 196064.1804 | 232661.8073 | 226350.3903 | 214241.155 | 252771.806 | 245373.1652 | 230968.5275 | 265071.6217 | 257081.5594 | 241422.8461 | 277445.8265 | 268902.1898 | 252070.918 | 298093.9633 | 288694.9205 | 270059.9986
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 1152 |  |  |  | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 279252.5962 | 272839.74 | 260830.4342 | 309517.4248 | 301121.1453 | 285011.8434 | 336270.3975 | 326427.7496 | 307264.8006 | 352633.2348 | 342003.8001 | 321172.5141 | 369095.0341 | 357729.1618 | 335337.984 | 396563.9093 | 384060.0629 | 359269.4318
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 8804840.556 | 161099.2384 | 176969.7293 | 436219.4236 | 416414.4721 | 380563.462 | 535896.3109 | 507216.1438 | 454397.9619 | 632539.7686 | 596052.7593 | 528124.3403 | 695595.9469 | 654293.2259 | 577015.2661 | 762056.1373 | 715845.4197 | 629036.8079 | 879704.7459 | 825104.3145 | 722023.1042
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17899.9154 | 19663.3033 | 978315.6173 | 933898.7658 | 853495.1864 | 1201862.4158 | 1137540.9898 | 1019084.8883 | 1418606.0975 | 1336776.1536 | 1184432.1047 | 1560023.1016 | 1467392.8912 | 1294080.4919 | 1709074.3328 | 1605436.8875 | 1410749.9569 | 1972926.5709 | 1850473.3927 | 1619291.6699
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 146747.3426 | 2684.9873 | 2949.4955 | 122363.3029 | 116807.8435 | 106751.3266 | 150323.5277 | 142278.494 | 127462.5393 | 177432.8494 | 167197.9292 | 148143.423 | 195120.6501 | 183534.8814 | 161857.7486 | 213763.3056 | 200800.8016 | 176450.2388 | 246764.7529 | 231448.8619 | 202533.6952
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 93918.2993 | 1718.3919 | 1887.6771 | 1070322.0896 | 1021728.0199 | 933762.8218 | 1314892.5249 | 1244521.9392 | 1114925.5392 | 1552020.039 | 1462494.3328 | 1295822.9664 | 1706736.7181 | 1605395.0257 | 1415783.3236 | 1869805.5912 | 1756421.4796 | 1543425.0614 | 2158472.0233 | 2024502.6384 | 1771579.2461
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 343501042.3568 | 343253485.634 | 342797284.8576 | 344706474.1306 | 344365915.9617 | 343725711.4503 | 345823030.0738 | 345406674.8055 | 344614643.6331 | 346529533.0138 | 346068545.3082 | 345187025.0515 | 347258374.8087 | 346753217.3642 | 345783310.1451 | 348514897.1774 | 347936671.4228 | 346821168.8465
| Survey, Design, Supervision etc. | [5 empty] | 5855660.5166 | 5853184.9493 | 5848622.9416 | 5867714.8343 | 5864309.2526 | 5857907.2075 | 5878880.3937 | 5874716.841 | 5866796.5293 | 5885945.4231 | 5881335.5461 | 5872520.3435 | 5893233.8411 | 5888182.2666 | 5878483.1944 | 5905799.0648 | 5900016.8072 | 5888861.7815
| TOTAL COST | [5 empty] | 349356702.8733 | 349106670.5834 | 348645907.7991 | 350574188.9649 | 350230225.2143 | 349583618.6578 | 351701910.4675 | 351281391.6466 | 350481440.1624 | 352415478.437 | 351949880.8543 | 351059545.395 | 353151608.6498 | 352641399.6309 | 351661793.3396 | 354420696.2422 | 353836688.23 | 352710030.6279
| TOTAL COST IN RS. LAKHS | [5 empty] | 3493.567 | 3491.0667 | 3486.4591 | 3505.7419 | 3502.3023 | 3495.8362 | 3517.0191 | 3512.8139 | 3504.8144 | 3524.1548 | 3519.4988 | 3510.5955 | 3531.5161 | 3526.414 | 3516.6179 | 3544.207 | 3538.3669 | 3527.1003
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 34.9357 | 34.9107 | 34.8646 | 35.0574 | 35.023 | 34.9584 | 35.1702 | 35.1281 | 35.0481 | 35.2415 | 35.195 | 35.106 | 35.3152 | 35.2641 | 35.1662 | 35.4421 | 35.3837 | 35.271
ESTIMATE FOR A 765 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1032283.4785 | 1030934.2231 | 1028404.008 | 1039243.8475 | 1037420.0191 | 1033942.2551 | 1045592.783 | 1043389.9626 | 1039147.8288 | 1049573.3657 | 1047149.8598 | 1042462.4696 | 1053655.3103 | 1051014.8778 | 1045890.6851 | 1060643.3608 | 1057646.7332 | 1051808.1234
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1032283.4785 | 1030934.2231 | 1028404.008 | 1039243.8475 | 1037420.0191 | 1033942.2551 | 1045592.783 | 1043389.9626 | 1039147.8288 | 1049573.3657 | 1047149.8598 | 1042462.4696 | 1053655.3103 | 1051014.8778 | 1045890.6851 | 1060643.3608 | 1057646.7332 | 1051808.1234
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 33.1275 | 39.4561 | 43.6035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 4.9691 | 5.9184 | 6.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3975.2993 | 4734.735 | 5232.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 6019909.3047 | 5887557.213 | 5636266.8142 | 6685615.8414 | 6513836.1661 | 6181104.1598 | 7269979.0049 | 7069546.8351 | 6676617.3372 | 7626261.5822 | 7410232.8633 | 6984431.5722 | 7984130.4966 | 7753482.5438 | 7296902.5122 | 8580455.5749 | 8327164.9246 | 7823094.8627
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 902986.3957 | 883133.582 | 845440.0221 | 1002842.3762 | 977075.4249 | 927165.624 | 1090496.8507 | 1060432.0253 | 1001492.6006 | 1143939.2373 | 1111534.9295 | 1047664.7358 | 1197619.5745 | 1163022.3816 | 1094535.3768 | 1287068.3362 | 1249074.7387 | 1173464.2294
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 282926.6305 | 276706.2825 | 264896.0139 | 314213.8307 | 306140.4458 | 290502.5449 | 341678.0154 | 332258.0066 | 313790.9146 | 358422.7575 | 348269.7345 | 328257.718 | 375242.0551 | 364401.9503 | 342943.3795 | 403268.4317 | 391364.1543 | 367673.6239
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 609 |  |  |  | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 1920 |  |  |  | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 376386.3227 | 368111.1952 | 352399.6181 | 418008.6832 | 407268.4017 | 386464.8032 | 454545.1642 | 442013.426 | 417446.0644 | 476821.2289 | 463314.3385 | 436691.7145 | 499196.4771 | 484775.5398 | 456228.5185 | 536480.86 | 520644.22 | 489127.9516
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 10110602.5806 | 0 | 0 | 417425.8089 | 399272.76 | 365916.9175 | 514851.8022 | 488734.5743 | 440079.8917 | 608787.4826 | 575681.8706 | 513466.8054 | 669919.7725 | 632503.7611 | 561903.2378 | 734268.0888 | 692457.3475 | 613304.977 | 848047.3378 | 798718.4809 | 704947.2066
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1123400.2867 | 1074545.7598 | 984776.6027 | 1385598.7097 | 1315310.5274 | 1184368.2541 | 1638403.8022 | 1549308.0799 | 1381871.3268 | 1802926.5283 | 1702230.4116 | 1512226.2327 | 1976104.4091 | 1863580.9432 | 1650561.5423 | 2282313.6519 | 2149557.0021 | 1897194.3686
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 168510.043 | 0 | 0 | 93673.2258 | 89599.5566 | 82114.2759 | 115536.2895 | 109675.4037 | 98756.9579 | 136616.103 | 129186.9757 | 115225.4867 | 150334.6098 | 141938.1992 | 126094.9556 | 164774.815 | 155392.1968 | 137629.8598 | 190307.6619 | 179237.9268 | 158195.0072
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 107846.4275 | 0 | 0 | 737430.8175 | 705361.3635 | 646434.4221 | 909545.0671 | 863405.9728 | 777451.8666 | 1075493.2765 | 1017008.3962 | 907098.3106 | 1183490.5147 | 1117390.8168 | 992666.8527 | 1297169.2343 | 1223305.7393 | 1083473.9512 | 1498173.3954 | 1411028.2826 | 1245370.5154
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 206456695.7018 | 206186844.6218 | 205680801.5957 | 207848769.5092 | 207484003.826 | 206788451.0114 | 209118556.6086 | 208677992.5246 | 207829565.7555 | 209914673.1405 | 209429971.9638 | 208492493.9285 | 210731062.0598 | 210202975.5514 | 209178137.0264 | 212128672.1591 | 211529346.6393 | 210361624.6747
| Survey, Design, Supervision etc. | [5 empty] | 4485217.05 | 4482518.5392 | 4477458.1089 | 4499137.7881 | 4495490.1312 | 4488534.6031 | 4511835.6591 | 4507430.0182 | 4498945.7505 | 4519796.8244 | 4514949.8126 | 4505575.0323 | 4527960.7136 | 4522679.8485 | 4512431.4633 | 4541936.8146 | 4535943.5594 | 4524266.3397
| TOTAL COST | [5 empty] | 210941912.7518 | 210669363.161 | 210158259.7047 | 212347907.2973 | 211979493.9573 | 211276985.6145 | 213630392.2677 | 213185422.5428 | 212328511.5061 | 214434469.9648 | 213944921.7764 | 212998068.9608 | 215259022.7734 | 214725655.3999 | 213690568.4897 | 216670608.9736 | 216065290.1986 | 214885891.0144
| TOTAL COST IN RS. LAKHS | [5 empty] | 2109.4191 | 2106.6936 | 2101.5826 | 2123.4791 | 2119.7949 | 2112.7699 | 2136.3039 | 2131.8542 | 2123.2851 | 2144.3447 | 2139.4492 | 2129.9807 | 2152.5902 | 2147.2566 | 2136.9057 | 2166.7061 | 2160.6529 | 2148.8589
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 21.0942 | 21.0669 | 21.0158 | 21.2348 | 21.1979 | 21.1277 | 21.363 | 21.3185 | 21.2329 | 21.4434 | 21.3945 | 21.2998 | 21.5259 | 21.4726 | 21.3691 | 21.6671 | 21.6065 | 21.4886
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1382135.7946 | 1380514.514 | 1377534.7666 | 1390332.1771 | 1388135.0608 | 1384023.8043 | 1397824.1906 | 1395167.2606 | 1390142.6811 | 1402525.4181 | 1399600.9268 | 1394044.6989 | 1407348.1532 | 1404160.8208 | 1398083.4632 | 1415606.5751 | 1411987.9995 | 1405059.3032
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1382135.7946 | 1380514.514 | 1377534.7666 | 1390332.1771 | 1388135.0608 | 1384023.8043 | 1397824.1906 | 1395167.2606 | 1390142.6811 | 1402525.4181 | 1399600.9268 | 1394044.6989 | 1407348.1532 | 1404160.8208 | 1398083.4632 | 1415606.5751 | 1411987.9995 | 1405059.3032
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 7142856.0815 | 6983337.2339 | 6686510.5709 | 7929272.5663 | 7721622.0606 | 7326915.7396 | 8621245.0377 | 8378603.2414 | 7911450.7189 | 9043561.9082 | 8781884.791 | 8275191.8837 | 9467959.7046 | 9188451.6777 | 8644766.4055 | 10175411.8588 | 9868311.4143 | 9267623.3067
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1071428.4122 | 1047500.5851 | 1002976.5856 | 1189390.8849 | 1158243.3091 | 1099037.3609 | 1293186.7556 | 1256790.4862 | 1186717.6078 | 1356534.2862 | 1317282.7187 | 1241278.7826 | 1420193.9557 | 1378267.7517 | 1296714.9608 | 1526311.7788 | 1480246.7122 | 1390143.496
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 335703.4303 | 328206.2858 | 314255.8816 | 372663.8154 | 362904.5558 | 344353.9558 | 405185.4747 | 393781.6774 | 371826.2155 | 425033.7288 | 412735.3001 | 388921.5 | 444979.7832 | 431843.3288 | 406290.9435 | 478228.9642 | 463795.7079 | 435564.2756
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 913.5 |  |  |  | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 1920 |  |  |  | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 446596.9831 | 436623.2925 | 418064.6249 | 495766.5625 | 482783.5081 | 458105.0531 | 539031.1635 | 523860.328 | 494652.2767 | 565435.929 | 549074.9371 | 517394.679 | 591970.8015 | 574494.9571 | 540501.8038 | 636203.2478 | 617002.2265 | 579445.0514
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 11903669.7617 | 0 | 0 | 491454.2867 | 469748.4528 | 430663.8307 | 605628.106 | 574323.266 | 517108.5544 | 715944.4158 | 676211.5413 | 602908.7438 | 787804.3234 | 742873.3842 | 659622.5192 | 863479.6957 | 813249.8642 | 719856.3715 | 997340.1927 | 938047.9099 | 827324.8593
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1322629.9735 | 1264213.9878 | 1159027.2104 | 1629901.1065 | 1545651.725 | 1391672.2106 | 1926790.6889 | 1819859.2973 | 1622582.603 | 2120184.1951 | 1999263.4737 | 1775213.9693 | 2323846.0991 | 2188664.6944 | 1937318.7685 | 2684099.1487 | 2524528.3554 | 2226544.129
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 198394.496 | 0 | 0 | 110285.7259 | 105414.7873 | 96643.929 | 135907.1171 | 128882.0955 | 116042.7202 | 160662.8566 | 151746.526 | 135296.8735 | 176788.7147 | 166705.9026 | 148023.8352 | 193770.7893 | 182498.8693 | 161540.7264 | 223810.0066 | 210504.41 | 185657.3951
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 126972.4775 | 0 | 0 | 868210.6584 | 829864.8002 | 760817.3091 | 1069911.8734 | 1014608.2643 | 913531.8799 | 1264798.3533 | 1194605.6496 | 1065107.8066 | 1391747.165 | 1312371.4807 | 1165299.2295 | 1525436.435 | 1436699.6464 | 1271709.2741 | 1761916.436 | 1657169.7825 | 1461564.7482
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 276427158.9297 | 276102902.8033 | 275506953.3202 | 278066435.4102 | 277627012.1623 | 276804760.8526 | 279564838.1242 | 279033452.1252 | 278028536.2239 | 280505083.6285 | 279920185.3661 | 278808939.7765 | 281469630.6422 | 280832164.1676 | 279616692.6321 | 283121315.0115 | 282397599.8968 | 281011860.6392
| Survey, Design, Supervision etc. | [5 empty] | 5184921.6823 | 5181679.121 | 5175719.6262 | 5201314.4471 | 5196920.2146 | 5188697.7015 | 5216298.4742 | 5210984.6142 | 5200935.4552 | 5225700.9293 | 5219851.9466 | 5208739.4908 | 5235346.3994 | 5228971.7347 | 5216817.0193 | 5251863.2431 | 5244626.092 | 5230768.6994
| TOTAL COST | [5 empty] | 281612080.6119 | 281284581.9243 | 280682672.9464 | 283267749.8573 | 282823932.3769 | 281993458.5541 | 284781136.5985 | 284244436.7395 | 283229471.6792 | 285730784.5578 | 285140037.3128 | 284017679.2673 | 286704977.0417 | 286061135.9022 | 284833509.6514 | 288373178.2546 | 287642225.9888 | 286242629.3386
| TOTAL COST IN RS. LAKHS | [5 empty] | 2816.1208 | 2812.8458 | 2806.8267 | 2832.6775 | 2828.2393 | 2819.9346 | 2847.8114 | 2842.4444 | 2832.2947 | 2857.3078 | 2851.4004 | 2840.1768 | 2867.0498 | 2860.6114 | 2848.3351 | 2883.7318 | 2876.4223 | 2862.4263
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 28.1612 | 28.1285 | 28.0683 | 28.3268 | 28.2824 | 28.1993 | 28.4781 | 28.4244 | 28.3229 | 28.5731 | 28.514 | 28.4018 | 28.6705 | 28.6061 | 28.4834 | 28.8373 | 28.7642 | 28.6243
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1865223.1539 | 1863113.3926 | 1859287.721 | 1875823.8377 | 1872938.5461 | 1867610.6791 | 1885594.2841 | 1882080.6874 | 1875522.7686 | 1891758.9247 | 1887876.3613 | 1880595.8159 | 1898107.116 | 1893859.9221 | 1885866.7352 | 1909029.3616 | 1904179.7826 | 1895014.1527
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1865223.1539 | 1863113.3926 | 1859287.721 | 1875823.8377 | 1872938.5461 | 1867610.6791 | 1885594.2841 | 1882080.6874 | 1875522.7686 | 1891758.9247 | 1887876.3613 | 1880595.8159 | 1898107.116 | 1893859.9221 | 1885866.7352 | 1909029.3616 | 1904179.7826 | 1895014.1527
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8111811.0163 | 7929102.5915 | 7592848.1894 | 9002736.6774 | 8764521.2587 | 8316329.7119 | 9787703.3704 | 9509126.779 | 8978022.3819 | 10267042.3324 | 9966516.4364 | 9390171.2997 | 10748868.8776 | 10427789.6464 | 9809137.8897 | 11552220.3544 | 11199351.082 | 10515553.7314
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1216771.6524 | 1189365.3887 | 1138927.2284 | 1350410.5016 | 1314678.1888 | 1247449.4568 | 1468155.5056 | 1426369.0169 | 1346703.3573 | 1540056.3499 | 1494977.4655 | 1408525.695 | 1612330.3316 | 1564168.447 | 1471370.6835 | 1732833.0532 | 1679902.6623 | 1577333.0597
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 381242.8464 | 372655.8268 | 356852.3786 | 423115.0047 | 411919.2404 | 390854.9157 | 460007.2518 | 446914.5734 | 421953.4702 | 482535.4579 | 468411.1954 | 441323.8458 | 505180.5766 | 490090.3385 | 461014.6418 | 542936.8807 | 526352.5587 | 494215.1177
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 1920 |  |  |  | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 163660.9478 | 100 |  |  |  | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 507179.5212 | 495755.9351 | 474732.1037 | 562883.3892 | 547989.3067 | 519966.7636 | 611962.3224 | 594544.7147 | 561338.1628 | 641932.3137 | 623142.3567 | 587107.1915 | 672057.8376 | 651982.8123 | 613302.4855 | 722286.2535 | 700223.6008 | 657470.1377
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 18358313.9123 | 0 | 0 | 757940.3873 | 724181.5816 | 664062.3139 | 933573.4582 | 884821.7681 | 796641.2663 | 1103471.1901 | 1041551.3259 | 928454.8056 | 1214199.6582 | 1144158.4584 | 1015655.5143 | 1330837.1975 | 1252517.8521 | 1108309.5618 | 1537199.8363 | 1444724.7722 | 1273689.8695
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 2039812.6569 | 1948959.0221 | 1787162.5997 | 2512486.4542 | 2381283.1087 | 2143966.683 | 2969724.9783 | 2803082.6871 | 2498710.8426 | 3267723.7846 | 3079224.8891 | 2733390.3932 | 3581625.4223 | 3370847.9064 | 2982746.2817 | 4137000.396 | 3888126.1976 | 3427827.2546
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 305971.8985 | 0 | 0 | 170087.0418 | 162511.3334 | 149020.1557 | 209500.3123 | 198560.0973 | 178771.7856 | 247626.5332 | 233731.2893 | 208351.6514 | 272474.7638 | 256757.0363 | 227920.0909 | 298649.0308 | 281073.6304 | 248712.2971 | 344958.2279 | 324206.1867 | 285824.7769
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 195822.0151 | 0 | 0 | 1338989.0788 | 1279350.2564 | 1173142.6388 | 1649265.1477 | 1563139.6664 | 1407358.6435 | 1949409.0791 | 1840020.5001 | 1640222.4577 | 2145023.684 | 2021287.8294 | 1794272.5633 | 2351077.3446 | 2212717.1913 | 1957956.6204 | 2715640.7381 | 2552272.8756 | 2250120.0011
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 373044630.7871 | 372622678.5216 | 371857544.1943 | 375164767.5311 | 374587709.221 | 373522135.8124 | 377118856.8168 | 376416137.4724 | 375104553.7152 | 378351784.9304 | 377575272.2533 | 376119163.1796 | 379621423.2045 | 378771984.4103 | 377173347.0473 | 381805872.3261 | 380835956.5219 | 379002830.5347
| Survey, Design, Supervision etc. | [5 empty] | 6151096.4009 | 6146876.8782 | 6139225.5349 | 6172297.7683 | 6166527.1852 | 6155871.4511 | 6191838.6612 | 6184811.4677 | 6171695.6301 | 6204167.9423 | 6196402.8155 | 6181841.7248 | 6216864.325 | 6208369.9371 | 6192383.5635 | 6238708.8162 | 6229009.6582 | 6210678.3983
| TOTAL COST | [5 empty] | 379195727.188 | 378769555.3998 | 377996769.7292 | 381337065.2994 | 380754236.4062 | 379678007.2635 | 383310695.478 | 382600948.9401 | 381276249.3454 | 384555952.8727 | 383771675.0688 | 382301004.9044 | 385838287.5295 | 384980354.3474 | 383365730.6108 | 388044581.1423 | 387064966.1801 | 385213508.933
| TOTAL COST IN RS. LAKHS | [5 empty] | 3791.9573 | 3787.6956 | 3779.9677 | 3813.3707 | 3807.5424 | 3796.7801 | 3833.107 | 3826.0095 | 3812.7625 | 3845.5595 | 3837.7168 | 3823.01 | 3858.3829 | 3849.8035 | 3833.6573 | 3880.4458 | 3870.6497 | 3852.1351
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 37.9196 | 37.877 | 37.7997 | 38.1337 | 38.0754 | 37.9678 | 38.3311 | 38.2601 | 38.1276 | 38.4556 | 38.3772 | 38.2301 | 38.5838 | 38.498 | 38.3366 | 38.8045 | 38.7065 | 38.5214
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 13309062.3407 | 13941842.3508 | 14341910.5814
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 12243.3706 | 13283.528 | 13922.4666 | 734602.2359 | 797011.6778 | 835347.9947
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 282821.8608 | 306849.4959 | 321608.978
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) x No. of Ckts. | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 2436 |  |  |  | 876960000 | 876960000 | 876960000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 21000 | 1680 |  |  |  | 35280000 | 35280000 | 35280000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 40 |  |  |  | 1240000 | 1240000 | 1240000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 840 |  |  |  | 49560000 | 49560000 | 49560000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 40 |  |  |  | 1800000 | 1800000 | 1800000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 812 |  |  |  | 1055600 | 1055600 | 1055600
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 5040 | 10080 |  |  |  | 50803200 | 50803200 | 50803200
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 1680 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 0 |  |  |  | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 380000 | 100 |  |  |  | 38000000 | 38000000 | 38000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 484837.4757 | 526027.7073 | 551329.6765
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 110476.1386 | 135501.5486 | 151914.4961 | 33142841.5799 | 40650464.5715 | 45574348.8348
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 12275.1265 | 15055.7276 | 16879.3885 | 69968221.113 | 85817647.4288 | 96212514.2067
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 1841.269 | 2258.3591 | 2531.9083 | 8653964.1903 | 10614287.9715 | 11899968.8624
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 1178.4121 | 1445.3499 | 1620.4213 | 63634255.8333 | 78048891.9773 | 87502749.7628
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 1565772040.0812 | 1640216747.1546 | 1687283597.8152
| Survey, Design, Supervision etc. | [5 empty] | 34966782.7415 | 36344009.8224 | 37214746.5596
| TOTAL COST | [5 empty] | 1600738822.8227 | 1676560756.9769 | 1724498344.3747
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 288132988.1081 | 301780936.2558 | 310409701.9875
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
v) | Contengency at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1984916140.3001 | 2078935338.6514 | 2138377947.0247
| TOTAL COST IN RS. LAKHS | [5 empty] | 19849.1614 | 20789.3534 | 21383.7795
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 198.4916 | 207.8935 | 213.8378
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 8411202.1434 | 8912246.9919 | 9223024.2025
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
III | Detailed survey (Rs. Per kM) | 50000 | 100 |  |  |  | 5000000 | 5000000 | 5000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 520753.4201 | 578395.2043 | 613278.8096 | 31245205.2042 | 34703712.2574 | 36796728.5749
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 12029404.0036 | 13360929.2191 | 14166740.5013
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 1218 |  |  |  | 438480000 | 438480000 | 438480000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of suspn.x1) | 24000 | 210 |  |  |  | 5040000 | 5040000 | 5040000
| b) Double 'I' Suspension Insulator Sring (No. Suspn. X 2) | 21000 | 420 |  |  |  | 8820000 | 8820000 | 8820000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'V' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
| f) Single 'I' Suspension Pilot strings (No. of Suspn x 1) | 15000 | 210 |  |  |  | 3150000 | 3150000 | 3150000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 406 |  |  |  | 527800 | 527800 | 527800
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 2700 | 5040 |  |  |  | 13608000 | 13608000 | 13608000
| f) Quad Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 1000 | 840 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190000 | 100 |  |  |  | 19000000 | 19000000 | 19000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 20621835.4348 | 22904450.0899 | 24285840.8595
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 48382.6073 | 59272.006 | 66421.8968 | 14514782.1992 | 17781601.804 | 19926569.0329
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 5375.8453 | 6585.7784 | 7380.2108 | 30642317.976 | 37538937.1417 | 42067201.2916
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 806.3768 | 987.8668 | 1107.0316 | 3789970.9076 | 4642973.8044 | 5203048.5808
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 516.0811 | 632.2347 | 708.5002 | 27868381.8224 | 34140675.4636 | 38259012.5431
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 989553193.3401 | 1048499646.1046 | 1085061670.8834
| Survey, Design, Supervision etc. | [5 empty] | 23306734.0768 | 24397243.4529 | 25073640.9113
| TOTAL COST | [5 empty] | 1012859927.4169 | 1072896889.5575 | 1110135311.7948
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 182314786.935 | 193121440.1204 | 199824356.1231
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
v) | Contengency at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1255946309.997 | 1330392143.0513 | 1376567786.6255
| TOTAL COST IN RS. LAKHS | [5 empty] | 12559.4631 | 13303.9214 | 13765.6779
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 125.5946 | 133.0392 | 137.6568
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 5050227.0344 | 5357651.6793 | 5546861.9223
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 10366.8386 | 11627.9013 | 12386.9423 | 130622166.4713 | 146511556.3957 | 156075473.2845
| b) 'B' Type towers | 60000 | 25 | 16898.4575 | 18612.4108 | 19653.708 | 25347686.3224 | 27918616.1635 | 29480562.0497
| c) 'C' Type towers | 60000 | 25 | 20290.3432 | 22180.6901 | 23333.1622 | 30435514.7251 | 33271035.0929 | 34999743.239
| d) 'D' Type towers | 60000 | 20 | 25560.0611 | 27781.5378 | 29139.1942 | 30672073.3304 | 33337845.351 | 34967032.9907
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 361795.7347 | 401731.755 | 425871.3526 | 21707744.0849 | 24103905.3003 | 25552281.1564
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 7163555.548 | 7954288.7491 | 8432252.7816
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 609 |  |  |  | 219240000 | 219240000 | 219240000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) | 21000 | 840 |  |  |  | 17640000 | 17640000 | 17640000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 203 |  |  |  | 263900 | 263900 | 263900
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 900 | 5040 |  |  |  | 4536000 | 4536000 | 4536000
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 840 |  |  |  | 420000 | 420000 | 420000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 3360 |  |  |  | 3024000 | 3024000 | 3024000
V | ERECTION
2 | Stringing of Conductor (Route kM) | 95000 | 100 |  |  |  | 9500000 | 9500000 | 9500000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 12280380.9395 | 13635923.5699 | 14455290.4828
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 21646.7931 | 26473.7232 | 29642.2493 | 6494037.9255 | 7942116.9663 | 8892674.7876
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 2405.1992 | 2941.5248 | 3293.5833 | 13709635.6204 | 16766691.3734 | 18773424.5515
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 360.7799 | 441.2287 | 494.0375 | 1695665.4583 | 2073774.9857 | 2321976.1945
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 230.8991 | 282.3864 | 316.184 | 12468552.8169 | 15248864.5753 | 17073935.5921
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 594144356.9927 | 630311962.2731 | 652571990.8604
| Survey, Design, Supervision etc. | [5 empty] | 16991670.6044 | 17660771.3021 | 18072581.8309
| TOTAL COST | [5 empty] | 611136027.5971 | 647972733.5751 | 670644572.6913
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 110004484.9675 | 116635092.0435 | 120716023.0844
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
v) | Contengency at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 757808674.2204 | 803486189.6332 | 831599270.1372
| TOTAL COST IN RS. LAKHS | [5 empty] | 7578.0867 | 8034.8619 | 8315.9927
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 75.7809 | 80.3486 | 83.1599

## Moose-Std-Hilly
CERC
Capital Cost Benchmarking
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1700395.8365 | 1699022.7175 | 1695633.3519 | 1709649.9572 | 1707788.2211 | 1703116.7876 | 1718144.227 | 1715886.8731 | 1710170.247 | 1723494.5223 | 1721004.1981 | 1714672.7711 | 1729000.1081 | 1726278.8979 | 1719339.7404 | 1738468.3193 | 1735364.1768 | 1727421.3217
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1700395.8365 | 1699022.7175 | 1695633.3519 | 1709649.9572 | 1707788.2211 | 1703116.7876 | 1718144.227 | 1715886.8731 | 1710170.247 | 1723494.5223 | 1721004.1981 | 1714672.7711 | 1729000.1081 | 1726278.8979 | 1719339.7404 | 1738468.3193 | 1735364.1768 | 1727421.3217
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 10366.8386 | 11627.9013 | 12386.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 16898.4575 | 18612.4108 | 19653.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 20290.3432 | 22180.6901 | 23333.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 25560.0611 | 27781.5378 | 29139.1942 | 6713449.1742 | 6598109.0913 | 6309276.5083 | 7467581.5258 | 7318955.0922 | 6939279.0957 | 8127742.3112 | 7955060.3041 | 7508853.8293 | 8529587.207 | 8343816.2595 | 7861380.4186 | 8932824.5617 | 8734772.7986 | 8218426.5393 | 9604040.2607 | 9386927.1116 | 8818212.4665
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 10224.0244 | 11112.6151 | 11655.6777 | 1007017.3761 | 989716.3637 | 946391.4763 | 1120137.2289 | 1097843.2638 | 1040891.8644 | 1219161.3467 | 1193259.0456 | 1126328.0744 | 1279438.0811 | 1251572.4389 | 1179207.0628 | 1339923.6842 | 1310215.9198 | 1232763.9809 | 1440606.0391 | 1408039.0667 | 1322731.87
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 315521.9552 | 310101.1458 | 296526.4514 | 350965.0349 | 343979.8174 | 326135.6199 | 381991.5932 | 373875.8001 | 352904.7708 | 400877.6954 | 392146.7419 | 369472.9872 | 419829.241 | 410521.1078 | 386253.6147 | 451375.3635 | 441171.3739 | 414442.6459
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 419748.923 | 412537.4473 | 394478.5982 | 466899.9826 | 457607.3249 | 433868.6197 | 508175.6029 | 497378.9044 | 469480.4751 | 533300.3871 | 521685.3211 | 491521.7019 | 558512.2329 | 546129.3263 | 513845.5061 | 600479.046 | 586904.3532 | 551346.2736
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 12823124.772 | 2915.0868 | 3206.9634 | 635297.8298 | 613655.9432 | 561106.2203 | 786042.2794 | 755064.6285 | 678757.5465 | 931163.2189 | 892016.5529 | 794754.9867 | 1025514.933 | 981330.7887 | 871131.2359 | 1124769.6014 | 1075447.4324 | 952057.8016 | 1300151.3314 | 1242032.192 | 1096092.1771
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 323.8985 | 356.3293 | 1424791.6413 | 1376255.0689 | 1258401.0446 | 1762868.401 | 1693394.3749 | 1522259.3773 | 2088333.2333 | 2000538.4386 | 1782408.5159 | 2299937.1887 | 2200844.7686 | 1953698.6359 | 2522537.0707 | 2411921.528 | 2135193.8165 | 2915868.2158 | 2785523.5803 | 2458221.7959
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 213718.7462 | 48.5848 | 53.4494 | 178206.5093 | 172135.7738 | 157395.1243 | 220491.6249 | 211802.1272 | 190397.3339 | 261199.2975 | 250218.3207 | 222935.6143 | 287665.7654 | 275271.7326 | 244359.8095 | 315507.5542 | 301672.2612 | 267060.4078 | 364703.6389 | 348400.7201 | 307463.2898
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 136779.9976 | 31.0943 | 34.2076 | 1558787.3073 | 1505686.0742 | 1376748.3742 | 1928658.7654 | 1852650.9991 | 1665421.4742 | 2284732.1974 | 2188680.6712 | 1950036.546 | 2516236.6154 | 2407824.9696 | 2137435.7818 | 2759771.0808 | 2638752.6113 | 2335999.8215 | 3190093.3671 | 3047490.3664 | 2689407.2247
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 340079167.3056 | 339804543.4975 | 339126670.3869 | 341929991.4322 | 341557644.2173 | 340623357.5209 | 343628845.3903 | 343177374.6269 | 342034049.4017 | 344698904.4624 | 344200839.6103 | 342934554.2229 | 345800021.6163 | 345255779.5747 | 343867948.0777 | 347693663.852 | 347072835.3535 | 345484264.3329
| Survey, Design, Supervision etc. | [5 empty] | 5821441.766 | 5818695.528 | 5811916.7969 | 5839950.0073 | 5836226.5352 | 5826883.6682 | 5856938.5469 | 5852423.8393 | 5840990.587 | 5867639.1376 | 5862658.4891 | 5849995.6352 | 5878650.3092 | 5873207.8887 | 5859329.5738 | 5897586.7315 | 5891378.4465 | 5875492.7363
| TOTAL COST | [5 empty] | 345900609.0716 | 345623239.0255 | 344938587.1837 | 347769941.4395 | 347393870.7525 | 346450241.1891 | 349485783.9372 | 349029798.4661 | 347875039.9887 | 350566543.6001 | 350063498.0994 | 348784549.8581 | 351678671.9254 | 351128987.4635 | 349727277.6514 | 353591250.5835 | 352964213.8001 | 351359757.0693
| TOTAL COST IN RS. LAKHS | [5 empty] | 3459.0061 | 3456.2324 | 3449.3859 | 3477.6994 | 3473.9387 | 3464.5024 | 3494.8578 | 3490.298 | 3478.7504 | 3505.6654 | 3500.635 | 3487.8455 | 3516.7867 | 3511.2899 | 3497.2728 | 3535.9125 | 3529.6421 | 3513.5976
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 34.5901 | 34.5623 | 34.4939 | 34.777 | 34.7394 | 34.645 | 34.9486 | 34.903 | 34.7875 | 35.0567 | 35.0063 | 34.8785 | 35.1679 | 35.1129 | 34.9727 | 35.3591 | 35.2964 | 35.136
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2399080.272 | 2397262.9183 | 2392813.3373 | 2411271.9209 | 2408791.8332 | 2402617.857 | 2422525.5993 | 2419504.4109 | 2411912.6056 | 2429639.0373 | 2426297.6368 | 2417867.6268 | 2436976.4214 | 2433316.6933 | 2424055.4848 | 2449631.2865 | 2445441.77 | 2434802.8932
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2399080.272 | 2397262.9183 | 2392813.3373 | 2411271.9209 | 2408791.8332 | 2402617.857 | 2422525.5993 | 2419504.4109 | 2411912.6056 | 2429639.0373 | 2426297.6368 | 2417867.6268 | 2436976.4214 | 2433316.6933 | 2424055.4848 | 2449631.2865 | 2445441.77 | 2434802.8932
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 39.6672 | 47.4027 | 52.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5.9501 | 7.1104 | 7.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4760.065 | 5688.3225 | 6294.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8071596.8224 | 7932218.9887 | 7585524.2727 | 8976104.3948 | 8796179.1737 | 8339381.5223 | 9768964.9637 | 9559735.8178 | 9022265.8025 | 10251848.7038 | 10026682.7192 | 9445301.6091 | 10736524.8785 | 10496412.8929 | 9873953.1559 | 11543450.8439 | 11280154.7492 | 10594306.1139
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1210739.5234 | 1189832.8483 | 1137828.6409 | 1346415.6592 | 1319426.8761 | 1250907.2283 | 1465344.7446 | 1433960.3727 | 1353339.8704 | 1537777.3056 | 1504002.4079 | 1416795.2414 | 1610478.7318 | 1574461.9339 | 1481092.9734 | 1731517.6266 | 1692023.2124 | 1589145.9171
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 379352.8401 | 372802.2928 | 356508.1656 | 421863.3277 | 413407.1145 | 391938.3159 | 459126.575 | 449293.1217 | 424032.844 | 481821.3803 | 471238.9197 | 443914.887 | 504600.4273 | 493315.5272 | 464060.8612 | 542524.727 | 530150.2089 | 497916.3605
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1827 |  |  |  | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'v'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 609 |  |  |  | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 288 |  |  |  | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 504665.1855 | 495950.7834 | 474274.1862 | 561218.2433 | 549968.6731 | 521408.0455 | 610790.73 | 597708.9733 | 564104.4201 | 640982.3535 | 626904.1685 | 590554.1361 | 671286.0465 | 656273.3839 | 617354.9684 | 721737.9522 | 705275.7359 | 662394.0192
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 18536228.6849 | 154.5809 | 171.1442 | 918342.9207 | 886901.4237 | 811067.8111 | 1135695.0972 | 1090621.6016 | 980287.9116 | 1345188.2499 | 1288183.5312 | 1147406.2106 | 1481461.391 | 1417100.0263 | 1257527.879 | 1624850.5834 | 1552986.8315 | 1374257.406 | 1878266.7778 | 1793560.6884 | 1582089.3092
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17.1757 | 19.016 | 2059580.965 | 1989066.6644 | 1818993.5233 | 2547039.8382 | 2445952.857 | 2198505.8929 | 3016873.165 | 2889027.8571 | 2573304.5217 | 3322494.9117 | 3178150.7472 | 2820275.9819 | 3644075.9295 | 3482906.0526 | 3082066.9824 | 4212416.098 | 4022444.5248 | 3548174.6007
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 308937.1447 | 2.5763 | 2.8524 | 257603.0935 | 248783.483 | 227511.5019 | 318572.2498 | 305928.7463 | 274979.1966 | 377336.8822 | 361346.568 | 321857.3179 | 415562.6712 | 397508.7544 | 352747.3937 | 455784.5738 | 435626.1729 | 385491.0307 | 526869.9975 | 503109.2104 | 443789.6684
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 197719.7726 | 1.6489 | 1.8255 | 2253275.899 | 2176130.0249 | 1990062.2196 | 2786578.2307 | 2675984.4437 | 2405266.1325 | 3300597.4073 | 3160728.7855 | 2815312.9973 | 3634961.5948 | 3477042.4683 | 3085511.0853 | 3986785.9558 | 3810458.7294 | 3371922.4292 | 4608576.1287 | 4400738.5274 | 3881865.5101
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 479816054.394 | 479452583.6535 | 478562667.4656 | 482254384.1853 | 481758366.6304 | 480523571.39 | 484505119.862 | 483900882.1716 | 482382521.1287 | 485927807.4562 | 485259527.3558 | 483573525.3577 | 487395284.2709 | 486663338.6687 | 484811096.9516 | 489926257.296 | 489088354.0016 | 486960578.6433
| Survey, Design, Supervision etc. | [5 empty] | 7218810.6369 | 7215175.9295 | 7206276.7676 | 7243193.9348 | 7238233.7593 | 7225885.8069 | 7265701.2916 | 7259658.9147 | 7244475.3043 | 7279928.1676 | 7273245.3665 | 7256385.3466 | 7294602.9357 | 7287283.4797 | 7268761.0625 | 7319912.6659 | 7311533.633 | 7290255.8794
| TOTAL COST | [5 empty] | 487034865.0309 | 486667759.583 | 485768944.2333 | 489497578.1202 | 488996600.3897 | 487749457.1969 | 491770821.1537 | 491160541.0863 | 489626996.433 | 493207735.6238 | 492532772.7223 | 490829910.7043 | 494689887.2066 | 493950622.1484 | 492079858.0141 | 497246169.9619 | 496399887.6346 | 494250834.5227
| TOTAL COST IN RS. LAKHS | [5 empty] | 4870.3487 | 4866.6776 | 4857.6894 | 4894.9758 | 4889.966 | 4877.4946 | 4917.7082 | 4911.6054 | 4896.27 | 4932.0774 | 4925.3277 | 4908.2991 | 4946.8989 | 4939.5062 | 4920.7986 | 4972.4617 | 4963.9989 | 4942.5083
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 48.7035 | 48.6668 | 48.5769 | 48.9498 | 48.8997 | 48.7749 | 49.1771 | 49.1161 | 48.9627 | 49.3208 | 49.2533 | 49.083 | 49.469 | 49.3951 | 49.208 | 49.7246 | 49.64 | 49.4251
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 3130465.3493 | 3128293.3724 | 3123002.5743 | 3145024.3527 | 3142042.1346 | 3134655.9501 | 3158535.8521 | 3154886.2832 | 3145761.9611 | 3167106.5024 | 3163059.9266 | 3152902.4463 | 3175968.4184 | 3171525.8596 | 3160340.2916 | 3191298.1249 | 3186194.0784 | 3173297.8037
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 3130465.3493 | 3128293.3724 | 3123002.5743 | 3145024.3527 | 3142042.1346 | 3134655.9501 | 3158535.8521 | 3154886.2832 | 3145761.9611 | 3167106.5024 | 3163059.9266 | 3152902.4463 | 3175968.4184 | 3171525.8596 | 3160340.2916 | 3191298.1249 | 3186194.0784 | 3173297.8037
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 4795.5834 | 6031.7 | 6844.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8616590.2871 | 8467404.143 | 8097622.1029 | 9580934.9506 | 9388165.7809 | 8900348.7823 | 10426848.0245 | 10202580.5495 | 9628258.4602 | 10942191.8119 | 10700798.4613 | 10079401.2181 | 11459515.8602 | 11202065.2527 | 10536641.663 | 12320881.171 | 12038530.5157 | 11305197.1335
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1292488.5431 | 1270110.6215 | 1214643.3154 | 1437140.2426 | 1408224.8671 | 1335052.3173 | 1564027.2037 | 1530387.0824 | 1444238.769 | 1641328.7718 | 1605119.7692 | 1511910.1827 | 1718927.379 | 1680309.7879 | 1580496.2495 | 1848132.1756 | 1805779.5774 | 1695779.57
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 404966.7085 | 397955.1854 | 380575.9889 | 450289.4489 | 441229.5895 | 418302.9285 | 490046.0837 | 479505.8516 | 452513.5822 | 514266.4621 | 502921.3398 | 473716.6094 | 538579.9097 | 526480.1206 | 495206.2186 | 579062.7763 | 565792.7226 | 531327.163
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 2436 |  |  |  | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 812 |  |  |  | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 384 |  |  |  | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 538740.1318 | 529412.4789 | 506292.3794 | 599034.4192 | 586981.7992 | 556481.7307 | 651923.9388 | 637901.9318 | 601993.2547 | 684145.0808 | 669052.3027 | 630200.3182 | 716490.0359 | 700393.3005 | 658788.6309 | 770345.6848 | 752692.1091 | 706841.4756
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 24249332.5977 | 85.5822 | 93.9493 | 1201388.0117 | 1160146.9043 | 1061029.4018 | 1485347.9151 | 1426178.5747 | 1281818.2767 | 1759213.2809 | 1684350.5096 | 1500057.4344 | 1937407.849 | 1852869.2639 | 1643924.522 | 2124931.5653 | 2030526.2306 | 1796457.0105 | 2456382.2242 | 2345089.1848 | 2068086.4412
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 9.5091 | 10.4388 | 2694370.2886 | 2601878.26 | 2379586.0021 | 3331211.2754 | 3198511.3392 | 2874752.4085 | 3945413.0966 | 3777517.2756 | 3364200.5275 | 4345052.6346 | 4155456.7258 | 3686853.3279 | 4765614.7882 | 4553890.5772 | 4028940.1482 | 5508963.9801 | 5259365.4692 | 4638127.4055
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 404155.5433 | 1.4264 | 1.5658 | 336999.6777 | 325431.1921 | 297627.8795 | 416652.8746 | 400055.3654 | 359561.0593 | 493474.4669 | 472474.8153 | 420779.0214 | 543459.577 | 519745.7763 | 461134.9778 | 596061.5935 | 569580.0845 | 503921.6536 | 689036.3561 | 657817.7007 | 580116.0469
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 258659.5477 | 0.91288 | 1.0021 | 2947764.4908 | 2846573.9755 | 2603376.065 | 3644497.6959 | 3499317.8884 | 3145110.7909 | 4316462.6172 | 4132776.8998 | 3680589.4485 | 4753686.5742 | 4546259.9669 | 4033586.3888 | 5213800.8308 | 4982164.8475 | 4407845.0369 | 6027058.8902 | 5753986.6883 | 5074323.7955
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 626093069.8553 | 625658674.4768 | 624600514.8511 | 629004870.5382 | 628408426.9205 | 626931190.0103 | 631707170.4283 | 630977256.6316 | 629152392.2142 | 633421300.4775 | 632611985.3218 | 630580489.261 | 635193683.6788 | 634305171.9177 | 632068058.3272 | 638259624.9744 | 637238815.6839 | 634659560.7473
| Survey, Design, Supervision etc. | [5 empty] | 8681580.7915 | 8677236.8378 | 8666655.2415 | 8710698.7984 | 8704734.3622 | 8689961.9931 | 8737721.7973 | 8730422.6593 | 8712174.0151 | 8754863.0978 | 8746769.9462 | 8726454.9856 | 8772586.9298 | 8763701.8122 | 8741330.6763 | 8803246.3427 | 8793038.2498 | 8767245.7005
| TOTAL COST | [5 empty] | 634774650.6468 | 634335911.3146 | 633267170.0926 | 637715569.3366 | 637113161.2827 | 635621152.0034 | 640444892.2256 | 639707679.2909 | 637864566.2293 | 642176163.5753 | 641358755.268 | 639306944.2466 | 643966270.6086 | 643068873.7299 | 640809389.0035 | 647062871.3171 | 646031853.9337 | 643426806.4478
| TOTAL COST IN RS. LAKHS | [5 empty] | 6347.7465 | 6343.3591 | 6332.6717 | 6377.1557 | 6371.1316 | 6356.2115 | 6404.4489 | 6397.0768 | 6378.6457 | 6421.7616 | 6413.5876 | 6393.0694 | 6439.6627 | 6430.6887 | 6408.0939 | 6470.6287 | 6460.3185 | 6434.2681
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 63.4775 | 63.4336 | 63.3267 | 63.7716 | 63.7113 | 63.5621 | 64.0445 | 63.9708 | 63.7865 | 64.2176 | 64.1359 | 63.9307 | 64.3966 | 64.3069 | 64.0809 | 64.7063 | 64.6032 | 64.3427
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 979948.6791 | 979154.8119 | 977657.6974 | 983872.732 | 982793.655 | 980719.7051 | 987469.6616 | 986161.4799 | 983618.7495 | 989731.0688 | 988289.1092 | 985472.4582 | 992054.0392 | 990480.3848 | 987394.6379 | 996038.4535 | 994248.2339 | 990721.8754
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 979948.6791 | 979154.8119 | 977657.6974 | 983872.732 | 982793.655 | 980719.7051 | 987469.6616 | 986161.4799 | 983618.7495 | 989731.0688 | 988289.1092 | 985472.4582 | 992054.0392 | 990480.3848 | 987394.6379 | 996038.4535 | 994248.2339 | 990721.8754
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 12.9621 | 15.239 | 16.7289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 1.9443 | 2.2858 | 2.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 1555.4579 | 1828.6799 | 2007.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 3314103.665 | 3239069.4172 | 3095630.46 | 3675264.3961 | 3577497.4891 | 3386322.1819 | 3993323.9735 | 3878993.5738 | 3652354.5296 | 4187540.3708 | 4064191.1802 | 3818167.0535 | 4382776.6055 | 4250976.547 | 3986807.2955 | 4708338.0976 | 4563459.2572 | 4271326.5244
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 497115.5497 | 485860.4126 | 464344.569 | 551289.6594 | 536624.6234 | 507948.3273 | 598998.596 | 581849.0361 | 547853.1794 | 628131.0556 | 609628.677 | 572725.058 | 657416.4908 | 637646.482 | 598021.0943 | 706250.7146 | 684518.8886 | 640698.9787
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 155757.8588 | 152231.3626 | 145489.9486 | 172731.8668 | 168136.97 | 159152.0198 | 187680.1857 | 182306.8299 | 171655.1377 | 196808.0626 | 191010.8373 | 179448.0755 | 205983.8703 | 199789.4669 | 187373.9117 | 221284.7679 | 214475.6816 | 200745.8851
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 609 |  |  |  | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 1152 |  |  |  | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 96 |  |  |  | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 207209.6486 | 202518.2382 | 193549.9201 | 229790.7129 | 223677.9752 | 211725.0093 | 249676.9386 | 242528.5919 | 228358.3059 | 261820.0444 | 254107.8105 | 238725.4996 | 274026.914 | 265786.3016 | 249269.4925 | 294382.1863 | 285323.8415 | 267058.6552
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 4847825.7959 | 0 | 0 | 240176.4985 | 229423.9972 | 209554.2888 | 295376.2046 | 279870.4243 | 250758.0488 | 348712.4248 | 329030.7226 | 291705.2098 | 383456.7128 | 361199.0414 | 318792.564 | 420046.1424 | 395162.5223 | 347575.2306 | 484767.6311 | 455393.3516 | 398954.9668
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 538647.3107 | 514532.5204 | 469970.4376 | 662444.4908 | 627669.4528 | 562378.7068 | 782062.4041 | 737921.9656 | 654211.4977 | 859983.9218 | 810066.3199 | 714960.699 | 942043.5653 | 886236.7103 | 779512.0023 | 1087195.3852 | 1021317.2633 | 894742.0806
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 80797.0966 | 0 | 0 | 67371.575 | 64355.4059 | 58781.7817 | 82855.5677 | 78506.0629 | 70339.791 | 97816.8365 | 92295.9497 | 81825.8221 | 107562.9084 | 101319.44 | 89424.0581 | 117826.5583 | 110846.4887 | 97497.8438 | 135981.4929 | 127741.7547 | 111910.302
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 51710.1418 | 0 | 0 | 589304.8265 | 562922.1415 | 514169.1821 | 724744.6111 | 686699.127 | 615268.0607 | 855612.0865 | 807320.4252 | 715737.3396 | 940861.7954 | 886249.6529 | 782199.7481 | 1030638.8036 | 969583.5484 | 852821.8301 | 1189441.5421 | 1117367.8596 | 978888.8129
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 195989735.816 | 195830962.3789 | 195531539.4713 | 196774546.3928 | 196558731.0082 | 196143941.0289 | 197493932.3293 | 197232295.9781 | 196723749.9053 | 197946213.7552 | 197657821.8425 | 197094491.6392 | 198410807.8336 | 198096076.9506 | 197478927.5842 | 199207690.7011 | 198849646.7815 | 198144375.0891
| Survey, Design, Supervision etc. | [5 empty] | 4380547.4511 | 4378959.7168 | 4375965.4877 | 4388395.5569 | 4386237.4031 | 4382089.5033 | 4395589.4163 | 4392973.0528 | 4387887.592 | 4400112.2305 | 4397228.3114 | 4391595.0094 | 4404758.1713 | 4401610.8625 | 4395439.3688 | 4412727 | 4409146.5608 | 4402093.8439
| TOTAL COST | [5 empty] | 200370283.2672 | 200209922.0957 | 199907504.959 | 201162941.9498 | 200944968.4113 | 200526030.5321 | 201889521.7455 | 201625269.0309 | 201111637.4973 | 202346325.9858 | 202055050.1539 | 201486086.6486 | 202815566.0049 | 202497687.8131 | 201874366.9531 | 203620417.7011 | 203258793.3423 | 202546468.933
| TOTAL COST IN RS. LAKHS | [5 empty] | 2003.7028 | 2002.0992 | 1999.075 | 2011.6294 | 2009.4497 | 2005.2603 | 2018.8952 | 2016.2527 | 2011.1164 | 2023.4633 | 2020.5505 | 2014.8609 | 2028.1557 | 2024.9769 | 2018.7437 | 2036.2042 | 2032.5879 | 2025.4647
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 20.037 | 20.021 | 19.9908 | 20.1163 | 20.0945 | 20.0526 | 20.189 | 20.1625 | 20.1112 | 20.2346 | 20.2055 | 20.1486 | 20.2816 | 20.2498 | 20.1874 | 20.362 | 20.3259 | 20.2546
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1327609.7786 | 1326587.2864 | 1324687.1891 | 1332613.3614 | 1331213.466 | 1328560.5627 | 1337228.5372 | 1335522.9161 | 1332252.7517 | 1340141.142 | 1338256.1409 | 1334623.4931 | 1343140.5467 | 1341078.4263 | 1337088.5898 | 1348300.5574 | 1345946.1835 | 1341369.5042
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1327609.7786 | 1326587.2864 | 1324687.1891 | 1332613.3614 | 1331213.466 | 1328560.5627 | 1337228.5372 | 1335522.9161 | 1332252.7517 | 1340141.142 | 1338256.1409 | 1334623.4931 | 1343140.5467 | 1341078.4263 | 1337088.5898 | 1348300.5574 | 1345946.1835 | 1341369.5042
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 26.1911 | 31.6347 | 35.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3.9287 | 4.7452 | 5.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 3142.9283 | 3796.1589 | 4225.0539 | 3932659.3307 | 3842800.086 | 3673289.6566 | 4359709.4552 | 4242258.0967 | 4015396.5614 | 4736703.0264 | 4599136.5048 | 4329598.4627 | 4967148.6419 | 4818636.2898 | 4525778.1752 | 5198922.7469 | 5040161.1033 | 4725490.2715 | 5585579.1548 | 5410971.3232 | 5062725.6683
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 1257.1713 | 1518.4636 | 1690.0215 | 589898.8996 | 576420.0129 | 550993.4485 | 653956.4183 | 636338.7145 | 602309.4842 | 710505.454 | 689870.4757 | 649439.7694 | 745072.2963 | 722795.4435 | 678866.7263 | 779838.412 | 756024.1655 | 708823.5407 | 837836.8732 | 811645.6985 | 759408.8502
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 184829.0393 | 180605.7907 | 172639.057 | 204899.7491 | 199379.713 | 188717.564 | 222617.8767 | 216152.4583 | 203484.578 | 233448.472 | 226468.6161 | 212704.7277 | 244341.5043 | 236879.9472 | 222090.8941 | 262513.7705 | 254307.4666 | 237940.4476
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 913.5 |  |  |  | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'v'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 1152 |  |  |  | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 144 |  |  |  | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 245883.9675 | 240265.6452 | 229667.2451 | 272584.6731 | 265241.1928 | 251056.9959 | 296155.6634 | 287554.511 | 270702.0258 | 310563.9499 | 301278.4249 | 282967.8851 | 325055.2983 | 315128.9508 | 295454.6017 | 349230.4438 | 338313.3359 | 316539.7684
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 6826333.1759 | 21028.6958 | 23851.7409 | 338197.961 | 322919.2346 | 295058.8754 | 415636.2578 | 393543.2841 | 352578.0053 | 490626.0967 | 462541.741 | 409914.7751 | 539526.3298 | 507746.1336 | 447903.9151 | 591051.1398 | 555503.971 | 488306.0193 | 682236.1885 | 640248.833 | 560489.0355
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 2336.5218 | 2650.1934 | 758481.464 | 724215.6431 | 661732.812 | 932153.4533 | 882605.2213 | 790731.7975 | 1100334.2508 | 1037349.0596 | 919321.8012 | 1210003.5117 | 1138729.6056 | 1004520.5955 | 1325558.9491 | 1245836.7989 | 1095130.9796 | 1530060.978 | 1435895.328 | 1257016.8752
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 113772.2196 | 350.4783 | 397.529 | 94867.439 | 90581.6247 | 82766.5541 | 116589.5477 | 110392.2784 | 98901.1652 | 137624.843 | 129746.9395 | 114984.6226 | 151341.7793 | 142427.1607 | 125640.9033 | 165794.9319 | 155823.6451 | 136974.0413 | 191373.1229 | 179595.3083 | 157221.9986
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 72814.2205 | 224.3061 | 254.4186 | 829813.458 | 792325.0807 | 723966.0019 | 1019818.568 | 965610.5331 | 865096.7999 | 1203816.0628 | 1134907.379 | 1005780.153 | 1323799.2568 | 1245822.3393 | 1098991.5358 | 1450222.1974 | 1363002.514 | 1198123.4458 | 1673956.7827 | 1570935.249 | 1375234.0295
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 265521955.7201 | 265317457.2788 | 264937437.8115 | 266522672.2834 | 266242693.1949 | 265712112.5343 | 267445707.4345 | 267104583.2296 | 266450550.3487 | 268028228.3985 | 267651228.1743 | 266924698.6249 | 268628109.3405 | 268215685.2568 | 267417717.9548 | 269660111.4754 | 269189236.7034 | 268273900.8343
| Survey, Design, Supervision etc. | [5 empty] | 5075869.6502 | 5073824.6658 | 5070024.4711 | 5085876.8158 | 5083077.0249 | 5077771.2183 | 5095107.1673 | 5091695.9253 | 5085155.5965 | 5100932.377 | 5097162.3747 | 5089897.0792 | 5106931.1864 | 5102806.9456 | 5094827.2725 | 5117251.2077 | 5112542.46 | 5103389.1013
| TOTAL COST | [5 empty] | 270597825.3703 | 270391281.9446 | 270007462.2826 | 271608549.0992 | 271325770.2198 | 270789883.7526 | 272540814.6019 | 272196279.1549 | 271535705.9452 | 273129160.7755 | 272748390.5491 | 272014595.7041 | 273735040.5269 | 273318492.2023 | 272512545.2274 | 274777362.6832 | 274301779.1634 | 273377289.9356
| TOTAL COST IN RS. LAKHS | [5 empty] | 2705.9783 | 2703.9128 | 2700.0746 | 2716.0855 | 2713.2577 | 2707.8988 | 2725.4081 | 2721.9628 | 2715.3571 | 2731.2916 | 2727.4839 | 2720.146 | 2737.3504 | 2733.1849 | 2725.1255 | 2747.7736 | 2743.0178 | 2733.7729
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 27.0598 | 27.0391 | 27.0007 | 27.1609 | 27.1326 | 27.079 | 27.2541 | 27.2196 | 27.1536 | 27.3129 | 27.2748 | 27.2015 | 27.3735 | 27.3318 | 27.2513 | 27.4777 | 27.4302 | 27.3377
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1712558.0392 | 1711320.2556 | 1709039.2517 | 1718585.198 | 1716882.4072 | 1713681.3846 | 1724167.9778 | 1722086.2014 | 1718126.0456 | 1727700.4925 | 1725395.5539 | 1720987.9526 | 1731344.7014 | 1728818.9142 | 1723969.3781 | 1737627.3133 | 1734736.1845 | 1729158.6716
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1712558.0392 | 1711320.2556 | 1709039.2517 | 1718585.198 | 1716882.4072 | 1713681.3846 | 1724167.9778 | 1722086.2014 | 1718126.0456 | 1727700.4925 | 1725395.5539 | 1720987.9526 | 1731344.7014 | 1728818.9142 | 1723969.3781 | 1737627.3133 | 1734736.1845 | 1729158.6716
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 6.3189 | 7.4431 | 8.1777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5055.1374 | 5954.461 | 6542.1879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 4466355.9779 | 4363788.9858 | 4171712.5808 | 4950410.5574 | 4816120.7661 | 4558469.1697 | 5378296.6414 | 5220873.6849 | 4914382.1674 | 5640003.2716 | 5469996.4751 | 5136821.6372 | 5903292.6983 | 5721507.3444 | 5363383.6521 | 6342628.8988 | 6142642.8294 | 5746142.3674
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 669953.3967 | 654568.3479 | 625756.8871 | 742561.5836 | 722418.1149 | 683770.3754 | 806744.4962 | 783131.0527 | 737157.3251 | 846000.4907 | 820499.4713 | 770523.2456 | 885493.9047 | 858226.1017 | 804507.5478 | 951394.3348 | 921396.4244 | 861921.3551
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 209911.9744 | 205091.4809 | 196064.1804 | 232661.8073 | 226350.3903 | 214241.155 | 252771.806 | 245373.1652 | 230968.5275 | 265071.6217 | 257081.5594 | 241422.8461 | 277445.8265 | 268902.1898 | 252070.918 | 298093.9633 | 288694.9205 | 270059.9986
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 1152 |  |  |  | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 279252.5962 | 272839.74 | 260830.4342 | 309517.4248 | 301121.1453 | 285011.8434 | 336270.3975 | 326427.7496 | 307264.8006 | 352633.2348 | 342003.8001 | 321172.5141 | 369095.0341 | 357729.1618 | 335337.984 | 396563.9093 | 384060.0629 | 359269.4318
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 8804840.556 | 161099.2384 | 176969.7293 | 436219.4236 | 416414.4721 | 380563.462 | 535896.3109 | 507216.1438 | 454397.9619 | 632539.7686 | 596052.7593 | 528124.3403 | 695595.9469 | 654293.2259 | 577015.2661 | 762056.1373 | 715845.4197 | 629036.8079 | 879704.7459 | 825104.3145 | 722023.1042
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17899.9154 | 19663.3033 | 978315.6173 | 933898.7658 | 853495.1864 | 1201862.4158 | 1137540.9898 | 1019084.8883 | 1418606.0975 | 1336776.1536 | 1184432.1047 | 1560023.1016 | 1467392.8912 | 1294080.4919 | 1709074.3328 | 1605436.8875 | 1410749.9569 | 1972926.5709 | 1850473.3927 | 1619291.6699
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 146747.3426 | 2684.9873 | 2949.4955 | 122363.3029 | 116807.8435 | 106751.3266 | 150323.5277 | 142278.494 | 127462.5393 | 177432.8494 | 167197.9292 | 148143.423 | 195120.6501 | 183534.8814 | 161857.7486 | 213763.3056 | 200800.8016 | 176450.2388 | 246764.7529 | 231448.8619 | 202533.6952
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 93918.2993 | 1718.3919 | 1887.6771 | 1070322.0896 | 1021728.0199 | 933762.8218 | 1314892.5249 | 1244521.9392 | 1114925.5392 | 1552020.039 | 1462494.3328 | 1295822.9664 | 1706736.7181 | 1605395.0257 | 1415783.3236 | 1869805.5912 | 1756421.4796 | 1543425.0614 | 2158472.0233 | 2024502.6384 | 1771579.2461
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 342511607.8337 | 342264051.111 | 341807850.3345 | 343717039.6076 | 343376481.4386 | 342736276.9272 | 344833595.5507 | 344417240.2825 | 343625209.1101 | 345540098.4908 | 345079110.7852 | 344197590.5284 | 346268940.2856 | 345763782.8412 | 344793875.6221 | 347525462.6543 | 346947236.8997 | 345831734.3234
| Survey, Design, Supervision etc. | [5 empty] | 5845766.1713 | 5843290.6041 | 5838728.5963 | 5857820.4891 | 5854414.9074 | 5848012.8623 | 5868986.0485 | 5864822.4958 | 5856902.1841 | 5876051.0779 | 5871441.2008 | 5862625.9983 | 5883339.4958 | 5878287.9214 | 5868588.8492 | 5895904.7195 | 5890122.462 | 5878967.4362
| TOTAL COST | [5 empty] | 348357374.005 | 348107341.7151 | 347646578.9308 | 349574860.0966 | 349230896.346 | 348584289.7895 | 350702581.5992 | 350282062.7783 | 349482111.2941 | 351416149.5687 | 350950551.986 | 350060216.5267 | 352152279.7815 | 351642070.7626 | 350662464.4713 | 353421367.3739 | 352837359.3617 | 351710701.7596
| TOTAL COST IN RS. LAKHS | [5 empty] | 3483.5737 | 3481.0734 | 3476.4658 | 3495.7486 | 3492.309 | 3485.8429 | 3507.0258 | 3502.8206 | 3494.8211 | 3514.1615 | 3509.5055 | 3500.6022 | 3521.5228 | 3516.4207 | 3506.6246 | 3534.2137 | 3528.3736 | 3517.107
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 34.8357 | 34.8107 | 34.7647 | 34.9575 | 34.9231 | 34.8584 | 35.0703 | 35.0282 | 34.9482 | 35.1416 | 35.0951 | 35.006 | 35.2152 | 35.1642 | 35.0662 | 35.3421 | 35.2837 | 35.1711
ESTIMATE FOR A 765 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1018851.8782 | 1017502.6228 | 1014972.4076 | 1025812.2472 | 1023988.4188 | 1020510.6547 | 1032161.1827 | 1029958.3623 | 1025716.2284 | 1036141.7653 | 1033718.2595 | 1029030.8693 | 1040223.7099 | 1037583.2774 | 1032459.0848 | 1047211.7604 | 1044215.1328 | 1038376.523
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1018851.8782 | 1017502.6228 | 1014972.4076 | 1025812.2472 | 1023988.4188 | 1020510.6547 | 1032161.1827 | 1029958.3623 | 1025716.2284 | 1036141.7653 | 1033718.2595 | 1029030.8693 | 1040223.7099 | 1037583.2774 | 1032459.0848 | 1047211.7604 | 1044215.1328 | 1038376.523
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 33.1275 | 39.4561 | 43.6035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 4.9691 | 5.9184 | 6.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3975.2993 | 4734.735 | 5232.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 6019909.3047 | 5887557.213 | 5636266.8142 | 6685615.8414 | 6513836.1661 | 6181104.1598 | 7269979.0049 | 7069546.8351 | 6676617.3372 | 7626261.5822 | 7410232.8633 | 6984431.5722 | 7984130.4966 | 7753482.5438 | 7296902.5122 | 8580455.5749 | 8327164.9246 | 7823094.8627
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 902986.3957 | 883133.582 | 845440.0221 | 1002842.3762 | 977075.4249 | 927165.624 | 1090496.8507 | 1060432.0253 | 1001492.6006 | 1143939.2373 | 1111534.9295 | 1047664.7358 | 1197619.5745 | 1163022.3816 | 1094535.3768 | 1287068.3362 | 1249074.7387 | 1173464.2294
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 282926.6305 | 276706.2825 | 264896.0139 | 314213.8307 | 306140.4458 | 290502.5449 | 341678.0154 | 332258.0066 | 313790.9146 | 358422.7575 | 348269.7345 | 328257.718 | 375242.0551 | 364401.9503 | 342943.3795 | 403268.4317 | 391364.1543 | 367673.6239
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 609 |  |  |  | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 1920 |  |  |  | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 376386.3227 | 368111.1952 | 352399.6181 | 418008.6832 | 407268.4017 | 386464.8032 | 454545.1642 | 442013.426 | 417446.0644 | 476821.2289 | 463314.3385 | 436691.7145 | 499196.4771 | 484775.5398 | 456228.5185 | 536480.86 | 520644.22 | 489127.9516
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 10110602.5806 | 0 | 0 | 417425.8089 | 399272.76 | 365916.9175 | 514851.8022 | 488734.5743 | 440079.8917 | 608787.4826 | 575681.8706 | 513466.8054 | 669919.7725 | 632503.7611 | 561903.2378 | 734268.0888 | 692457.3475 | 613304.977 | 848047.3378 | 798718.4809 | 704947.2066
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1123400.2867 | 1074545.7598 | 984776.6027 | 1385598.7097 | 1315310.5274 | 1184368.2541 | 1638403.8022 | 1549308.0799 | 1381871.3268 | 1802926.5283 | 1702230.4116 | 1512226.2327 | 1976104.4091 | 1863580.9432 | 1650561.5423 | 2282313.6519 | 2149557.0021 | 1897194.3686
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 168510.043 | 0 | 0 | 93673.2258 | 89599.5566 | 82114.2759 | 115536.2895 | 109675.4037 | 98756.9579 | 136616.103 | 129186.9757 | 115225.4867 | 150334.6098 | 141938.1992 | 126094.9556 | 164774.815 | 155392.1968 | 137629.8598 | 190307.6619 | 179237.9268 | 158195.0072
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 107846.4275 | 0 | 0 | 737430.8175 | 705361.3635 | 646434.4221 | 909545.0671 | 863405.9728 | 777451.8666 | 1075493.2765 | 1017008.3962 | 907098.3106 | 1183490.5147 | 1117390.8168 | 992666.8527 | 1297169.2343 | 1223305.7393 | 1083473.9512 | 1498173.3954 | 1411028.2826 | 1245370.5154
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 203770375.6311 | 203500524.551 | 202994481.525 | 205162449.4385 | 204797683.7553 | 204102130.9406 | 206432236.5379 | 205991672.4539 | 205143245.6848 | 207228353.0697 | 206743651.8931 | 205806173.8578 | 208044741.9891 | 207516655.4806 | 206491816.9557 | 209442352.0883 | 208843026.5685 | 207675304.604
| Survey, Design, Supervision etc. | [5 empty] | 4458353.8493 | 4455655.3385 | 4450594.9082 | 4472274.5874 | 4468626.9305 | 4461671.4024 | 4484972.4584 | 4480566.8175 | 4472082.5498 | 4492933.6237 | 4488086.6119 | 4478711.8316 | 4501097.5129 | 4495816.6478 | 4485568.2625 | 4515073.6139 | 4509080.3587 | 4497403.139
| TOTAL COST | [5 empty] | 208228729.4804 | 207956179.8895 | 207445076.4333 | 209634724.0259 | 209266310.6859 | 208563802.343 | 210917208.9963 | 210472239.2714 | 209615328.2346 | 211721286.6934 | 211231738.505 | 210284885.6894 | 212545839.502 | 212012472.1284 | 210977385.2183 | 213957425.7022 | 213352106.9272 | 212172707.743
| TOTAL COST IN RS. LAKHS | [5 empty] | 2082.2873 | 2079.5618 | 2074.4508 | 2096.3472 | 2092.6631 | 2085.638 | 2109.1721 | 2104.7224 | 2096.1533 | 2117.2129 | 2112.3174 | 2102.8489 | 2125.4584 | 2120.1247 | 2109.7739 | 2139.5743 | 2133.5211 | 2121.7271
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 20.8229 | 20.7956 | 20.7445 | 20.9635 | 20.9266 | 20.8564 | 21.0917 | 21.0472 | 20.9615 | 21.1721 | 21.1232 | 21.0285 | 21.2546 | 21.2012 | 21.0977 | 21.3957 | 21.3352 | 21.2173
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1368704.1943 | 1367082.9137 | 1364103.1662 | 1376900.5767 | 1374703.4605 | 1370592.2039 | 1384392.5903 | 1381735.6603 | 1376711.0808 | 1389093.8178 | 1386169.3265 | 1380613.0985 | 1393916.5529 | 1390729.2205 | 1384651.8628 | 1402174.9747 | 1398556.3991 | 1391627.7028
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1368704.1943 | 1367082.9137 | 1364103.1662 | 1376900.5767 | 1374703.4605 | 1370592.2039 | 1384392.5903 | 1381735.6603 | 1376711.0808 | 1389093.8178 | 1386169.3265 | 1380613.0985 | 1393916.5529 | 1390729.2205 | 1384651.8628 | 1402174.9747 | 1398556.3991 | 1391627.7028
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 7142856.0815 | 6983337.2339 | 6686510.5709 | 7929272.5663 | 7721622.0606 | 7326915.7396 | 8621245.0377 | 8378603.2414 | 7911450.7189 | 9043561.9082 | 8781884.791 | 8275191.8837 | 9467959.7046 | 9188451.6777 | 8644766.4055 | 10175411.8588 | 9868311.4143 | 9267623.3067
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1071428.4122 | 1047500.5851 | 1002976.5856 | 1189390.8849 | 1158243.3091 | 1099037.3609 | 1293186.7556 | 1256790.4862 | 1186717.6078 | 1356534.2862 | 1317282.7187 | 1241278.7826 | 1420193.9557 | 1378267.7517 | 1296714.9608 | 1526311.7788 | 1480246.7122 | 1390143.496
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 335703.4303 | 328206.2858 | 314255.8816 | 372663.8154 | 362904.5558 | 344353.9558 | 405185.4747 | 393781.6774 | 371826.2155 | 425033.7288 | 412735.3001 | 388921.5 | 444979.7832 | 431843.3288 | 406290.9435 | 478228.9642 | 463795.7079 | 435564.2756
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 913.5 |  |  |  | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 1920 |  |  |  | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 446596.9831 | 436623.2925 | 418064.6249 | 495766.5625 | 482783.5081 | 458105.0531 | 539031.1635 | 523860.328 | 494652.2767 | 565435.929 | 549074.9371 | 517394.679 | 591970.8015 | 574494.9571 | 540501.8038 | 636203.2478 | 617002.2265 | 579445.0514
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 11903669.7617 | 0 | 0 | 491454.2867 | 469748.4528 | 430663.8307 | 605628.106 | 574323.266 | 517108.5544 | 715944.4158 | 676211.5413 | 602908.7438 | 787804.3234 | 742873.3842 | 659622.5192 | 863479.6957 | 813249.8642 | 719856.3715 | 997340.1927 | 938047.9099 | 827324.8593
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1322629.9735 | 1264213.9878 | 1159027.2104 | 1629901.1065 | 1545651.725 | 1391672.2106 | 1926790.6889 | 1819859.2973 | 1622582.603 | 2120184.1951 | 1999263.4737 | 1775213.9693 | 2323846.0991 | 2188664.6944 | 1937318.7685 | 2684099.1487 | 2524528.3554 | 2226544.129
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 198394.496 | 0 | 0 | 110285.7259 | 105414.7873 | 96643.929 | 135907.1171 | 128882.0955 | 116042.7202 | 160662.8566 | 151746.526 | 135296.8735 | 176788.7147 | 166705.9026 | 148023.8352 | 193770.7893 | 182498.8693 | 161540.7264 | 223810.0066 | 210504.41 | 185657.3951
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 126972.4775 | 0 | 0 | 868210.6584 | 829864.8002 | 760817.3091 | 1069911.8734 | 1014608.2643 | 913531.8799 | 1264798.3533 | 1194605.6496 | 1065107.8066 | 1391747.165 | 1312371.4807 | 1165299.2295 | 1525436.435 | 1436699.6464 | 1271709.2741 | 1761916.436 | 1657169.7825 | 1461564.7482
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 273740838.8589 | 273416582.7326 | 272820633.2495 | 275380115.3395 | 274940692.0916 | 274118440.7819 | 276878518.0535 | 276347132.0545 | 275342216.1532 | 277818763.5578 | 277233865.2954 | 276122619.7058 | 278783310.5715 | 278145844.0968 | 276930372.5613 | 280434994.9408 | 279711279.8261 | 278325540.5685
| Survey, Design, Supervision etc. | [5 empty] | 5158058.4816 | 5154815.9203 | 5148856.4255 | 5174451.2464 | 5170057.0139 | 5161834.5008 | 5189435.2735 | 5184121.4135 | 5174072.2545 | 5198837.7286 | 5192988.7459 | 5181876.29 | 5208483.1987 | 5202108.534 | 5189953.8186 | 5225000.0424 | 5217762.8912 | 5203905.4987
| TOTAL COST | [5 empty] | 278898897.3405 | 278571398.6529 | 277969489.675 | 280554566.5859 | 280110749.1055 | 279280275.2827 | 282067953.327 | 281531253.468 | 280516288.4077 | 283017601.2863 | 282426854.0414 | 281304495.9958 | 283991793.7702 | 283347952.6308 | 282120326.3799 | 285659994.9832 | 284929042.7173 | 283529446.0672
| TOTAL COST IN RS. LAKHS | [5 empty] | 2788.989 | 2785.714 | 2779.6949 | 2805.5457 | 2801.1075 | 2792.8028 | 2820.6795 | 2815.3125 | 2805.1629 | 2830.176 | 2824.2685 | 2813.045 | 2839.9179 | 2833.4795 | 2821.2033 | 2856.5999 | 2849.2904 | 2835.2945
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 27.8899 | 27.8571 | 27.7969 | 28.0555 | 28.0111 | 27.928 | 28.2068 | 28.1531 | 28.0516 | 28.3018 | 28.2427 | 28.1304 | 28.3992 | 28.3348 | 28.212 | 28.566 | 28.4929 | 28.3529
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1851791.5536 | 1849681.7923 | 1845856.1206 | 1862392.2373 | 1859506.9458 | 1854179.0787 | 1872162.6837 | 1868649.087 | 1862091.1682 | 1878327.3243 | 1874444.7609 | 1867164.2155 | 1884675.5157 | 1880428.3217 | 1872435.1349 | 1895597.7613 | 1890748.1823 | 1881582.5523
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1851791.5536 | 1849681.7923 | 1845856.1206 | 1862392.2373 | 1859506.9458 | 1854179.0787 | 1872162.6837 | 1868649.087 | 1862091.1682 | 1878327.3243 | 1874444.7609 | 1867164.2155 | 1884675.5157 | 1880428.3217 | 1872435.1349 | 1895597.7613 | 1890748.1823 | 1881582.5523
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8111811.0163 | 7929102.5915 | 7592848.1894 | 9002736.6774 | 8764521.2587 | 8316329.7119 | 9787703.3704 | 9509126.779 | 8978022.3819 | 10267042.3324 | 9966516.4364 | 9390171.2997 | 10748868.8776 | 10427789.6464 | 9809137.8897 | 11552220.3544 | 11199351.082 | 10515553.7314
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1216771.6524 | 1189365.3887 | 1138927.2284 | 1350410.5016 | 1314678.1888 | 1247449.4568 | 1468155.5056 | 1426369.0169 | 1346703.3573 | 1540056.3499 | 1494977.4655 | 1408525.695 | 1612330.3316 | 1564168.447 | 1471370.6835 | 1732833.0532 | 1679902.6623 | 1577333.0597
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 381242.8464 | 372655.8268 | 356852.3786 | 423115.0047 | 411919.2404 | 390854.9157 | 460007.2518 | 446914.5734 | 421953.4702 | 482535.4579 | 468411.1954 | 441323.8458 | 505180.5766 | 490090.3385 | 461014.6418 | 542936.8807 | 526352.5587 | 494215.1177
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 1920 |  |  |  | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 163660.9478 | 100 |  |  |  | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 507179.5212 | 495755.9351 | 474732.1037 | 562883.3892 | 547989.3067 | 519966.7636 | 611962.3224 | 594544.7147 | 561338.1628 | 641932.3137 | 623142.3567 | 587107.1915 | 672057.8376 | 651982.8123 | 613302.4855 | 722286.2535 | 700223.6008 | 657470.1377
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 18358313.9123 | 0 | 0 | 757940.3873 | 724181.5816 | 664062.3139 | 933573.4582 | 884821.7681 | 796641.2663 | 1103471.1901 | 1041551.3259 | 928454.8056 | 1214199.6582 | 1144158.4584 | 1015655.5143 | 1330837.1975 | 1252517.8521 | 1108309.5618 | 1537199.8363 | 1444724.7722 | 1273689.8695
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 2039812.6569 | 1948959.0221 | 1787162.5997 | 2512486.4542 | 2381283.1087 | 2143966.683 | 2969724.9783 | 2803082.6871 | 2498710.8426 | 3267723.7846 | 3079224.8891 | 2733390.3932 | 3581625.4223 | 3370847.9064 | 2982746.2817 | 4137000.396 | 3888126.1976 | 3427827.2546
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 305971.8985 | 0 | 0 | 170087.0418 | 162511.3334 | 149020.1557 | 209500.3123 | 198560.0973 | 178771.7856 | 247626.5332 | 233731.2893 | 208351.6514 | 272474.7638 | 256757.0363 | 227920.0909 | 298649.0308 | 281073.6304 | 248712.2971 | 344958.2279 | 324206.1867 | 285824.7769
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 195822.0151 | 0 | 0 | 1338989.0788 | 1279350.2564 | 1173142.6388 | 1649265.1477 | 1563139.6664 | 1407358.6435 | 1949409.0791 | 1840020.5001 | 1640222.4577 | 2145023.684 | 2021287.8294 | 1794272.5633 | 2351077.3446 | 2212717.1913 | 1957956.6204 | 2715640.7381 | 2552272.8756 | 2250120.0011
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 370358310.7164 | 369936358.4509 | 369171224.1235 | 372478447.4604 | 371901389.1503 | 370835815.7417 | 374432536.7461 | 373729817.4016 | 372418233.6445 | 375665464.8597 | 374888952.1826 | 373432843.1089 | 376935103.1338 | 376085664.3396 | 374487026.9766 | 379119552.2553 | 378149636.4512 | 376316510.464
| Survey, Design, Supervision etc. | [5 empty] | 6124233.2002 | 6120013.6775 | 6112362.3342 | 6145434.5676 | 6139663.9845 | 6129008.2504 | 6164975.4604 | 6157948.267 | 6144832.4294 | 6177304.7416 | 6169539.6148 | 6154978.5241 | 6190001.1243 | 6181506.7364 | 6165520.3628 | 6211845.6155 | 6202146.4575 | 6183815.1976
| TOTAL COST | [5 empty] | 376482543.9165 | 376056372.1284 | 375283586.4578 | 378623882.028 | 378041053.1348 | 376964823.9921 | 380597512.2065 | 379887765.6686 | 378563066.0739 | 381842769.6013 | 381058491.7974 | 379587821.6329 | 383125104.2581 | 382267171.076 | 380652547.3393 | 385331397.8709 | 384351782.9087 | 382500325.6616
| TOTAL COST IN RS. LAKHS | [5 empty] | 3764.8254 | 3760.5637 | 3752.8359 | 3786.2388 | 3780.4105 | 3769.6482 | 3805.9751 | 3798.8777 | 3785.6307 | 3818.4277 | 3810.5849 | 3795.8782 | 3831.251 | 3822.6717 | 3806.5255 | 3853.314 | 3843.5178 | 3825.0033
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 37.6483 | 37.6056 | 37.5284 | 37.8624 | 37.8041 | 37.6965 | 38.0598 | 37.9888 | 37.8563 | 38.1843 | 38.1058 | 37.9588 | 38.3125 | 38.2267 | 38.0653 | 38.5331 | 38.4352 | 38.25
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 13309062.3407 | 13941842.3508 | 14341910.5814
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 12243.3706 | 13283.528 | 13922.4666 | 734602.2359 | 797011.6778 | 835347.9947
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 282821.8608 | 306849.4959 | 321608.978
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) x No. of Ckts. | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 2436 |  |  |  | 876960000 | 876960000 | 876960000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 21000 | 1680 |  |  |  | 35280000 | 35280000 | 35280000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 40 |  |  |  | 1240000 | 1240000 | 1240000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 840 |  |  |  | 49560000 | 49560000 | 49560000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 40 |  |  |  | 1800000 | 1800000 | 1800000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 812 |  |  |  | 1055600 | 1055600 | 1055600
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 5040 | 10080 |  |  |  | 50803200 | 50803200 | 50803200
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 1680 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 0 |  |  |  | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 380000 | 100 |  |  |  | 38000000 | 38000000 | 38000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 484837.4757 | 526027.7073 | 551329.6765
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 110476.1386 | 135501.5486 | 151914.4961 | 33142841.5799 | 40650464.5715 | 45574348.8348
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 12275.1265 | 15055.7276 | 16879.3885 | 69968221.113 | 85817647.4288 | 96212514.2067
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 1841.269 | 2258.3591 | 2531.9083 | 8653964.1903 | 10614287.9715 | 11899968.8624
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 1178.4121 | 1445.3499 | 1620.4213 | 63634255.8333 | 78048891.9773 | 87502749.7628
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 1565772040.0812 | 1640216747.1546 | 1687283597.8152
| Survey, Design, Supervision etc. | [5 empty] | 34966782.7415 | 36344009.8224 | 37214746.5596
| TOTAL COST | [5 empty] | 1600738822.8227 | 1676560756.9769 | 1724498344.3747
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 288132988.1081 | 301780936.2558 | 310409701.9875
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
v) | Contengency at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1984916140.3001 | 2078935338.6514 | 2138377947.0247
| TOTAL COST IN RS. LAKHS | [5 empty] | 19849.1614 | 20789.3534 | 21383.7795
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 198.4916 | 207.8935 | 213.8378
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 8411202.1434 | 8912246.9919 | 9223024.2025
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
III | Detailed survey (Rs. Per kM) | 50000 | 100 |  |  |  | 5000000 | 5000000 | 5000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 520753.4201 | 578395.2043 | 613278.8096 | 31245205.2042 | 34703712.2574 | 36796728.5749
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 12029404.0036 | 13360929.2191 | 14166740.5013
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 1218 |  |  |  | 438480000 | 438480000 | 438480000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of suspn.x1) | 24000 | 210 |  |  |  | 5040000 | 5040000 | 5040000
| b) Double 'I' Suspension Insulator Sring (No. Suspn. X 2) | 21000 | 420 |  |  |  | 8820000 | 8820000 | 8820000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'V' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
| f) Single 'I' Suspension Pilot strings (No. of Suspn x 1) | 15000 | 210 |  |  |  | 3150000 | 3150000 | 3150000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 406 |  |  |  | 527800 | 527800 | 527800
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 2700 | 5040 |  |  |  | 13608000 | 13608000 | 13608000
| f) Quad Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 1000 | 840 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190000 | 100 |  |  |  | 19000000 | 19000000 | 19000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 20621835.4348 | 22904450.0899 | 24285840.8595
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 48382.6073 | 59272.006 | 66421.8968 | 14514782.1992 | 17781601.804 | 19926569.0329
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 5375.8453 | 6585.7784 | 7380.2108 | 30642317.976 | 37538937.1417 | 42067201.2916
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 806.3768 | 987.8668 | 1107.0316 | 3789970.9076 | 4642973.8044 | 5203048.5808
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 516.0811 | 632.2347 | 708.5002 | 27868381.8224 | 34140675.4636 | 38259012.5431
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 989553193.3401 | 1048499646.1046 | 1085061670.8834
| Survey, Design, Supervision etc. | [5 empty] | 23306734.0768 | 24397243.4529 | 25073640.9113
| TOTAL COST | [5 empty] | 1012859927.4169 | 1072896889.5575 | 1110135311.7948
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 182314786.935 | 193121440.1204 | 199824356.1231
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
v) | Contengency at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1255946309.997 | 1330392143.0513 | 1376567786.6255
| TOTAL COST IN RS. LAKHS | [5 empty] | 12559.4631 | 13303.9214 | 13765.6779
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 125.5946 | 133.0392 | 137.6568
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 5050227.0344 | 5357651.6793 | 5546861.9223
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 10366.8386 | 11627.9013 | 12386.9423 | 130622166.4713 | 146511556.3957 | 156075473.2845
| b) 'B' Type towers | 60000 | 25 | 16898.4575 | 18612.4108 | 19653.708 | 25347686.3224 | 27918616.1635 | 29480562.0497
| c) 'C' Type towers | 60000 | 25 | 20290.3432 | 22180.6901 | 23333.1622 | 30435514.7251 | 33271035.0929 | 34999743.239
| d) 'D' Type towers | 60000 | 20 | 25560.0611 | 27781.5378 | 29139.1942 | 30672073.3304 | 33337845.351 | 34967032.9907
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 361795.7347 | 401731.755 | 425871.3526 | 21707744.0849 | 24103905.3003 | 25552281.1564
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 7163555.548 | 7954288.7491 | 8432252.7816
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 609 |  |  |  | 219240000 | 219240000 | 219240000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) | 21000 | 840 |  |  |  | 17640000 | 17640000 | 17640000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 203 |  |  |  | 263900 | 263900 | 263900
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 900 | 5040 |  |  |  | 4536000 | 4536000 | 4536000
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 840 |  |  |  | 420000 | 420000 | 420000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 3360 |  |  |  | 3024000 | 3024000 | 3024000
V | ERECTION
2 | Stringing of Conductor (Route kM) | 95000 | 100 |  |  |  | 9500000 | 9500000 | 9500000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 12280380.9395 | 13635923.5699 | 14455290.4828
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 21646.7931 | 26473.7232 | 29642.2493 | 6494037.9255 | 7942116.9663 | 8892674.7876
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 2405.1992 | 2941.5248 | 3293.5833 | 13709635.6204 | 16766691.3734 | 18773424.5515
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 360.7799 | 441.2287 | 494.0375 | 1695665.4583 | 2073774.9857 | 2321976.1945
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 230.8991 | 282.3864 | 316.184 | 12468552.8169 | 15248864.5753 | 17073935.5921
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 594144356.9927 | 630311962.2731 | 652571990.8604
| Survey, Design, Supervision etc. | [5 empty] | 16991670.6044 | 17660771.3021 | 18072581.8309
| TOTAL COST | [5 empty] | 611136027.5971 | 647972733.5751 | 670644572.6913
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 110004484.9675 | 116635092.0435 | 120716023.0844
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
v) | Contengency at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 757808674.2204 | 803486189.6332 | 831599270.1372
| TOTAL COST IN RS. LAKHS | [5 empty] | 7578.0867 | 8034.8619 | 8315.9927
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 75.7809 | 80.3486 | 83.1599

## Moose-Antifog-Plain
CERC
Capital Cost Benchmarking
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
I | Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1634798.2139 | 1633551.909 | 1630470.4671 | 1643169.023 | 1641488.8055 | 1637264.5057 | 1650812.9331 | 1648784.9655 | 1643638.2593 | 1655610.3593 | 1653378.9392 | 1647693.2444 | 1660534.3462 | 1658102.1473 | 1651886.0113 | 1668974.8797 | 1666211.2957 | 1659123.5998
III | Detailed survey (Rs. Per km) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1634798.2139 | 1633551.909 | 1630470.4671 | 1643169.023 | 1641488.8055 | 1637264.5057 | 1650812.9331 | 1648784.9655 | 1643638.2593 | 1655610.3593 | 1653378.9392 | 1647693.2444 | 1660534.3462 | 1658102.1473 | 1651886.0113 | 1668974.8797 | 1666211.2957 | 1659123.5998
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 10366.8386 | 11627.9013 | 12386.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 16898.4575 | 18612.4108 | 19653.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 20290.3432 | 22180.6901 | 23333.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 25560.0611 | 27781.5378 | 29139.1942 | 6713449.1742 | 6598109.0913 | 6309276.5083 | 7467581.5258 | 7318955.0922 | 6939279.0957 | 8127742.3112 | 7955060.3041 | 7508853.8293 | 8529587.207 | 8343816.2595 | 7861380.4186 | 8932824.5617 | 8734772.7986 | 8218426.5393 | 9604040.2607 | 9386927.1116 | 8818212.4665
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 10224.0244 | 11112.6151 | 11655.6777 | 1007017.3761 | 989716.3637 | 946391.4763 | 1120137.2289 | 1097843.2638 | 1040891.8644 | 1219161.3467 | 1193259.0456 | 1126328.0744 | 1279438.0811 | 1251572.4389 | 1179207.0628 | 1339923.6842 | 1310215.9198 | 1232763.9809 | 1440606.0391 | 1408039.0667 | 1322731.87
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 315521.9552 | 310101.1458 | 296526.4514 | 350965.0349 | 343979.8174 | 326135.6199 | 381991.5932 | 373875.8001 | 352904.7708 | 400877.6954 | 392146.7419 | 369472.9872 | 419829.241 | 410521.1078 | 386253.6147 | 451375.3635 | 441171.3739 | 414442.6459
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 419748.923 | 412537.4473 | 394478.5982 | 466899.9826 | 457607.3249 | 433868.6197 | 508175.6029 | 497378.9044 | 469480.4751 | 533300.3871 | 521685.3211 | 491521.7019 | 558512.2329 | 546129.3263 | 513845.5061 | 600479.046 | 586904.3532 | 551346.2736
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 10308786.5814 | 2915.0868 | 3206.9634 | 510729.6279 | 493331.2484 | 451085.3928 | 631916.3422 | 607012.7406 | 545667.8315 | 748582.1956 | 717111.3464 | 638920.6756 | 824433.5736 | 788912.987 | 700321.1897 | 904226.5423 | 864575.3868 | 765379.8013 | 1045219.6978 | 998496.4681 | 881172.1424
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 323.8985 | 356.3293 | 1145420.7313 | 1106401.1338 | 1011655.7417 | 1417207.9302 | 1361356.2622 | 1223777.1465 | 1678856.1287 | 1608275.9997 | 1432916.65 | 1848969.1125 | 1769306.5786 | 1570620.472 | 2027921.9588 | 1938995.7382 | 1716528.3623 | 2344129.35 | 2239342.4861 | 1976217.5222
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 171813.1097 | 48.5848 | 53.4494 | 143264.0565 | 138383.6613 | 126533.3352 | 177257.9729 | 170272.2983 | 153064.5233 | 209983.749 | 201155.9049 | 179222.7487 | 231260.7133 | 221296.8831 | 196446.1214 | 253643.3279 | 242520.8375 | 214695.6219 | 293193.1215 | 280086.8534 | 247176.3702
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 109960.3902 | 31.0943 | 34.2076 | 1253142.7372 | 1210453.5106 | 1106797.7126 | 1550490.38 | 1489386.0973 | 1338868.244 | 1836745.492 | 1759527.5984 | 1567676.4389 | 2022856.8869 | 1935702.4266 | 1718330.7266 | 2218639.4963 | 2121350.1385 | 1877960.6408 | 2564584.8638 | 2449943.2357 | 2162072.4748
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 326959642.7822 | 326710381.803 | 326094093.4172 | 328633804.5984 | 328297761.0975 | 327452901.1457 | 330162586.6199 | 329756993.1043 | 328727651.8636 | 331122071.8577 | 330675787.8375 | 329538648.8808 | 332106869.2459 | 331620429.4542 | 330377202.268 | 333794975.9432 | 333242259.1495 | 331824719.9664
| Survey, Design, Supervision etc. | [5 empty] | 5690246.5208 | 5687753.911 | 5681591.0272 | 5706988.139 | 5703627.704 | 5695179.1044 | 5722275.9592 | 5718220.024 | 5707926.6116 | 5731870.8116 | 5727407.9714 | 5716036.5818 | 5741718.7854 | 5736854.3875 | 5724422.1157 | 5758599.8524 | 5753072.6845 | 5738897.2927
| TOTAL COST | [5 empty] | 332649889.303 | 332398135.7141 | 331775684.4444 | 334340792.7374 | 334001388.8014 | 333148080.2502 | 335884862.5791 | 335475213.1284 | 334435578.4752 | 336853942.6693 | 336403195.8089 | 335254685.4626 | 337848588.0314 | 337357283.8418 | 336101624.3837 | 339553575.7956 | 338995331.834 | 337563617.2591
| TOTAL COST IN RS. LAKHS | [5 empty] | 3326.4989 | 3323.9814 | 3317.7568 | 3343.4079 | 3340.0139 | 3331.4808 | 3358.8486 | 3354.7521 | 3344.3558 | 3368.5394 | 3364.032 | 3352.5469 | 3378.4859 | 3373.5728 | 3361.0162 | 3395.5358 | 3389.9533 | 3375.6362
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 33.265 | 33.2398 | 33.1776 | 33.4341 | 33.4001 | 33.3148 | 33.5885 | 33.5475 | 33.4436 | 33.6854 | 33.6403 | 33.5255 | 33.7849 | 33.7357 | 33.6102 | 33.9554 | 33.8995 | 33.7564
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2331824.1007 | 2330190.9836 | 2326185.762 | 2342742.1394 | 2340526.167 | 2334998.709 | 2352768.2586 | 2350081.0986 | 2343314.2009 | 2359083.182 | 2356118.9174 | 2348623.9463 | 2365580.3539 | 2362341.7232 | 2354127.8086 | 2376750.2857 | 2373057.1183 | 2363657.3924
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2331824.1007 | 2330190.9836 | 2326185.762 | 2342742.1394 | 2340526.167 | 2334998.709 | 2352768.2586 | 2350081.0986 | 2343314.2009 | 2359083.182 | 2356118.9174 | 2348623.9463 | 2365580.3539 | 2362341.7232 | 2354127.8086 | 2376750.2857 | 2373057.1183 | 2363657.3924
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 39.6672 | 47.4027 | 52.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5.9501 | 7.1104 | 7.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4760.065 | 5688.3225 | 6294.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8071596.8224 | 7932218.9887 | 7585524.2727 | 8976104.3948 | 8796179.1737 | 8339381.5223 | 9768964.9637 | 9559735.8178 | 9022265.8025 | 10251848.7038 | 10026682.7192 | 9445301.6091 | 10736524.8785 | 10496412.8929 | 9873953.1559 | 11543450.8439 | 11280154.7492 | 10594306.1139
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1210739.5234 | 1189832.8483 | 1137828.6409 | 1346415.6592 | 1319426.8761 | 1250907.2283 | 1465344.7446 | 1433960.3727 | 1353339.8704 | 1537777.3056 | 1504002.4079 | 1416795.2414 | 1610478.7318 | 1574461.9339 | 1481092.9734 | 1731517.6266 | 1692023.2124 | 1589145.9171
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 379352.8401 | 372802.2928 | 356508.1656 | 421863.3277 | 413407.1145 | 391938.3159 | 459126.575 | 449293.1217 | 424032.844 | 481821.3803 | 471238.9197 | 443914.887 | 504600.4273 | 493315.5272 | 464060.8612 | 542524.727 | 530150.2089 | 497916.3605
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1827 |  |  |  | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 609 |  |  |  | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 288 |  |  |  | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 504665.1855 | 495950.7834 | 474274.1862 | 561218.2433 | 549968.6731 | 521408.0455 | 610790.73 | 597708.9733 | 564104.4201 | 640982.3535 | 626904.1685 | 590554.1361 | 671286.0465 | 656273.3839 | 617354.9684 | 721737.9522 | 705275.7359 | 662394.0192
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 14901674.0408 | 154.5809 | 171.1442 | 738275.6814 | 712999.1838 | 652034.9069 | 913009.784 | 876774.2288 | 788074.5956 | 1081425.848 | 1035598.5251 | 922424.6007 | 1190978.7653 | 1139237.2761 | 1010953.7851 | 1306252.4298 | 1248479.6096 | 1104795.1696 | 1509979.1743 | 1441882.122 | 1271875.7191
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17.1757 | 19.016 | 1655741.5601 | 1599053.593 | 1462328.1266 | 2047620.2621 | 1966354.2576 | 1767426.306 | 2425329.4071 | 2322551.8067 | 2068735.0076 | 2671025.3211 | 2554983.934 | 2267280.6913 | 2929551.2374 | 2799983.2972 | 2477740.1231 | 3386452.1572 | 3233729.9121 | 2852454.0907
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 248361.234 | 2.5763 | 2.8524 | 207092.683 | 200002.4079 | 182901.4035 | 256107.1027 | 245942.7176 | 221061.7071 | 303349.2582 | 290494.2998 | 258748.0398 | 334079.7945 | 319565.8614 | 283581.238 | 366415.0495 | 350209.2762 | 309904.5541 | 423562.1549 | 404460.3456 | 356772.0863
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 158951.1898 | 1.6489 | 1.8255 | 1811457.0953 | 1749437.8631 | 1599853.9412 | 2240190.3423 | 2151281.6116 | 1933645.3222 | 2653421.4451 | 2540978.0432 | 2263290.8409 | 2922224.0272 | 2795269.4353 | 2480508.9117 | 3205063.2194 | 3063309.9589 | 2710761.1686 | 3704933.7505 | 3537848.62 | 3120715.4101
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 466364820.1469 | 466038196.7167 | 465237152.3995 | 468548427.8721 | 468105233.4088 | 466999741.7988 | 470553651.7275 | 470016219.716 | 468662840.1818 | 471816636.4071 | 471223783.4778 | 469724789.2555 | 473116070.776 | 472468344.6358 | 470825561.73 | 475350057.1423 | 474611423.6619 | 472731478.4727
| Survey, Design, Supervision etc. | [5 empty] | 7084298.2945 | 7081032.0602 | 7073021.617 | 7106134.3717 | 7101702.4271 | 7090647.511 | 7126186.6103 | 7120812.2901 | 7107278.4948 | 7138816.4571 | 7132887.9278 | 7117897.9855 | 7151810.8007 | 7145333.5393 | 7128905.7103 | 7174150.6644 | 7166764.3296 | 7147964.8777
| TOTAL COST | [5 empty] | 473449118.4414 | 473119228.7769 | 472310174.0164 | 475654562.2438 | 475206935.8359 | 474090389.3098 | 477679838.3378 | 477137032.0062 | 475770118.6766 | 478955452.8642 | 478356671.4055 | 476842687.241 | 480267881.5767 | 479613678.1751 | 477954467.4403 | 482524207.8067 | 481778187.9915 | 479879443.3504
| TOTAL COST IN RS. LAKHS | [5 empty] | 4734.4912 | 4731.1923 | 4723.1017 | 4756.5456 | 4752.0694 | 4740.9039 | 4776.7984 | 4771.3703 | 4757.7012 | 4789.5545 | 4783.5667 | 4768.4269 | 4802.6788 | 4796.1368 | 4779.5447 | 4825.2421 | 4817.7819 | 4798.7944
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 47.3449 | 47.3119 | 47.231 | 47.5655 | 47.5207 | 47.409 | 47.768 | 47.7137 | 47.577 | 47.8955 | 47.8357 | 47.6843 | 48.0268 | 47.9614 | 47.7954 | 48.2524 | 48.1778 | 47.9879
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 3073096.5719 | 3071166.254 | 3066456.251 | 3085991.6662 | 3083356.1605 | 3076815.8785 | 3097898.4072 | 3094687.5087 | 3086643.0818 | 3105424.8974 | 3101873.6892 | 3092940.5545 | 3113187.9878 | 3109298.6124 | 3099484.611 | 3126575.5054 | 3122123.5986 | 3110850.4664
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 3073096.5719 | 3071166.254 | 3066456.251 | 3085991.6662 | 3083356.1605 | 3076815.8785 | 3097898.4072 | 3094687.5087 | 3086643.0818 | 3105424.8974 | 3101873.6892 | 3092940.5545 | 3113187.9878 | 3109298.6124 | 3099484.611 | 3126575.5054 | 3122123.5986 | 3110850.4664
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 4795.5834 | 6031.7 | 6844.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8616590.2871 | 8467404.143 | 8097622.1029 | 9580934.9506 | 9388165.7809 | 8900348.7823 | 10426848.0245 | 10202580.5495 | 9628258.4602 | 10942191.8119 | 10700798.4613 | 10079401.2181 | 11459515.8602 | 11202065.2527 | 10536641.663 | 12320881.171 | 12038530.5157 | 11305197.1335
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1292488.5431 | 1270110.6215 | 1214643.3154 | 1437140.2426 | 1408224.8671 | 1335052.3173 | 1564027.2037 | 1530387.0824 | 1444238.769 | 1641328.7718 | 1605119.7692 | 1511910.1827 | 1718927.379 | 1680309.7879 | 1580496.2495 | 1848132.1756 | 1805779.5774 | 1695779.57
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 404966.7085 | 397955.1854 | 380575.9889 | 450289.4489 | 441229.5895 | 418302.9285 | 490046.0837 | 479505.8516 | 452513.5822 | 514266.4621 | 502921.3398 | 473716.6094 | 538579.9097 | 526480.1206 | 495206.2186 | 579062.7763 | 565792.7226 | 531327.163
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 2436 |  |  |  | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 4608 |  |  |  | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 812 |  |  |  | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 384 |  |  |  | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 538740.1318 | 529412.4789 | 506292.3794 | 599034.4192 | 586981.7992 | 556481.7307 | 651923.9388 | 637901.9318 | 601993.2547 | 684145.0808 | 669052.3027 | 630200.3182 | 716490.0359 | 700393.3005 | 658788.6309 | 770345.6848 | 752692.1091 | 706841.4756
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 19494561.5001 | 85.5822 | 93.9493 | 965821.7349 | 932667.1191 | 852984.4211 | 1194103.2258 | 1146535.7169 | 1030481.3597 | 1414269.5003 | 1354085.7038 | 1205928.5257 | 1557523.957 | 1489561.5651 | 1321586.3805 | 1708278.3172 | 1632383.8324 | 1444210.5378 | 1974738.6508 | 1885267.776 | 1662579.2959
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 9.5091 | 10.4388 | 2166062.3889 | 2091706.0522 | 1913000.5115 | 2678032.5939 | 2571352.2531 | 2311075.4656 | 3171802.6855 | 3036827.6137 | 2704553.3652 | 3493081.5298 | 3340661.2893 | 2963940.9107 | 3831180.516 | 3660970.8562 | 3238951.8839 | 4428774.9644 | 4228117.338 | 3728690.6593
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 324909.3583 | 1.4264 | 1.5658 | 270921.3095 | 261621.1544 | 239269.4718 | 334956.2326 | 321613.1369 | 289058.8908 | 396714.7675 | 379832.6946 | 338273.331 | 436898.8757 | 417834.8398 | 370716.3547 | 479186.7712 | 457897.715 | 405113.4863 | 553931.1882 | 528833.8378 | 466367.8024
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 207941.9893 | 0.91288 | 1.0021 | 2369771.4534 | 2288422.2156 | 2092910.1699 | 2929890.3046 | 2813177.1259 | 2528422.4005 | 3470097.3981 | 3322428.488 | 2958905.2429 | 3821591.1675 | 3654836.444 | 3242687.0969 | 4191486.9424 | 4005269.7794 | 3543561.6963 | 4845282.6372 | 4625754.0043 | 4079358.3454
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 614619314.3885 | 614233250.8016 | 613291250.1922 | 617198333.2495 | 616671232.101 | 615363175.7069 | 619579681.4335 | 618937501.7469 | 617328616.3625 | 621084979.4879 | 620374737.8425 | 618588110.9025 | 622637597.5632 | 621859722.4762 | 619896922.1976 | 625315101.0798 | 624424719.7123 | 622170093.2766
| Survey, Design, Supervision etc. | [5 empty] | 8566843.2369 | 8562982.601 | 8553562.5949 | 8592633.4255 | 8587362.414 | 8574281.8501 | 8616446.9073 | 8610025.1105 | 8593936.2566 | 8631499.8879 | 8624397.4714 | 8606531.202 | 8647026.0686 | 8639247.3178 | 8619619.315 | 8673801.1038 | 8664897.2901 | 8642351.0258
| TOTAL COST | [5 empty] | 623186157.6254 | 622796233.4026 | 621844812.7872 | 625790966.6749 | 625258594.515 | 623937457.557 | 628196128.3408 | 627547526.8573 | 625922552.6191 | 629716479.3758 | 628999135.3139 | 627194642.1045 | 631284623.6319 | 630498969.794 | 628516541.5126 | 633988902.1836 | 633089617.0024 | 630812444.3023
| TOTAL COST IN RS. LAKHS | [5 empty] | 6231.8616 | 6227.9623 | 6218.4481 | 6257.9097 | 6252.5859 | 6239.3746 | 6281.9613 | 6275.4753 | 6259.2255 | 6297.1648 | 6289.9914 | 6271.9464 | 6312.8462 | 6304.9897 | 6285.1654 | 6339.889 | 6330.8962 | 6308.1244
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 62.3186 | 62.2796 | 62.1845 | 62.5791 | 62.5259 | 62.3937 | 62.8196 | 62.7548 | 62.5923 | 62.9716 | 62.8999 | 62.7195 | 63.1285 | 63.0499 | 62.8517 | 63.3989 | 63.309 | 63.0812
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 914871.8935 | 914141.0324 | 912760.3476 | 918472.4948 | 917484.2765 | 915580.9153 | 921756.8922 | 920564.0386 | 918240.0231 | 923814.7096 | 922503.1725 | 919935.0091 | 925923.2783 | 924495.4335 | 921688.5321 | 929528.4466 | 927910.3503 | 924714.7017
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 914871.8935 | 914141.0324 | 912760.3476 | 918472.4948 | 917484.2765 | 915580.9153 | 921756.8922 | 920564.0386 | 918240.0231 | 923814.7096 | 922503.1725 | 919935.0091 | 925923.2783 | 924495.4335 | 921688.5321 | 929528.4466 | 927910.3503 | 924714.7017
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 12.9621 | 15.239 | 16.7289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 1.9443 | 2.2858 | 2.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 1555.4579 | 1828.6799 | 2007.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 3314103.665 | 3239069.4172 | 3095630.46 | 3675264.3961 | 3577497.4891 | 3386322.1819 | 3993323.9735 | 3878993.5738 | 3652354.5296 | 4187540.3708 | 4064191.1802 | 3818167.0535 | 4382776.6055 | 4250976.547 | 3986807.2955 | 4708338.0976 | 4563459.2572 | 4271326.5244
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 497115.5497 | 485860.4126 | 464344.569 | 551289.6594 | 536624.6234 | 507948.3273 | 598998.596 | 581849.0361 | 547853.1794 | 628131.0556 | 609628.677 | 572725.058 | 657416.4908 | 637646.482 | 598021.0943 | 706250.7146 | 684518.8886 | 640698.9787
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 155757.8588 | 152231.3626 | 145489.9486 | 172731.8668 | 168136.97 | 159152.0198 | 187680.1857 | 182306.8299 | 171655.1377 | 196808.0626 | 191010.8373 | 179448.0755 | 205983.8703 | 199789.4669 | 187373.9117 | 221284.7679 | 214475.6816 | 200745.8851
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 609 |  |  |  | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 1152 |  |  |  | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 96 |  |  |  | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 207209.6486 | 202518.2382 | 193549.9201 | 229790.7129 | 223677.9752 | 211725.0093 | 249676.9386 | 242528.5919 | 228358.3059 | 261820.0444 | 254107.8105 | 238725.4996 | 274026.914 | 265786.3016 | 249269.4925 | 294382.1863 | 285323.8415 | 267058.6552
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 3897271.7182 | 0 | 0 | 193083.0674 | 184438.8997 | 168465.2126 | 237459.3017 | 224993.8705 | 201589.8039 | 280337.4396 | 264514.8946 | 234508.1099 | 308269.122 | 290375.6999 | 256284.2181 | 337684.1537 | 317679.6748 | 279423.2246 | 389715.1544 | 366100.5376 | 320728.5027
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 433030.1909 | 413643.7909 | 377819.3714 | 532553.4142 | 504597.0111 | 452108.3721 | 628716.8347 | 593231.3841 | 525934.7334 | 691359.6234 | 651229.7866 | 574772.3267 | 757329.1407 | 712464.8063 | 626666.5116 | 874019.8195 | 821058.9763 | 719302.4569
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 64954.5286 | 0 | 0 | 54161.4623 | 51736.6988 | 47255.9421 | 66609.378 | 63112.7172 | 56547.6751 | 78637.0647 | 74198.7046 | 65781.5432 | 86472.142 | 81452.8831 | 71889.929 | 94723.3116 | 89111.8831 | 78380.6195 | 109318.4551 | 102694.3518 | 89967.1055
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 41570.8983 | 0 | 0 | 473754.8605 | 452545.251 | 413351.6954 | 582637.8246 | 552052.2394 | 494627.2645 | 687845.0107 | 649022.3026 | 575396.6848 | 756379.0905 | 712475.2111 | 628827.2484 | 828552.7636 | 779469.1271 | 685601.8634 | 956217.7103 | 898276.1224 | 786949.83
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 182974378.709 | 182828206.4769 | 182552069.5251 | 183694498.9596 | 183496855.3018 | 183116183.0597 | 184351378.4494 | 184112807.7235 | 183648004.6299 | 184762941.9172 | 184500634.4916 | 183987001.8148 | 185184655.6561 | 184899086.6947 | 184337706.4191 | 185905689.3116 | 185582070.063 | 184942940.3444
| Survey, Design, Supervision etc. | [5 empty] | 4250393.8801 | 4248932.1578 | 4246170.7882 | 4257595.0826 | 4255618.646 | 4251811.9236 | 4264163.8775 | 4261778.1702 | 4257130.1393 | 4268279.5122 | 4265656.4379 | 4260520.1111 | 4272496.6495 | 4269640.9599 | 4264027.1572 | 4279706.9861 | 4276470.7936 | 4270079.4964
| TOTAL COST | [5 empty] | 187224772.589 | 187077138.6346 | 186798240.3133 | 187952094.0422 | 187752473.9478 | 187367994.9833 | 188615542.3269 | 188374585.8937 | 187905134.7691 | 189031221.4294 | 188766290.9295 | 188247521.9259 | 189457152.3057 | 189168727.6546 | 188601733.5763 | 190185396.2977 | 189858540.8566 | 189213019.8409
| TOTAL COST IN RS. LAKHS | [5 empty] | 1872.2477 | 1870.7714 | 1867.9824 | 1879.5209 | 1877.5247 | 1873.6799 | 1886.1554 | 1883.7459 | 1879.0513 | 1890.3122 | 1887.6629 | 1882.4752 | 1894.5715 | 1891.6873 | 1886.0173 | 1901.854 | 1898.5854 | 1892.1302
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 18.7225 | 18.7077 | 18.6798 | 18.7952 | 18.7752 | 18.7368 | 18.8616 | 18.8375 | 18.7905 | 18.9031 | 18.8766 | 18.8248 | 18.9457 | 18.9169 | 18.8602 | 19.0185 | 18.9859 | 18.9213
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1261958.6204 | 1261025.6564 | 1259288.8113 | 1266508.441 | 1265238.0029 | 1262825.1423 | 1270684.2016 | 1269143.1454 | 1266181.3572 | 1273310.2676 | 1271611.4877 | 1268329.4951 | 1276007.7543 | 1274153.9283 | 1270557.8491 | 1280633.4514 | 1278525.1092 | 1274415.7954
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1261958.6204 | 1261025.6564 | 1259288.8113 | 1266508.441 | 1265238.0029 | 1262825.1423 | 1270684.2016 | 1269143.1454 | 1266181.3572 | 1273310.2676 | 1271611.4877 | 1268329.4951 | 1276007.7543 | 1274153.9283 | 1270557.8491 | 1280633.4514 | 1278525.1092 | 1274415.7954
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 26.1911 | 31.6347 | 35.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3.9287 | 4.7452 | 5.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 3142.9283 | 3796.1589 | 4225.0539 | 3932659.3307 | 3842800.086 | 3673289.6566 | 4359709.4552 | 4242258.0967 | 4015396.5614 | 4736703.0264 | 4599136.5048 | 4329598.4627 | 4967148.6419 | 4818636.2898 | 4525778.1752 | 5198922.7469 | 5040161.1033 | 4725490.2715 | 5585579.1548 | 5410971.3232 | 5062725.6683
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 1257.1713 | 1518.4636 | 1690.0215 | 589898.8996 | 576420.0129 | 550993.4485 | 653956.4183 | 636338.7145 | 602309.4842 | 710505.454 | 689870.4757 | 649439.7694 | 745072.2963 | 722795.4435 | 678866.7263 | 779838.412 | 756024.1655 | 708823.5407 | 837836.8732 | 811645.6985 | 759408.8502
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 184829.0393 | 180605.7907 | 172639.057 | 204899.7491 | 199379.713 | 188717.564 | 222617.8767 | 216152.4583 | 203484.578 | 233448.472 | 226468.6161 | 212704.7277 | 244341.5043 | 236879.9472 | 222090.8941 | 262513.7705 | 254307.4666 | 237940.4476
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 913.5 |  |  |  | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 1152 |  |  |  | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 144 |  |  |  | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 245883.9675 | 240265.6452 | 229667.2451 | 272584.6731 | 265241.1928 | 251056.9959 | 296155.6634 | 287554.511 | 270702.0258 | 310563.9499 | 301278.4249 | 282967.8851 | 325055.2983 | 315128.9508 | 295454.6017 | 349230.4438 | 338313.3359 | 316539.7684
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 5487836.4748 | 21028.6958 | 23851.7409 | 271884.6353 | 259601.7377 | 237204.1939 | 334138.9523 | 316377.9343 | 283445.0631 | 394424.9013 | 371847.2819 | 329539.329 | 433736.8534 | 408188.0682 | 360079.618 | 475158.7595 | 446581.6237 | 392559.741 | 548464.3868 | 514709.8462 | 450589.2246
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 2336.5218 | 2650.1934 | 609759.6083 | 582212.5758 | 531981.2802 | 749378.2664 | 709545.374 | 635686.347 | 884582.4369 | 833947.2832 | 739062.6245 | 972747.9212 | 915449.2907 | 807555.7728 | 1065645.4297 | 1001555.0736 | 880399.415 | 1230049.0216 | 1154347.2245 | 1010542.9781
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 91463.9412 | 350.4783 | 397.529 | 76265.9803 | 72820.5218 | 66537.818 | 93728.8521 | 88746.7336 | 79508.7798 | 110639.5796 | 104306.3631 | 92438.6181 | 121666.9206 | 114500.2664 | 101005.4321 | 133286.1217 | 125269.9892 | 110116.3861 | 153848.9812 | 144380.542 | 126394.1558
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 58536.9224 | 224.3061 | 254.4186 | 667104.9369 | 636967.2217 | 582011.8839 | 819854.1429 | 776275.1344 | 695469.9764 | 967773.6975 | 912376.5204 | 808568.3583 | 1064230.7751 | 1001543.4492 | 883502.9994 | 1165864.9038 | 1095747.1191 | 963197.2799 | 1345729.9626 | 1262908.7296 | 1105580.2982
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 252391724.0814 | 252205131.2752 | 251857762.2666 | 253301688.1928 | 253047600.5768 | 252565028.4552 | 254136840.3191 | 253828629.0817 | 253236271.4492 | 254662053.5136 | 254322297.5322 | 253665899.0199 | 255201550.8594 | 254830785.6559 | 254111569.8134 | 256126690.2779 | 255705021.8497 | 254883159.0746
| Survey, Design, Supervision etc. | [5 empty] | 4944567.3338 | 4942701.4057 | 4939227.7157 | 4953666.9749 | 4951126.0988 | 4946300.3775 | 4962018.4962 | 4958936.3838 | 4953012.8075 | 4967270.6281 | 4963873.0683 | 4957309.0832 | 4972665.6016 | 4968957.9495 | 4961765.7911 | 4981916.9958 | 4977700.3115 | 4969481.6837
| TOTAL COST | [5 empty] | 257336291.4152 | 257147832.6809 | 256796989.9823 | 258255355.1677 | 257998726.6755 | 257511328.8328 | 259098858.8153 | 258787565.4655 | 258189284.2567 | 259629324.1417 | 259286170.6006 | 258623208.1031 | 260174216.461 | 259799743.6055 | 259073335.6045 | 261108607.2736 | 260682722.1612 | 259852640.7583
| TOTAL COST IN RS. LAKHS | [5 empty] | 2573.3629 | 2571.4783 | 2567.9699 | 2582.5536 | 2579.9873 | 2575.1133 | 2590.9886 | 2587.8757 | 2581.8928 | 2596.2932 | 2592.8617 | 2586.2321 | 2601.7422 | 2597.9974 | 2590.7334 | 2611.0861 | 2606.8272 | 2598.5264
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 25.7336 | 25.7148 | 25.6797 | 25.8255 | 25.7999 | 25.7511 | 25.9099 | 25.8788 | 25.8189 | 25.9629 | 25.9286 | 25.8623 | 26.0174 | 25.98 | 25.9073 | 26.1109 | 26.0683 | 25.9853
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1652105.4796 | 1650983.7463 | 1648912.8172 | 1657548.5656 | 1656013.8308 | 1653122.305 | 1662565.0473 | 1660697.0725 | 1657134.9542 | 1665728.0741 | 1663665.1555 | 1659710.377 | 1668982.8488 | 1666727.8407 | 1662386.9738 | 1674576.0795 | 1672004.8908 | 1667031.399
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1652105.4796 | 1650983.7463 | 1648912.8172 | 1657548.5656 | 1656013.8308 | 1653122.305 | 1662565.0473 | 1660697.0725 | 1657134.9542 | 1665728.0741 | 1663665.1555 | 1659710.377 | 1668982.8488 | 1666727.8407 | 1662386.9738 | 1674576.0795 | 1672004.8908 | 1667031.399
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 6.3189 | 7.4431 | 8.1777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5055.1374 | 5954.461 | 6542.1879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 4466355.9779 | 4363788.9858 | 4171712.5808 | 4950410.5574 | 4816120.7661 | 4558469.1697 | 5378296.6414 | 5220873.6849 | 4914382.1674 | 5640003.2716 | 5469996.4751 | 5136821.6372 | 5903292.6983 | 5721507.3444 | 5363383.6521 | 6342628.8988 | 6142642.8294 | 5746142.3674
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 669953.3967 | 654568.3479 | 625756.8871 | 742561.5836 | 722418.1149 | 683770.3754 | 806744.4962 | 783131.0527 | 737157.3251 | 846000.4907 | 820499.4713 | 770523.2456 | 885493.9047 | 858226.1017 | 804507.5478 | 951394.3348 | 921396.4244 | 861921.3551
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 209911.9744 | 205091.4809 | 196064.1804 | 232661.8073 | 226350.3903 | 214241.155 | 252771.806 | 245373.1652 | 230968.5275 | 265071.6217 | 257081.5594 | 241422.8461 | 277445.8265 | 268902.1898 | 252070.918 | 298093.9633 | 288694.9205 | 270059.9986
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 279252.5962 | 272839.74 | 260830.4342 | 309517.4248 | 301121.1453 | 285011.8434 | 336270.3975 | 326427.7496 | 307264.8006 | 352633.2348 | 342003.8001 | 321172.5141 | 369095.0341 | 357729.1618 | 335337.984 | 396563.9093 | 384060.0629 | 359269.4318
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 7078401.2313 | 161099.2384 | 176969.7293 | 350686.2033 | 334764.5756 | 305943.1753 | 430818.6029 | 407761.998 | 365300.3223 | 508512.363 | 479179.6693 | 424570.5481 | 559204.5848 | 526000.4365 | 463875.0179 | 612633.3653 | 575483.5727 | 505696.2573 | 707213.6193 | 663319.1548 | 580449.9465
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17899.9154 | 19663.3033 | 786489.0257 | 750781.3607 | 686143.1891 | 966203.1185 | 914493.7369 | 819264.3219 | 1140448.0391 | 1074663.1823 | 952190.5155 | 1254136.219 | 1179668.7949 | 1040339.219 | 1373961.7186 | 1290645.3409 | 1134132.3183 | 1586078.2236 | 1487635.4726 | 1301783.4993
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 117973.3539 | 2684.9873 | 2949.4955 | 98370.4984 | 93904.3448 | 85819.694 | 120848.3262 | 114380.7501 | 102469.8846 | 142642.0946 | 134414.0216 | 119095.693 | 156861.6991 | 147547.6498 | 130120.9351 | 171848.9319 | 161428.0954 | 141852.1527 | 198379.5072 | 186066.7321 | 162821.206
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 75502.9465 | 1718.3919 | 1887.6771 | 860455.0132 | 821389.1924 | 750672.0724 | 1057070.4612 | 1000498.0295 | 896312.6883 | 1247702.3843 | 1175730.7381 | 1041740.0318 | 1372082.4597 | 1290611.6873 | 1138178.7504 | 1503177.0439 | 1412025.1111 | 1240792.6964 | 1735242.2148 | 1627541.3367 | 1424210.7665
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 330421095.9153 | 330196749.2577 | 329782563.4429 | 331509713.1115 | 331202766.1607 | 330624460.9901 | 332513009.4517 | 332139414.4932 | 331426990.8385 | 333145614.8109 | 332733031.1039 | 331942075.3949 | 333796569.7528 | 333345568.1473 | 332477394.7563 | 334915215.9007 | 334400978.1629 | 333406279.8007
| Survey, Design, Supervision etc. | [5 empty] | 5724861.0521 | 5722617.5856 | 5718475.7274 | 5735747.2241 | 5732677.7546 | 5726894.7029 | 5745780.1875 | 5742044.2379 | 5734920.0014 | 5752106.2411 | 5747980.404 | 5740070.8469 | 5758615.7905 | 5754105.7745 | 5745424.0406 | 5769802.252 | 5764659.8746 | 5754712.891
| TOTAL COST | [5 empty] | 336145956.9674 | 335919366.8432 | 335501039.1703 | 337245460.3356 | 336935443.9153 | 336351355.693 | 338258789.6392 | 337881458.7311 | 337161910.8399 | 338897721.052 | 338481011.5079 | 337682146.2419 | 339555185.5433 | 339099673.9217 | 338222818.7968 | 340685018.1527 | 340165638.0375 | 339160992.6917
| TOTAL COST IN RS. LAKHS | [5 empty] | 3361.4596 | 3359.1937 | 3355.0104 | 3372.4546 | 3369.3544 | 3363.5136 | 3382.5879 | 3378.8146 | 3371.6191 | 3388.9772 | 3384.8101 | 3376.8215 | 3395.5519 | 3390.9967 | 3382.2282 | 3406.8502 | 3401.6564 | 3391.6099
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 33.6146 | 33.5919 | 33.5501 | 33.7245 | 33.6935 | 33.6351 | 33.8259 | 33.7881 | 33.7162 | 33.8898 | 33.8481 | 33.7682 | 33.9555 | 33.91 | 33.8223 | 34.0685 | 34.0166 | 33.9161
ESTIMATE FOR A 765 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 961239.4596 | 959995.7678 | 957659.5235 | 967633.2772 | 965961.3256 | 962766.4982 | 973435.9581 | 971425.6533 | 967545.3124 | 977061.0443 | 974855.12 | 970578.2858 | 980768.7907 | 978371.4959 | 973707.59 | 987095.1923 | 984385.4218 | 979092.1105
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 961239.4596 | 959995.7678 | 957659.5235 | 967633.2772 | 965961.3256 | 962766.4982 | 973435.9581 | 971425.6533 | 967545.3124 | 977061.0443 | 974855.12 | 970578.2858 | 980768.7907 | 978371.4959 | 973707.59 | 987095.1923 | 984385.4218 | 979092.1105
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 33.1275 | 39.4561 | 43.6035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 4.9691 | 5.9184 | 6.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3975.2993 | 4734.735 | 5232.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 6019909.3047 | 5887557.213 | 5636266.8142 | 6685615.8414 | 6513836.1661 | 6181104.1598 | 7269979.0049 | 7069546.8351 | 6676617.3372 | 7626261.5822 | 7410232.8633 | 6984431.5722 | 7984130.4966 | 7753482.5438 | 7296902.5122 | 8580455.5749 | 8327164.9246 | 7823094.8627
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 902986.3957 | 883133.582 | 845440.0221 | 1002842.3762 | 977075.4249 | 927165.624 | 1090496.8507 | 1060432.0253 | 1001492.6006 | 1143939.2373 | 1111534.9295 | 1047664.7358 | 1197619.5745 | 1163022.3816 | 1094535.3768 | 1287068.3362 | 1249074.7387 | 1173464.2294
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 282926.6305 | 276706.2825 | 264896.0139 | 314213.8307 | 306140.4458 | 290502.5449 | 341678.0154 | 332258.0066 | 313790.9146 | 358422.7575 | 348269.7345 | 328257.718 | 375242.0551 | 364401.9503 | 342943.3795 | 403268.4317 | 391364.1543 | 367673.6239
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 609 |  |  |  | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 1920 |  |  |  | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 376386.3227 | 368111.1952 | 352399.6181 | 418008.6832 | 407268.4017 | 386464.8032 | 454545.1642 | 442013.426 | 417446.0644 | 476821.2289 | 463314.3385 | 436691.7145 | 499196.4771 | 484775.5398 | 456228.5185 | 536480.86 | 520644.22 | 489127.9516
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 8041180.9998 | 0 | 0 | 331987.7779 | 317550.2652 | 291021.642 | 409472.7784 | 388701.1819 | 350005.0601 | 484181.8575 | 457852.248 | 408371.2605 | 532801.6904 | 503043.927 | 446893.8032 | 583979.2987 | 550726.3115 | 487774.7185 | 674470.3973 | 635238.0901 | 560659.7667
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 893464.5555 | 854609.4932 | 783214.1402 | 1101996.6346 | 1046094.9224 | 941953.6992 | 1303057.9947 | 1232198.239 | 1099032.1664 | 1433906.4786 | 1353820.6783 | 1202706.2435 | 1571638.5944 | 1482146.2472 | 1312727.3085 | 1815173.4307 | 1709589.1947 | 1508879.7318
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 134019.6833 | 0 | 0 | 74500.3433 | 71260.4661 | 65307.2603 | 91888.511 | 87227.2217 | 78543.5455 | 108653.7427 | 102745.1971 | 91641.3227 | 119564.368 | 112886.521 | 100286.0466 | 131048.9757 | 123586.7764 | 109460.0055 | 151355.8013 | 142551.8014 | 125815.9121
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 85772.5973 | 0 | 0 | 586494.6852 | 560989.1546 | 514123.2831 | 723380.8721 | 686685.4521 | 618324.2915 | 855363.0737 | 808848.7829 | 721434.9137 | 941255.614 | 888685.094 | 789489.4267 | 1031666.7595 | 972921.5237 | 861710.2769 | 1191529.718 | 1122221.3242 | 990470.1175
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 192247891.9242 | 191999153.5603 | 191531904.7025 | 193526655.4361 | 193192265.1252 | 192553299.6367 | 194687191.6124 | 194285130.6685 | 193509062.4886 | 195412208.8657 | 194971023.9947 | 194115657.1691 | 196153758.1402 | 195674299.1827 | 194741518.005 | 197419038.4588 | 196877084.3566 | 195818422.1044
| Survey, Design, Supervision etc. | [5 empty] | 4343129.0122 | 4340641.6286 | 4335969.14 | 4355916.6473 | 4352572.7442 | 4346183.0894 | 4367522.0091 | 4363501.3997 | 4355740.7179 | 4374772.1816 | 4370360.3329 | 4361806.6647 | 4382187.6744 | 4377393.0848 | 4368065.273 | 4394840.4776 | 4389420.9366 | 4378834.314
| TOTAL COST | [5 empty] | 196591020.9365 | 196339795.1889 | 195867873.8425 | 197882572.0834 | 197544837.8695 | 196899482.7261 | 199054713.6215 | 198648632.0682 | 197864803.2065 | 199786981.0473 | 199341384.3277 | 198477463.8338 | 200535945.8146 | 200051692.2675 | 199109583.2781 | 201813878.9364 | 201266505.2931 | 200197256.4184
| TOTAL COST IN RS. LAKHS | [5 empty] | 1965.9102 | 1963.398 | 1958.6787 | 1978.8257 | 1975.4484 | 1968.9948 | 1990.5471 | 1986.4863 | 1978.648 | 1997.8698 | 1993.4138 | 1984.7746 | 2005.3595 | 2000.5169 | 1991.0958 | 2018.1388 | 2012.6651 | 2001.9726
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 19.6591 | 19.634 | 19.5868 | 19.7883 | 19.7545 | 19.6899 | 19.9055 | 19.8649 | 19.7865 | 19.9787 | 19.9341 | 19.8477 | 20.0536 | 20.0052 | 19.911 | 20.1814 | 20.1267 | 20.0197
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1302858.9814 | 1301474.8904 | 1298922.2386 | 1309807.7338 | 1307952.7 | 1304466.655 | 1316094.2703 | 1313871.5197 | 1309647.9536 | 1320010.2515 | 1317576.7412 | 1312930.2338 | 1324006.0469 | 1321367.599 | 1316310.7951 | 1330801.7134 | 1327831.0519 | 1322112.2774
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1302858.9814 | 1301474.8904 | 1298922.2386 | 1309807.7338 | 1307952.7 | 1304466.655 | 1316094.2703 | 1313871.5197 | 1309647.9536 | 1320010.2515 | 1317576.7412 | 1312930.2338 | 1324006.0469 | 1321367.599 | 1316310.7951 | 1330801.7134 | 1327831.0519 | 1322112.2774
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 7142856.0815 | 6983337.2339 | 6686510.5709 | 7929272.5663 | 7721622.0606 | 7326915.7396 | 8621245.0377 | 8378603.2414 | 7911450.7189 | 9043561.9082 | 8781884.791 | 8275191.8837 | 9467959.7046 | 9188451.6777 | 8644766.4055 | 10175411.8588 | 9868311.4143 | 9267623.3067
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1071428.4122 | 1047500.5851 | 1002976.5856 | 1189390.8849 | 1158243.3091 | 1099037.3609 | 1293186.7556 | 1256790.4862 | 1186717.6078 | 1356534.2862 | 1317282.7187 | 1241278.7826 | 1420193.9557 | 1378267.7517 | 1296714.9608 | 1526311.7788 | 1480246.7122 | 1390143.496
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 335703.4303 | 328206.2858 | 314255.8816 | 372663.8154 | 362904.5558 | 344353.9558 | 405185.4747 | 393781.6774 | 371826.2155 | 425033.7288 | 412735.3001 | 388921.5 | 444979.7832 | 431843.3288 | 406290.9435 | 478228.9642 | 463795.7079 | 435564.2756
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 913.5 |  |  |  | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 887.4291 | 5880 |  |  |  | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769 | 5218083.2769
| Insulators 210 kN | 1002.252 | 1920 |  |  |  | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532 | 1924323.7532
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 446596.9831 | 436623.2925 | 418064.6249 | 495766.5625 | 482783.5081 | 458105.0531 | 539031.1635 | 523860.328 | 494652.2767 | 565435.929 | 549074.9371 | 517394.679 | 591970.8015 | 574494.9571 | 540501.8038 | 636203.2478 | 617002.2265 | 579445.0514
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 7325335.2379 | 0 | 0 | 302433.4072 | 289075.9709 | 265023.8958 | 372694.2191 | 353429.7021 | 318220.6489 | 440581.1789 | 416130.1792 | 371020.7654 | 484802.6605 | 457152.8518 | 405921.5503 | 531372.1205 | 500461.4549 | 442988.5363 | 613747.8109 | 577260.2523 | 509122.9904
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 813926.1375 | 777977.8386 | 713247.5141 | 1003016.0656 | 951170.2923 | 856413.668 | 1185717.347 | 1119913.4137 | 998512.3711 | 1304728.7355 | 1230315.9838 | 1092439.3657 | 1430059.1379 | 1346870.5812 | 1192196.1652 | 1651753.3223 | 1553555.911 | 1370181.0025
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 122088.9206 | 0 | 0 | 67868.139 | 64870.6384 | 59473.1871 | 83635.149 | 79312.0587 | 71410.9048 | 98869.4502 | 93382.4775 | 83259.6145 | 108793.0552 | 102588.2477 | 91091.5909 | 119243.5627 | 112306.9965 | 99409.6778 | 137729.2348 | 129541.1754 | 114250.7047
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 78136.9092 | 0 | 0 | 534283.4821 | 510686.0309 | 468195.2671 | 658407.3067 | 624374.3165 | 562173.4646 | 778337.4482 | 735141.9382 | 655450.9579 | 856459.7938 | 807613.2189 | 717107.2181 | 938730.1139 | 884122.8593 | 782590.3225 | 1084256.2683 | 1019796.7892 | 899424.4604
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 260571796.2714 | 260294978.0745 | 259784447.7256 | 261961546.7679 | 261590540.0017 | 260893330.9942 | 263218854.0544 | 262774303.9402 | 261929590.7263 | 264002050.2958 | 263515348.2477 | 262586046.7688 | 264801209.3784 | 264273519.8056 | 263262159.0139 | 266160342.6843 | 265566210.3873 | 264422455.486
| Survey, Design, Supervision etc. | [5 empty] | 5026368.0557 | 5023599.8737 | 5018494.5702 | 5040265.5607 | 5036555.493 | 5029583.4029 | 5052838.6335 | 5048393.1324 | 5039946.0003 | 5060670.5959 | 5055803.5755 | 5046510.5607 | 5068662.1868 | 5063385.291 | 5053271.6831 | 5082253.5198 | 5076312.1969 | 5064874.6478
| TOTAL COST | [5 empty] | 265598164.3271 | 265318577.9482 | 264802942.2958 | 267001812.3286 | 266627095.4947 | 265922914.3971 | 268271692.688 | 267822697.0726 | 266969536.7266 | 269062720.8918 | 268571151.8231 | 267632557.3295 | 269869871.5652 | 269336905.0966 | 268315430.697 | 271242596.2042 | 270642522.5842 | 269487330.1338
| TOTAL COST IN RS. LAKHS | [5 empty] | 2655.9816 | 2653.1858 | 2648.0294 | 2670.0181 | 2666.271 | 2659.2291 | 2682.7169 | 2678.227 | 2669.6954 | 2690.6272 | 2685.7115 | 2676.3256 | 2698.6987 | 2693.3691 | 2683.1543 | 2712.426 | 2706.4252 | 2694.8733
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 26.5598 | 26.5319 | 26.4803 | 26.7002 | 26.6627 | 26.5923 | 26.8272 | 26.7823 | 26.697 | 26.9063 | 26.8571 | 26.7633 | 26.987 | 26.9337 | 26.8315 | 27.1243 | 27.0643 | 26.9487
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1797689.9913 | 1796045.7749 | 1793049.1677 | 1805868.6374 | 1803655.6477 | 1799543.8186 | 1813296.1385 | 1810636.437 | 1805638.1562 | 1817933.7972 | 1815017.1249 | 1809508.6772 | 1822673.5187 | 1819506.3742 | 1813501.8669 | 1830749.9559 | 1827175.6383 | 1820368.6357
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1797689.9913 | 1796045.7749 | 1793049.1677 | 1805868.6374 | 1803655.6477 | 1799543.8186 | 1813296.1385 | 1810636.437 | 1805638.1562 | 1817933.7972 | 1815017.1249 | 1809508.6772 | 1822673.5187 | 1819506.3742 | 1813501.8669 | 1830749.9559 | 1827175.6383 | 1820368.6357
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8111811.0163 | 7929102.5915 | 7592848.1894 | 9002736.6774 | 8764521.2587 | 8316329.7119 | 9787703.3704 | 9509126.779 | 8978022.3819 | 10267042.3324 | 9966516.4364 | 9390171.2997 | 10748868.8776 | 10427789.6464 | 9809137.8897 | 11552220.3544 | 11199351.082 | 10515553.7314
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1216771.6524 | 1189365.3887 | 1138927.2284 | 1350410.5016 | 1314678.1888 | 1247449.4568 | 1468155.5056 | 1426369.0169 | 1346703.3573 | 1540056.3499 | 1494977.4655 | 1408525.695 | 1612330.3316 | 1564168.447 | 1471370.6835 | 1732833.0532 | 1679902.6623 | 1577333.0597
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 381242.8464 | 372655.8268 | 356852.3786 | 423115.0047 | 411919.2404 | 390854.9157 | 460007.2518 | 446914.5734 | 421953.4702 | 482535.4579 | 468411.1954 | 441323.8458 | 505180.5766 | 490090.3385 | 461014.6418 | 542936.8807 | 526352.5587 | 494215.1177
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 3840 |  |  |  | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 163660.9478 | 100 |  |  |  | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 507179.5212 | 495755.9351 | 474732.1037 | 562883.3892 | 547989.3067 | 519966.7636 | 611962.3224 | 594544.7147 | 561338.1628 | 641932.3137 | 623142.3567 | 587107.1915 | 672057.8376 | 651982.8123 | 613302.4855 | 722286.2535 | 700223.6008 | 657470.1377
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 9447553.3584 | 0 | 0 | 390051.1935 | 372678.2408 | 341739.6703 | 480435.4639 | 455346.8748 | 409967.4353 | 567868.2148 | 536003.0215 | 477801.3034 | 624851.2861 | 588806.6921 | 522676.522 | 684875.2829 | 644570.5905 | 570358.1371 | 791073.6 | 743484.0933 | 655466.1317
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1049728.1509 | 1002973.064 | 919709.408 | 1292975.4852 | 1225455.6349 | 1103327.8837 | 1528279.521 | 1442522.0846 | 1285886.2816 | 1681635.6318 | 1584630.3523 | 1406657.0444 | 1843175.6559 | 1734705.3554 | 1534980.5426 | 2128982.6599 | 2000907.049 | 1764028.0608
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 157459.2226 | 0 | 0 | 87530.1736 | 83631.5634 | 76688.7351 | 107813.0262 | 102182.9741 | 91999.5154 | 127433.5375 | 120282.7688 | 107221.9025 | 140220.9311 | 132132.276 | 117292.2105 | 153690.7293 | 144646.0788 | 127992.2932 | 177522.3629 | 166842.9499 | 147091.1133
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 100773.9025 | 0 | 0 | 689070.4031 | 658379.0793 | 603722.5276 | 848744.6374 | 804422.7523 | 724254.7405 | 1003204.6723 | 946911.1345 | 844091.0893 | 1103871.8374 | 1040194.9064 | 923368.3367 | 1209911.1481 | 1138708.2622 | 1007603.407 | 1397522.719 | 1313450.3687 | 1157956.4918
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 359537998.2576 | 359209154.9899 | 358609833.5414 | 361173727.4856 | 360731129.5308 | 359908763.723 | 362659227.696 | 362127287.3936 | 361127631.2491 | 363586759.4404 | 363003424.9809 | 361901735.4458 | 364534703.7398 | 363901274.8312 | 362700373.3805 | 366149991.1838 | 365435127.665 | 364073727.1444
| Survey, Design, Supervision etc. | [5 empty] | 6016030.0756 | 6012741.6429 | 6006748.4284 | 6032387.3678 | 6027961.3883 | 6019737.7302 | 6047242.3699 | 6041922.9669 | 6031926.4055 | 6056517.6874 | 6050684.3428 | 6039667.4474 | 6065997.1304 | 6059662.8413 | 6047653.8268 | 6082150.0048 | 6075001.3696 | 6061387.3644
| TOTAL COST | [5 empty] | 365554028.3331 | 365221896.6327 | 364616581.9698 | 367206114.8535 | 366759090.9191 | 365928501.4532 | 368706470.0659 | 368169210.3605 | 367159557.6545 | 369643277.1278 | 369054109.3237 | 367941402.8932 | 370600700.8702 | 369960937.6725 | 368748027.2073 | 372232141.1886 | 371510129.0347 | 370135114.5088
| TOTAL COST IN RS. LAKHS | [5 empty] | 3655.5403 | 3652.219 | 3646.1658 | 3672.0611 | 3667.5909 | 3659.285 | 3687.0647 | 3681.6921 | 3671.5956 | 3696.4328 | 3690.5411 | 3679.414 | 3706.007 | 3699.6094 | 3687.4803 | 3722.3214 | 3715.1013 | 3701.3511
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 36.5554 | 36.5222 | 36.4617 | 36.7206 | 36.6759 | 36.5929 | 36.8706 | 36.8169 | 36.716 | 36.9643 | 36.9054 | 36.7941 | 37.0601 | 36.9961 | 36.8748 | 37.2232 | 37.151 | 37.0135
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 13309062.3407 | 13941842.3508 | 14341910.5814
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 12243.3706 | 13283.528 | 13922.4666 | 734602.2359 | 797011.6778 | 835347.9947
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 282821.8608 | 306849.4959 | 321608.978
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) x No. of Ckts. | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 2436 |  |  |  | 876960000 | 876960000 | 876960000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 21000 | 1680 |  |  |  | 35280000 | 35280000 | 35280000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 40 |  |  |  | 1240000 | 1240000 | 1240000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 840 |  |  |  | 49560000 | 49560000 | 49560000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 40 |  |  |  | 1800000 | 1800000 | 1800000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 812 |  |  |  | 1055600 | 1055600 | 1055600
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 5040 | 10080 |  |  |  | 50803200 | 50803200 | 50803200
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 1680 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 0 |  |  |  | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 380000 | 100 |  |  |  | 38000000 | 38000000 | 38000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 484837.4757 | 526027.7073 | 551329.6765
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 110476.1386 | 135501.5486 | 151914.4961 | 33142841.5799 | 40650464.5715 | 45574348.8348
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 12275.1265 | 15055.7276 | 16879.3885 | 69968221.113 | 85817647.4288 | 96212514.2067
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 1841.269 | 2258.3591 | 2531.9083 | 8653964.1903 | 10614287.9715 | 11899968.8624
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 1178.4121 | 1445.3499 | 1620.4213 | 63634255.8333 | 78048891.9773 | 87502749.7628
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 1565772040.0812 | 1640216747.1546 | 1687283597.8152
| Survey, Design, Supervision etc. | [5 empty] | 34966782.7415 | 36344009.8224 | 37214746.5596
| TOTAL COST | [5 empty] | 1600738822.8227 | 1676560756.9769 | 1724498344.3747
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 288132988.1081 | 301780936.2558 | 310409701.9875
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
v) | Contengency at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1984916140.3001 | 2078935338.6514 | 2138377947.0247
| TOTAL COST IN RS. LAKHS | [5 empty] | 19849.1614 | 20789.3534 | 21383.7795
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 198.4916 | 207.8935 | 213.8378
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 8411202.1434 | 8912246.9919 | 9223024.2025
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
III | Detailed survey (Rs. Per kM) | 50000 | 100 |  |  |  | 5000000 | 5000000 | 5000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 520753.4201 | 578395.2043 | 613278.8096 | 31245205.2042 | 34703712.2574 | 36796728.5749
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 12029404.0036 | 13360929.2191 | 14166740.5013
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 1218 |  |  |  | 438480000 | 438480000 | 438480000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of suspn.x1) | 24000 | 210 |  |  |  | 5040000 | 5040000 | 5040000
| b) Double 'I' Suspension Insulator Sring (No. Suspn. X 2) | 21000 | 420 |  |  |  | 8820000 | 8820000 | 8820000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'V' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
| f) Single 'I' Suspension Pilot strings (No. of Suspn x 1) | 15000 | 210 |  |  |  | 3150000 | 3150000 | 3150000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 406 |  |  |  | 527800 | 527800 | 527800
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 2700 | 5040 |  |  |  | 13608000 | 13608000 | 13608000
| f) Quad Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 1000 | 840 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190000 | 100 |  |  |  | 19000000 | 19000000 | 19000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 20621835.4348 | 22904450.0899 | 24285840.8595
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 48382.6073 | 59272.006 | 66421.8968 | 14514782.1992 | 17781601.804 | 19926569.0329
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 5375.8453 | 6585.7784 | 7380.2108 | 30642317.976 | 37538937.1417 | 42067201.2916
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 806.3768 | 987.8668 | 1107.0316 | 3789970.9076 | 4642973.8044 | 5203048.5808
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 516.0811 | 632.2347 | 708.5002 | 27868381.8224 | 34140675.4636 | 38259012.5431
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 989553193.3401 | 1048499646.1046 | 1085061670.8834
| Survey, Design, Supervision etc. | [5 empty] | 23306734.0768 | 24397243.4529 | 25073640.9113
| TOTAL COST | [5 empty] | 1012859927.4169 | 1072896889.5575 | 1110135311.7948
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 182314786.935 | 193121440.1204 | 199824356.1231
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
v) | Contengency at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1255946309.997 | 1330392143.0513 | 1376567786.6255
| TOTAL COST IN RS. LAKHS | [5 empty] | 12559.4631 | 13303.9214 | 13765.6779
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 125.5946 | 133.0392 | 137.6568
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 5050227.0344 | 5357651.6793 | 5546861.9223
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 10366.8386 | 11627.9013 | 12386.9423 | 130622166.4713 | 146511556.3957 | 156075473.2845
| b) 'B' Type towers | 60000 | 25 | 16898.4575 | 18612.4108 | 19653.708 | 25347686.3224 | 27918616.1635 | 29480562.0497
| c) 'C' Type towers | 60000 | 25 | 20290.3432 | 22180.6901 | 23333.1622 | 30435514.7251 | 33271035.0929 | 34999743.239
| d) 'D' Type towers | 60000 | 20 | 25560.0611 | 27781.5378 | 29139.1942 | 30672073.3304 | 33337845.351 | 34967032.9907
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 361795.7347 | 401731.755 | 425871.3526 | 21707744.0849 | 24103905.3003 | 25552281.1564
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 7163555.548 | 7954288.7491 | 8432252.7816
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 609 |  |  |  | 219240000 | 219240000 | 219240000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) | 21000 | 840 |  |  |  | 17640000 | 17640000 | 17640000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 203 |  |  |  | 263900 | 263900 | 263900
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 900 | 5040 |  |  |  | 4536000 | 4536000 | 4536000
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 840 |  |  |  | 420000 | 420000 | 420000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 3360 |  |  |  | 3024000 | 3024000 | 3024000
V | ERECTION
2 | Stringing of Conductor (Route kM) | 95000 | 100 |  |  |  | 9500000 | 9500000 | 9500000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 12280380.9395 | 13635923.5699 | 14455290.4828
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 21646.7931 | 26473.7232 | 29642.2493 | 6494037.9255 | 7942116.9663 | 8892674.7876
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 2405.1992 | 2941.5248 | 3293.5833 | 13709635.6204 | 16766691.3734 | 18773424.5515
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 360.7799 | 441.2287 | 494.0375 | 1695665.4583 | 2073774.9857 | 2321976.1945
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 230.8991 | 282.3864 | 316.184 | 12468552.8169 | 15248864.5753 | 17073935.5921
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 594144356.9927 | 630311962.2731 | 652571990.8604
| Survey, Design, Supervision etc. | [5 empty] | 16991670.6044 | 17660771.3021 | 18072581.8309
| TOTAL COST | [5 empty] | 611136027.5971 | 647972733.5751 | 670644572.6913
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 110004484.9675 | 116635092.0435 | 120716023.0844
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
v) | Contengency at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 757808674.2204 | 803486189.6332 | 831599270.1372
| TOTAL COST IN RS. LAKHS | [5 empty] | 7578.0867 | 8034.8619 | 8315.9927
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 75.7809 | 80.3486 | 83.1599

## Moose-Std-Plain
CERC
Capital Cost Benchmarking
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1628056.6009 | 1626810.296 | 1623728.854 | 1636427.4099 | 1634747.1924 | 1630522.8927 | 1644071.32 | 1642043.3525 | 1636896.6463 | 1648868.7462 | 1646637.3261 | 1640951.6313 | 1653792.7332 | 1651360.5342 | 1645144.3983 | 1662233.2667 | 1659469.6827 | 1652381.9868
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1628056.6009 | 1626810.296 | 1623728.854 | 1636427.4099 | 1634747.1924 | 1630522.8927 | 1644071.32 | 1642043.3525 | 1636896.6463 | 1648868.7462 | 1646637.3261 | 1640951.6313 | 1653792.7332 | 1651360.5342 | 1645144.3983 | 1662233.2667 | 1659469.6827 | 1652381.9868
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 10366.8386 | 11627.9013 | 12386.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 16898.4575 | 18612.4108 | 19653.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 20290.3432 | 22180.6901 | 23333.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 25560.0611 | 27781.5378 | 29139.1942 | 6713449.1742 | 6598109.0913 | 6309276.5083 | 7467581.5258 | 7318955.0922 | 6939279.0957 | 8127742.3112 | 7955060.3041 | 7508853.8293 | 8529587.207 | 8343816.2595 | 7861380.4186 | 8932824.5617 | 8734772.7986 | 8218426.5393 | 9604040.2607 | 9386927.1116 | 8818212.4665
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 10224.0244 | 11112.6151 | 11655.6777 | 1007017.3761 | 989716.3637 | 946391.4763 | 1120137.2289 | 1097843.2638 | 1040891.8644 | 1219161.3467 | 1193259.0456 | 1126328.0744 | 1279438.0811 | 1251572.4389 | 1179207.0628 | 1339923.6842 | 1310215.9198 | 1232763.9809 | 1440606.0391 | 1408039.0667 | 1322731.87
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 315521.9552 | 310101.1458 | 296526.4514 | 350965.0349 | 343979.8174 | 326135.6199 | 381991.5932 | 373875.8001 | 352904.7708 | 400877.6954 | 392146.7419 | 369472.9872 | 419829.241 | 410521.1078 | 386253.6147 | 451375.3635 | 441171.3739 | 414442.6459
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 419748.923 | 412537.4473 | 394478.5982 | 466899.9826 | 457607.3249 | 433868.6197 | 508175.6029 | 497378.9044 | 469480.4751 | 533300.3871 | 521685.3211 | 491521.7019 | 558512.2329 | 546129.3263 | 513845.5061 | 600479.046 | 586904.3532 | 551346.2736
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 10308786.5814 | 2915.0868 | 3206.9634 | 510729.6279 | 493331.2484 | 451085.3928 | 631916.3422 | 607012.7406 | 545667.8315 | 748582.1956 | 717111.3464 | 638920.6756 | 824433.5736 | 788912.987 | 700321.1897 | 904226.5423 | 864575.3868 | 765379.8013 | 1045219.6978 | 998496.4681 | 881172.1424
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 323.8985 | 356.3293 | 1145420.7313 | 1106401.1338 | 1011655.7417 | 1417207.9302 | 1361356.2622 | 1223777.1465 | 1678856.1287 | 1608275.9997 | 1432916.65 | 1848969.1125 | 1769306.5786 | 1570620.472 | 2027921.9588 | 1938995.7382 | 1716528.3623 | 2344129.35 | 2239342.4861 | 1976217.5222
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 171813.1097 | 48.5848 | 53.4494 | 143264.0565 | 138383.6613 | 126533.3352 | 177257.9729 | 170272.2983 | 153064.5233 | 209983.749 | 201155.9049 | 179222.7487 | 231260.7133 | 221296.8831 | 196446.1214 | 253643.3279 | 242520.8375 | 214695.6219 | 293193.1215 | 280086.8534 | 247176.3702
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 109960.3902 | 31.0943 | 34.2076 | 1253142.7372 | 1210453.5106 | 1106797.7126 | 1550490.38 | 1489386.0973 | 1338868.244 | 1836745.492 | 1759527.5984 | 1567676.4389 | 2022856.8869 | 1935702.4266 | 1718330.7266 | 2218639.4963 | 2121350.1385 | 1877960.6408 | 2564584.8638 | 2449943.2357 | 2162072.4748
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 325611320.1701 | 325362059.191 | 324745770.8052 | 327285481.9864 | 326949438.4854 | 326104578.5337 | 328814264.0079 | 328408670.4923 | 327379329.2515 | 329773749.2457 | 329327465.2255 | 328190326.2687 | 330758546.6339 | 330272106.8422 | 329028879.656 | 332446653.3311 | 331893936.5375 | 330476397.3544
| Survey, Design, Supervision etc. | [5 empty] | 5676763.2947 | 5674270.6849 | 5668107.801 | 5693504.9129 | 5690144.4778 | 5681695.8783 | 5708792.7331 | 5704736.7979 | 5694443.3855 | 5718387.5854 | 5713924.7452 | 5702553.3557 | 5728235.5593 | 5723371.1614 | 5710938.8895 | 5745116.6263 | 5739589.4584 | 5725414.0665
| TOTAL COST | [5 empty] | 331288083.4648 | 331036329.8759 | 330413878.6062 | 332978986.8992 | 332639582.9633 | 331786274.412 | 334523056.741 | 334113407.2902 | 333073772.6371 | 335492136.8311 | 335041389.9708 | 333892879.6244 | 336486782.1932 | 335995478.0036 | 334739818.5456 | 338191769.9574 | 337633525.9959 | 336201811.4209
| TOTAL COST IN RS. LAKHS | [5 empty] | 3312.8808 | 3310.3633 | 3304.1388 | 3329.7899 | 3326.3958 | 3317.8627 | 3345.2306 | 3341.1341 | 3330.7377 | 3354.9214 | 3350.4139 | 3338.9288 | 3364.8678 | 3359.9548 | 3347.3982 | 3381.9177 | 3376.3353 | 3362.0181
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 33.1288 | 33.1036 | 33.0414 | 33.2979 | 33.264 | 33.1786 | 33.4523 | 33.4113 | 33.3074 | 33.5492 | 33.5041 | 33.3893 | 33.6487 | 33.5995 | 33.474 | 33.8192 | 33.7634 | 33.6202
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2325082.4877 | 2323449.3705 | 2319444.1489 | 2336000.5263 | 2333784.554 | 2328257.0959 | 2346026.6456 | 2343339.4855 | 2336572.5878 | 2352341.569 | 2349377.3043 | 2341882.3332 | 2358838.7408 | 2355600.1101 | 2347386.1956 | 2370008.6727 | 2366315.5052 | 2356915.7793
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2325082.4877 | 2323449.3705 | 2319444.1489 | 2336000.5263 | 2333784.554 | 2328257.0959 | 2346026.6456 | 2343339.4855 | 2336572.5878 | 2352341.569 | 2349377.3043 | 2341882.3332 | 2358838.7408 | 2355600.1101 | 2347386.1956 | 2370008.6727 | 2366315.5052 | 2356915.7793
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 39.6672 | 47.4027 | 52.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5.9501 | 7.1104 | 7.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4760.065 | 5688.3225 | 6294.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8071596.8224 | 7932218.9887 | 7585524.2727 | 8976104.3948 | 8796179.1737 | 8339381.5223 | 9768964.9637 | 9559735.8178 | 9022265.8025 | 10251848.7038 | 10026682.7192 | 9445301.6091 | 10736524.8785 | 10496412.8929 | 9873953.1559 | 11543450.8439 | 11280154.7492 | 10594306.1139
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1210739.5234 | 1189832.8483 | 1137828.6409 | 1346415.6592 | 1319426.8761 | 1250907.2283 | 1465344.7446 | 1433960.3727 | 1353339.8704 | 1537777.3056 | 1504002.4079 | 1416795.2414 | 1610478.7318 | 1574461.9339 | 1481092.9734 | 1731517.6266 | 1692023.2124 | 1589145.9171
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 379352.8401 | 372802.2928 | 356508.1656 | 421863.3277 | 413407.1145 | 391938.3159 | 459126.575 | 449293.1217 | 424032.844 | 481821.3803 | 471238.9197 | 443914.887 | 504600.4273 | 493315.5272 | 464060.8612 | 542524.727 | 530150.2089 | 497916.3605
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1827 |  |  |  | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108 | 407883280.2108
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 609 |  |  |  | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 288 |  |  |  | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 504665.1855 | 495950.7834 | 474274.1862 | 561218.2433 | 549968.6731 | 521408.0455 | 610790.73 | 597708.9733 | 564104.4201 | 640982.3535 | 626904.1685 | 590554.1361 | 671286.0465 | 656273.3839 | 617354.9684 | 721737.9522 | 705275.7359 | 662394.0192
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 14901674.0408 | 154.5809 | 171.1442 | 738275.6814 | 712999.1838 | 652034.9069 | 913009.784 | 876774.2288 | 788074.5956 | 1081425.848 | 1035598.5251 | 922424.6007 | 1190978.7653 | 1139237.2761 | 1010953.7851 | 1306252.4298 | 1248479.6096 | 1104795.1696 | 1509979.1743 | 1441882.122 | 1271875.7191
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17.1757 | 19.016 | 1655741.5601 | 1599053.593 | 1462328.1266 | 2047620.2621 | 1966354.2576 | 1767426.306 | 2425329.4071 | 2322551.8067 | 2068735.0076 | 2671025.3211 | 2554983.934 | 2267280.6913 | 2929551.2374 | 2799983.2972 | 2477740.1231 | 3386452.1572 | 3233729.9121 | 2852454.0907
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 248361.234 | 2.5763 | 2.8524 | 207092.683 | 200002.4079 | 182901.4035 | 256107.1027 | 245942.7176 | 221061.7071 | 303349.2582 | 290494.2998 | 258748.0398 | 334079.7945 | 319565.8614 | 283581.238 | 366415.0495 | 350209.2762 | 309904.5541 | 423562.1549 | 404460.3456 | 356772.0863
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 158951.1898 | 1.6489 | 1.8255 | 1811457.0953 | 1749437.8631 | 1599853.9412 | 2240190.3423 | 2151281.6116 | 1933645.3222 | 2653421.4451 | 2540978.0432 | 2263290.8409 | 2922224.0272 | 2795269.4353 | 2480508.9117 | 3205063.2194 | 3063309.9589 | 2710761.1686 | 3704933.7505 | 3537848.62 | 3120715.4101
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 465016497.5349 | 464689874.1047 | 463888829.7874 | 467200105.26 | 466756910.7968 | 465651419.1868 | 469205329.1155 | 468667897.104 | 467314517.5698 | 470468313.7951 | 469875460.8657 | 468376466.6434 | 471767748.1639 | 471120022.0237 | 469477239.1179 | 474001734.5303 | 473263101.0499 | 471383155.8607
| Survey, Design, Supervision etc. | [5 empty] | 7070815.0683 | 7067548.834 | 7059538.3909 | 7092651.1456 | 7088219.201 | 7077164.2849 | 7112703.3841 | 7107329.064 | 7093795.2687 | 7125333.2309 | 7119404.7016 | 7104414.7594 | 7138327.5746 | 7131850.3132 | 7115422.4842 | 7160667.4383 | 7153281.1035 | 7134481.6516
| TOTAL COST | [5 empty] | 472087312.6032 | 471757422.9387 | 470948368.1783 | 474292756.4056 | 473845129.9977 | 472728583.4716 | 476318032.4996 | 475775226.168 | 474408312.8385 | 477593647.0261 | 476994865.5674 | 475480881.4029 | 478906075.7386 | 478251872.337 | 476592661.6021 | 481162401.9686 | 480416382.1534 | 478517637.5123
| TOTAL COST IN RS. LAKHS | [5 empty] | 4720.8731 | 4717.5742 | 4709.4837 | 4742.9276 | 4738.4513 | 4727.2858 | 4763.1803 | 4757.7523 | 4744.0831 | 4775.9365 | 4769.9487 | 4754.8088 | 4789.0608 | 4782.5187 | 4765.9266 | 4811.624 | 4804.1638 | 4785.1764
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 47.2087 | 47.1757 | 47.0948 | 47.4293 | 47.3845 | 47.2729 | 47.6318 | 47.5775 | 47.4408 | 47.7594 | 47.6995 | 47.5481 | 47.8906 | 47.8252 | 47.6593 | 48.1162 | 48.0416 | 47.8518
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 3062766.078 | 3060835.7601 | 3056125.757 | 3075661.1723 | 3073025.6666 | 3066485.3846 | 3087567.9132 | 3084357.0148 | 3076312.5879 | 3095094.4035 | 3091543.1953 | 3082610.0606 | 3102857.4939 | 3098968.1184 | 3089154.117 | 3116245.0114 | 3111793.1046 | 3100519.9724
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 3062766.078 | 3060835.7601 | 3056125.757 | 3075661.1723 | 3073025.6666 | 3066485.3846 | 3087567.9132 | 3084357.0148 | 3076312.5879 | 3095094.4035 | 3091543.1953 | 3082610.0606 | 3102857.4939 | 3098968.1184 | 3089154.117 | 3116245.0114 | 3111793.1046 | 3100519.9724
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 4795.5834 | 6031.7 | 6844.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8616590.2871 | 8467404.143 | 8097622.1029 | 9580934.9506 | 9388165.7809 | 8900348.7823 | 10426848.0245 | 10202580.5495 | 9628258.4602 | 10942191.8119 | 10700798.4613 | 10079401.2181 | 11459515.8602 | 11202065.2527 | 10536641.663 | 12320881.171 | 12038530.5157 | 11305197.1335
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1292488.5431 | 1270110.6215 | 1214643.3154 | 1437140.2426 | 1408224.8671 | 1335052.3173 | 1564027.2037 | 1530387.0824 | 1444238.769 | 1641328.7718 | 1605119.7692 | 1511910.1827 | 1718927.379 | 1680309.7879 | 1580496.2495 | 1848132.1756 | 1805779.5774 | 1695779.57
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 404966.7085 | 397955.1854 | 380575.9889 | 450289.4489 | 441229.5895 | 418302.9285 | 490046.0837 | 479505.8516 | 452513.5822 | 514266.4621 | 502921.3398 | 473716.6094 | 538579.9097 | 526480.1206 | 495206.2186 | 579062.7763 | 565792.7226 | 531327.163
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 2436 |  |  |  | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144 | 543844373.6144
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 4608 |  |  |  | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 812 |  |  |  | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 384 |  |  |  | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 538740.1318 | 529412.4789 | 506292.3794 | 599034.4192 | 586981.7992 | 556481.7307 | 651923.9388 | 637901.9318 | 601993.2547 | 684145.0808 | 669052.3027 | 630200.3182 | 716490.0359 | 700393.3005 | 658788.6309 | 770345.6848 | 752692.1091 | 706841.4756
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 19494561.5001 | 85.5822 | 93.9493 | 965821.7349 | 932667.1191 | 852984.4211 | 1194103.2258 | 1146535.7169 | 1030481.3597 | 1414269.5003 | 1354085.7038 | 1205928.5257 | 1557523.957 | 1489561.5651 | 1321586.3805 | 1708278.3172 | 1632383.8324 | 1444210.5378 | 1974738.6508 | 1885267.776 | 1662579.2959
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 9.5091 | 10.4388 | 2166062.3889 | 2091706.0522 | 1913000.5115 | 2678032.5939 | 2571352.2531 | 2311075.4656 | 3171802.6855 | 3036827.6137 | 2704553.3652 | 3493081.5298 | 3340661.2893 | 2963940.9107 | 3831180.516 | 3660970.8562 | 3238951.8839 | 4428774.9644 | 4228117.338 | 3728690.6593
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 324909.3583 | 1.4264 | 1.5658 | 270921.3095 | 261621.1544 | 239269.4718 | 334956.2326 | 321613.1369 | 289058.8908 | 396714.7675 | 379832.6946 | 338273.331 | 436898.8757 | 417834.8398 | 370716.3547 | 479186.7712 | 457897.715 | 405113.4863 | 553931.1882 | 528833.8378 | 466367.8024
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 207941.9893 | 0.91288 | 1.0021 | 2369771.4534 | 2288422.2156 | 2092910.1699 | 2929890.3046 | 2813177.1259 | 2528422.4005 | 3470097.3981 | 3322428.488 | 2958905.2429 | 3821591.1675 | 3654836.444 | 3242687.0969 | 4191486.9424 | 4005269.7794 | 3543561.6963 | 4845282.6372 | 4625754.0043 | 4079358.3454
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 612553215.5985 | 612167152.0116 | 611225151.4023 | 615132234.4595 | 614605133.311 | 613297076.9169 | 617513582.6435 | 616871402.9569 | 615262517.5725 | 619018880.698 | 618308639.0525 | 616522012.1125 | 620571498.7733 | 619793623.6862 | 617830823.4076 | 623249002.2898 | 622358620.9223 | 620103994.4866
| Survey, Design, Supervision etc. | [5 empty] | 8546182.249 | 8542321.6131 | 8532901.607 | 8571972.4376 | 8566701.4261 | 8553620.8622 | 8595785.9194 | 8589364.1226 | 8573275.2687 | 8610838.9 | 8603736.4835 | 8585870.2141 | 8626365.0807 | 8618586.3299 | 8598958.3271 | 8653140.1159 | 8644236.3022 | 8621690.0379
| TOTAL COST | [5 empty] | 621099397.8475 | 620709473.6247 | 619758053.0093 | 623704206.8971 | 623171834.7371 | 621850697.7791 | 626109368.5629 | 625460767.0794 | 623835792.8412 | 627629719.5979 | 626912375.536 | 625107882.3266 | 629197863.854 | 628412210.0161 | 626429781.7347 | 631902142.4057 | 631002857.2246 | 628725684.5244
| TOTAL COST IN RS. LAKHS | [5 empty] | 6210.994 | 6207.0947 | 6197.5805 | 6237.0421 | 6231.7183 | 6218.507 | 6261.0937 | 6254.6077 | 6238.3579 | 6276.2972 | 6269.1238 | 6251.0788 | 6291.9786 | 6284.1221 | 6264.2978 | 6319.0214 | 6310.0286 | 6287.2568
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 62.1099 | 62.0709 | 61.9758 | 62.3704 | 62.3172 | 62.1851 | 62.6109 | 62.5461 | 62.3836 | 62.763 | 62.6912 | 62.5108 | 62.9198 | 62.8412 | 62.643 | 63.1902 | 63.1003 | 62.8726
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 909924.7209 | 909193.8598 | 907813.175 | 913525.3222 | 912537.1039 | 910633.7427 | 916809.7196 | 915616.866 | 913292.8505 | 918867.537 | 917555.9998 | 914987.8365 | 920976.1057 | 919548.2609 | 916741.3595 | 924581.2739 | 922963.1777 | 919767.5291
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 909924.7209 | 909193.8598 | 907813.175 | 913525.3222 | 912537.1039 | 910633.7427 | 916809.7196 | 915616.866 | 913292.8505 | 918867.537 | 917555.9998 | 914987.8365 | 920976.1057 | 919548.2609 | 916741.3595 | 924581.2739 | 922963.1777 | 919767.5291
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 12.9621 | 15.239 | 16.7289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 1.9443 | 2.2858 | 2.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 1555.4579 | 1828.6799 | 2007.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 3314103.665 | 3239069.4172 | 3095630.46 | 3675264.3961 | 3577497.4891 | 3386322.1819 | 3993323.9735 | 3878993.5738 | 3652354.5296 | 4187540.3708 | 4064191.1802 | 3818167.0535 | 4382776.6055 | 4250976.547 | 3986807.2955 | 4708338.0976 | 4563459.2572 | 4271326.5244
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 497115.5497 | 485860.4126 | 464344.569 | 551289.6594 | 536624.6234 | 507948.3273 | 598998.596 | 581849.0361 | 547853.1794 | 628131.0556 | 609628.677 | 572725.058 | 657416.4908 | 637646.482 | 598021.0943 | 706250.7146 | 684518.8886 | 640698.9787
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 155757.8588 | 152231.3626 | 145489.9486 | 172731.8668 | 168136.97 | 159152.0198 | 187680.1857 | 182306.8299 | 171655.1377 | 196808.0626 | 191010.8373 | 179448.0755 | 205983.8703 | 199789.4669 | 187373.9117 | 221284.7679 | 214475.6816 | 200745.8851
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 609 |  |  |  | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 1152 |  |  |  | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 96 |  |  |  | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 207209.6486 | 202518.2382 | 193549.9201 | 229790.7129 | 223677.9752 | 211725.0093 | 249676.9386 | 242528.5919 | 228358.3059 | 261820.0444 | 254107.8105 | 238725.4996 | 274026.914 | 265786.3016 | 249269.4925 | 294382.1863 | 285323.8415 | 267058.6552
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 3897271.7182 | 0 | 0 | 193083.0674 | 184438.8997 | 168465.2126 | 237459.3017 | 224993.8705 | 201589.8039 | 280337.4396 | 264514.8946 | 234508.1099 | 308269.122 | 290375.6999 | 256284.2181 | 337684.1537 | 317679.6748 | 279423.2246 | 389715.1544 | 366100.5376 | 320728.5027
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 433030.1909 | 413643.7909 | 377819.3714 | 532553.4142 | 504597.0111 | 452108.3721 | 628716.8347 | 593231.3841 | 525934.7334 | 691359.6234 | 651229.7866 | 574772.3267 | 757329.1407 | 712464.8063 | 626666.5116 | 874019.8195 | 821058.9763 | 719302.4569
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 64954.5286 | 0 | 0 | 54161.4623 | 51736.6988 | 47255.9421 | 66609.378 | 63112.7172 | 56547.6751 | 78637.0647 | 74198.7046 | 65781.5432 | 86472.142 | 81452.8831 | 71889.929 | 94723.3116 | 89111.8831 | 78380.6195 | 109318.4551 | 102694.3518 | 89967.1055
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 41570.8983 | 0 | 0 | 473754.8605 | 452545.251 | 413351.6954 | 582637.8246 | 552052.2394 | 494627.2645 | 687845.0107 | 649022.3026 | 575396.6848 | 756379.0905 | 712475.2111 | 628827.2484 | 828552.7636 | 779469.1271 | 685601.8634 | 956217.7103 | 898276.1224 | 786949.83
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 181984944.1859 | 181838771.9538 | 181562635.002 | 182705064.4365 | 182507420.7787 | 182126748.5366 | 183361943.9263 | 183123373.2004 | 182658570.1068 | 183773507.3942 | 183511199.9685 | 182997567.2917 | 184195221.1331 | 183909652.1716 | 183348271.896 | 184916254.7885 | 184592635.5399 | 183953505.8214
| Survey, Design, Supervision etc. | [5 empty] | 4240499.5348 | 4239037.8125 | 4236276.443 | 4247700.7374 | 4245724.3008 | 4241917.5784 | 4254269.5323 | 4251883.825 | 4247235.7941 | 4258385.1669 | 4255762.0927 | 4250625.7659 | 4262602.3043 | 4259746.6147 | 4254132.8119 | 4269812.6409 | 4266576.4484 | 4260185.1512
| TOTAL COST | [5 empty] | 186225443.7207 | 186077809.7663 | 185798911.445 | 186952765.1739 | 186753145.0795 | 186368666.115 | 187616213.4586 | 187375257.0254 | 186905805.9008 | 188031892.5611 | 187766962.0612 | 187248193.0576 | 188457823.4374 | 188169398.7863 | 187602404.708 | 189186067.4294 | 188859211.9883 | 188213690.9726
| TOTAL COST IN RS. LAKHS | [5 empty] | 1862.2544 | 1860.7781 | 1857.9891 | 1869.5277 | 1867.5315 | 1863.6867 | 1876.1621 | 1873.7526 | 1869.0581 | 1880.3189 | 1877.6696 | 1872.4819 | 1884.5782 | 1881.694 | 1876.024 | 1891.8607 | 1888.5921 | 1882.1369
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 18.6225 | 18.6078 | 18.5799 | 18.6953 | 18.6753 | 18.6369 | 18.7616 | 18.7375 | 18.6906 | 18.8032 | 18.7767 | 18.7248 | 18.8458 | 18.8169 | 18.7602 | 18.9186 | 18.8859 | 18.8214
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1257011.4478 | 1256078.4838 | 1254341.6387 | 1261561.2683 | 1260290.8303 | 1257877.9697 | 1265737.029 | 1264195.9728 | 1261234.1846 | 1268363.095 | 1266664.315 | 1263382.3225 | 1271060.5817 | 1269206.7557 | 1265610.6765 | 1275686.2788 | 1273577.9366 | 1269468.6228
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1257011.4478 | 1256078.4838 | 1254341.6387 | 1261561.2683 | 1260290.8303 | 1257877.9697 | 1265737.029 | 1264195.9728 | 1261234.1846 | 1268363.095 | 1266664.315 | 1263382.3225 | 1271060.5817 | 1269206.7557 | 1265610.6765 | 1275686.2788 | 1273577.9366 | 1269468.6228
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 26.1911 | 31.6347 | 35.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3.9287 | 4.7452 | 5.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 3142.9283 | 3796.1589 | 4225.0539 | 3932659.3307 | 3842800.086 | 3673289.6566 | 4359709.4552 | 4242258.0967 | 4015396.5614 | 4736703.0264 | 4599136.5048 | 4329598.4627 | 4967148.6419 | 4818636.2898 | 4525778.1752 | 5198922.7469 | 5040161.1033 | 4725490.2715 | 5585579.1548 | 5410971.3232 | 5062725.6683
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 1257.1713 | 1518.4636 | 1690.0215 | 589898.8996 | 576420.0129 | 550993.4485 | 653956.4183 | 636338.7145 | 602309.4842 | 710505.454 | 689870.4757 | 649439.7694 | 745072.2963 | 722795.4435 | 678866.7263 | 779838.412 | 756024.1655 | 708823.5407 | 837836.8732 | 811645.6985 | 759408.8502
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 184829.0393 | 180605.7907 | 172639.057 | 204899.7491 | 199379.713 | 188717.564 | 222617.8767 | 216152.4583 | 203484.578 | 233448.472 | 226468.6161 | 212704.7277 | 244341.5043 | 236879.9472 | 222090.8941 | 262513.7705 | 254307.4666 | 237940.4476
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 913.5 |  |  |  | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 1152 |  |  |  | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 144 |  |  |  | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 245883.9675 | 240265.6452 | 229667.2451 | 272584.6731 | 265241.1928 | 251056.9959 | 296155.6634 | 287554.511 | 270702.0258 | 310563.9499 | 301278.4249 | 282967.8851 | 325055.2983 | 315128.9508 | 295454.6017 | 349230.4438 | 338313.3359 | 316539.7684
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 5487836.4748 | 21028.6958 | 23851.7409 | 271884.6353 | 259601.7377 | 237204.1939 | 334138.9523 | 316377.9343 | 283445.0631 | 394424.9013 | 371847.2819 | 329539.329 | 433736.8534 | 408188.0682 | 360079.618 | 475158.7595 | 446581.6237 | 392559.741 | 548464.3868 | 514709.8462 | 450589.2246
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 2336.5218 | 2650.1934 | 609759.6083 | 582212.5758 | 531981.2802 | 749378.2664 | 709545.374 | 635686.347 | 884582.4369 | 833947.2832 | 739062.6245 | 972747.9212 | 915449.2907 | 807555.7728 | 1065645.4297 | 1001555.0736 | 880399.415 | 1230049.0216 | 1154347.2245 | 1010542.9781
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 91463.9412 | 350.4783 | 397.529 | 76265.9803 | 72820.5218 | 66537.818 | 93728.8521 | 88746.7336 | 79508.7798 | 110639.5796 | 104306.3631 | 92438.6181 | 121666.9206 | 114500.2664 | 101005.4321 | 133286.1217 | 125269.9892 | 110116.3861 | 153848.9812 | 144380.542 | 126394.1558
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 58536.9224 | 224.3061 | 254.4186 | 667104.9369 | 636967.2217 | 582011.8839 | 819854.1429 | 776275.1344 | 695469.9764 | 967773.6975 | 912376.5204 | 808568.3583 | 1064230.7751 | 1001543.4492 | 883502.9994 | 1165864.9038 | 1095747.1191 | 963197.2799 | 1345729.9626 | 1262908.7296 | 1105580.2982
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 251402289.5583 | 251215696.7521 | 250868327.7436 | 252312253.6697 | 252058166.0537 | 251575593.9321 | 253147405.796 | 252839194.5586 | 252246836.9261 | 253672618.9905 | 253332863.0092 | 252676464.4969 | 254212116.3364 | 253841351.1328 | 253122135.2903 | 255137255.7548 | 254715587.3266 | 253893724.5515
| Survey, Design, Supervision etc. | [5 empty] | 4934672.9886 | 4932807.0605 | 4929333.3704 | 4943772.6297 | 4941231.7535 | 4936406.0323 | 4952124.1509 | 4949042.0386 | 4943118.4622 | 4957376.2829 | 4953978.7231 | 4947414.738 | 4962771.2564 | 4959063.6043 | 4951871.4459 | 4972022.6505 | 4967805.9663 | 4959587.3385
| TOTAL COST | [5 empty] | 256336962.5469 | 256148503.8126 | 255797661.114 | 257256026.2994 | 256999397.8072 | 256511999.9645 | 258099529.947 | 257788236.5972 | 257189955.3884 | 258629995.2734 | 258286841.7323 | 257623879.2348 | 259174887.5927 | 258800414.7372 | 258074006.7362 | 260109278.4053 | 259683393.2929 | 258853311.89
| TOTAL COST IN RS. LAKHS | [5 empty] | 2563.3696 | 2561.485 | 2557.9766 | 2572.5603 | 2569.994 | 2565.12 | 2580.9953 | 2577.8824 | 2571.8996 | 2586.3 | 2582.8684 | 2576.2388 | 2591.7489 | 2588.0041 | 2580.7401 | 2601.0928 | 2596.8339 | 2588.5331
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 25.6337 | 25.6149 | 25.5798 | 25.7256 | 25.6999 | 25.6512 | 25.81 | 25.7788 | 25.719 | 25.863 | 25.8287 | 25.7624 | 25.9175 | 25.88 | 25.8074 | 26.0109 | 25.9683 | 25.8853
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1645363.8665 | 1644242.1332 | 1642171.2042 | 1650806.9525 | 1649272.2177 | 1646380.6919 | 1655823.4342 | 1653955.4594 | 1650393.3411 | 1658986.461 | 1656923.5425 | 1652968.7639 | 1662241.2357 | 1659986.2277 | 1655645.3607 | 1667834.4664 | 1665263.2778 | 1660289.7859
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1645363.8665 | 1644242.1332 | 1642171.2042 | 1650806.9525 | 1649272.2177 | 1646380.6919 | 1655823.4342 | 1653955.4594 | 1650393.3411 | 1658986.461 | 1656923.5425 | 1652968.7639 | 1662241.2357 | 1659986.2277 | 1655645.3607 | 1667834.4664 | 1665263.2778 | 1660289.7859
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 6.3189 | 7.4431 | 8.1777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5055.1374 | 5954.461 | 6542.1879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 4466355.9779 | 4363788.9858 | 4171712.5808 | 4950410.5574 | 4816120.7661 | 4558469.1697 | 5378296.6414 | 5220873.6849 | 4914382.1674 | 5640003.2716 | 5469996.4751 | 5136821.6372 | 5903292.6983 | 5721507.3444 | 5363383.6521 | 6342628.8988 | 6142642.8294 | 5746142.3674
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 669953.3967 | 654568.3479 | 625756.8871 | 742561.5836 | 722418.1149 | 683770.3754 | 806744.4962 | 783131.0527 | 737157.3251 | 846000.4907 | 820499.4713 | 770523.2456 | 885493.9047 | 858226.1017 | 804507.5478 | 951394.3348 | 921396.4244 | 861921.3551
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 209911.9744 | 205091.4809 | 196064.1804 | 232661.8073 | 226350.3903 | 214241.155 | 252771.806 | 245373.1652 | 230968.5275 | 265071.6217 | 257081.5594 | 241422.8461 | 277445.8265 | 268902.1898 | 252070.918 | 298093.9633 | 288694.9205 | 270059.9986
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 279252.5962 | 272839.74 | 260830.4342 | 309517.4248 | 301121.1453 | 285011.8434 | 336270.3975 | 326427.7496 | 307264.8006 | 352633.2348 | 342003.8001 | 321172.5141 | 369095.0341 | 357729.1618 | 335337.984 | 396563.9093 | 384060.0629 | 359269.4318
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 7078401.2313 | 161099.2384 | 176969.7293 | 350686.2033 | 334764.5756 | 305943.1753 | 430818.6029 | 407761.998 | 365300.3223 | 508512.363 | 479179.6693 | 424570.5481 | 559204.5848 | 526000.4365 | 463875.0179 | 612633.3653 | 575483.5727 | 505696.2573 | 707213.6193 | 663319.1548 | 580449.9465
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17899.9154 | 19663.3033 | 786489.0257 | 750781.3607 | 686143.1891 | 966203.1185 | 914493.7369 | 819264.3219 | 1140448.0391 | 1074663.1823 | 952190.5155 | 1254136.219 | 1179668.7949 | 1040339.219 | 1373961.7186 | 1290645.3409 | 1134132.3183 | 1586078.2236 | 1487635.4726 | 1301783.4993
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 117973.3539 | 2684.9873 | 2949.4955 | 98370.4984 | 93904.3448 | 85819.694 | 120848.3262 | 114380.7501 | 102469.8846 | 142642.0946 | 134414.0216 | 119095.693 | 156861.6991 | 147547.6498 | 130120.9351 | 171848.9319 | 161428.0954 | 141852.1527 | 198379.5072 | 186066.7321 | 162821.206
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 75502.9465 | 1718.3919 | 1887.6771 | 860455.0132 | 821389.1924 | 750672.0724 | 1057070.4612 | 1000498.0295 | 896312.6883 | 1247702.3843 | 1175730.7381 | 1041740.0318 | 1372082.4597 | 1290611.6873 | 1138178.7504 | 1503177.0439 | 1412025.1111 | 1240792.6964 | 1735242.2148 | 1627541.3367 | 1424210.7665
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 329072773.3033 | 328848426.6456 | 328434240.8308 | 330161390.4995 | 329854443.5487 | 329276138.3781 | 331164686.8397 | 330791091.8812 | 330078668.2265 | 331797292.1989 | 331384708.4918 | 330593752.7829 | 332448247.1408 | 331997245.5352 | 331129072.1442 | 333566893.2886 | 333052655.5509 | 332057957.1886
| Survey, Design, Supervision etc. | [5 empty] | 5711377.826 | 5709134.3594 | 5704992.5013 | 5722263.998 | 5719194.5285 | 5713411.4768 | 5732296.9614 | 5728561.0118 | 5721436.7753 | 5738623.015 | 5734497.1779 | 5726587.6208 | 5745132.5644 | 5740622.5483 | 5731940.8144 | 5756319.0259 | 5751176.6485 | 5741229.6649
| TOTAL COST | [5 empty] | 334784151.1293 | 334557561.0051 | 334139233.3321 | 335883654.4975 | 335573638.0771 | 334989549.8549 | 336896983.8011 | 336519652.8929 | 335800105.0017 | 337535915.2139 | 337119205.6697 | 336320340.4037 | 338193379.7052 | 337737868.0836 | 336861012.9587 | 339323212.3145 | 338803832.1994 | 337799186.8535
| TOTAL COST IN RS. LAKHS | [5 empty] | 3347.8415 | 3345.5756 | 3341.3923 | 3358.8365 | 3355.7364 | 3349.8955 | 3368.9698 | 3365.1965 | 3358.0011 | 3375.3592 | 3371.1921 | 3363.2034 | 3381.9338 | 3377.3787 | 3368.6101 | 3393.2321 | 3388.0383 | 3377.9919
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 33.4784 | 33.4558 | 33.4139 | 33.5884 | 33.5574 | 33.499 | 33.6897 | 33.652 | 33.58 | 33.7536 | 33.7119 | 33.632 | 33.8193 | 33.7738 | 33.6861 | 33.9323 | 33.8804 | 33.7799
ESTIMATE FOR A 765 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 947807.8593 | 946564.1674 | 944227.9232 | 954201.6768 | 952529.7253 | 949334.8978 | 960004.3577 | 957994.053 | 954113.7121 | 963629.444 | 961423.5196 | 957146.6855 | 967337.1903 | 964939.8956 | 960275.9897 | 973663.5919 | 970953.8214 | 965660.5102
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 947807.8593 | 946564.1674 | 944227.9232 | 954201.6768 | 952529.7253 | 949334.8978 | 960004.3577 | 957994.053 | 954113.7121 | 963629.444 | 961423.5196 | 957146.6855 | 967337.1903 | 964939.8956 | 960275.9897 | 973663.5919 | 970953.8214 | 965660.5102
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 33.1275 | 39.4561 | 43.6035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 4.9691 | 5.9184 | 6.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3975.2993 | 4734.735 | 5232.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 6019909.3047 | 5887557.213 | 5636266.8142 | 6685615.8414 | 6513836.1661 | 6181104.1598 | 7269979.0049 | 7069546.8351 | 6676617.3372 | 7626261.5822 | 7410232.8633 | 6984431.5722 | 7984130.4966 | 7753482.5438 | 7296902.5122 | 8580455.5749 | 8327164.9246 | 7823094.8627
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 902986.3957 | 883133.582 | 845440.0221 | 1002842.3762 | 977075.4249 | 927165.624 | 1090496.8507 | 1060432.0253 | 1001492.6006 | 1143939.2373 | 1111534.9295 | 1047664.7358 | 1197619.5745 | 1163022.3816 | 1094535.3768 | 1287068.3362 | 1249074.7387 | 1173464.2294
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 282926.6305 | 276706.2825 | 264896.0139 | 314213.8307 | 306140.4458 | 290502.5449 | 341678.0154 | 332258.0066 | 313790.9146 | 358422.7575 | 348269.7345 | 328257.718 | 375242.0551 | 364401.9503 | 342943.3795 | 403268.4317 | 391364.1543 | 367673.6239
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 609 |  |  |  | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036 | 135961093.4036
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 1920 |  |  |  | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 376386.3227 | 368111.1952 | 352399.6181 | 418008.6832 | 407268.4017 | 386464.8032 | 454545.1642 | 442013.426 | 417446.0644 | 476821.2289 | 463314.3385 | 436691.7145 | 499196.4771 | 484775.5398 | 456228.5185 | 536480.86 | 520644.22 | 489127.9516
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 8041180.9998 | 0 | 0 | 331987.7779 | 317550.2652 | 291021.642 | 409472.7784 | 388701.1819 | 350005.0601 | 484181.8575 | 457852.248 | 408371.2605 | 532801.6904 | 503043.927 | 446893.8032 | 583979.2987 | 550726.3115 | 487774.7185 | 674470.3973 | 635238.0901 | 560659.7667
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 893464.5555 | 854609.4932 | 783214.1402 | 1101996.6346 | 1046094.9224 | 941953.6992 | 1303057.9947 | 1232198.239 | 1099032.1664 | 1433906.4786 | 1353820.6783 | 1202706.2435 | 1571638.5944 | 1482146.2472 | 1312727.3085 | 1815173.4307 | 1709589.1947 | 1508879.7318
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 134019.6833 | 0 | 0 | 74500.3433 | 71260.4661 | 65307.2603 | 91888.511 | 87227.2217 | 78543.5455 | 108653.7427 | 102745.1971 | 91641.3227 | 119564.368 | 112886.521 | 100286.0466 | 131048.9757 | 123586.7764 | 109460.0055 | 151355.8013 | 142551.8014 | 125815.9121
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 85772.5973 | 0 | 0 | 586494.6852 | 560989.1546 | 514123.2831 | 723380.8721 | 686685.4521 | 618324.2915 | 855363.0737 | 808848.7829 | 721434.9137 | 941255.614 | 888685.094 | 789489.4267 | 1031666.7595 | 972921.5237 | 861710.2769 | 1191529.718 | 1122221.3242 | 990470.1175
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 189561571.8535 | 189312833.4896 | 188845584.6318 | 190840335.3654 | 190505945.0545 | 189866979.566 | 192000871.5417 | 191598810.5978 | 190822742.4179 | 192725888.7949 | 192284703.924 | 191429337.0984 | 193467438.0695 | 192987979.112 | 192055197.9343 | 194732718.3881 | 194190764.2858 | 193132102.0336
| Survey, Design, Supervision etc. | [5 empty] | 4316265.8115 | 4313778.4279 | 4309105.9393 | 4329053.4466 | 4325709.5435 | 4319319.8886 | 4340658.8084 | 4336638.199 | 4328877.5172 | 4347908.9809 | 4343497.1322 | 4334943.464 | 4355324.4737 | 4350529.8841 | 4341202.0723 | 4367977.2769 | 4362557.7358 | 4351971.1133
| TOTAL COST | [5 empty] | 193877837.665 | 193626611.9175 | 193154690.5711 | 195169388.812 | 194831654.598 | 194186299.4546 | 196341530.3501 | 195935448.7968 | 195151619.9351 | 197073797.7759 | 196628201.0562 | 195764280.5623 | 197822762.5431 | 197338508.9961 | 196396400.0066 | 199100695.6649 | 198553322.0217 | 197484073.147
| TOTAL COST IN RS. LAKHS | [5 empty] | 1938.7784 | 1936.2661 | 1931.5469 | 1951.6939 | 1948.3165 | 1941.863 | 1963.4153 | 1959.3545 | 1951.5162 | 1970.738 | 1966.282 | 1957.6428 | 1978.2276 | 1973.3851 | 1963.964 | 1991.007 | 1985.5332 | 1974.8407
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 19.3878 | 19.3627 | 19.3155 | 19.5169 | 19.4832 | 19.4186 | 19.6342 | 19.5935 | 19.5152 | 19.7074 | 19.6628 | 19.5764 | 19.7823 | 19.7339 | 19.6396 | 19.9101 | 19.8553 | 19.7484
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH TRIPPLE ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1294717.2419 | 1293333.1509 | 1290780.4992 | 1301665.9944 | 1299810.9605 | 1296324.9155 | 1307952.5308 | 1305729.7802 | 1301506.2142 | 1311868.512 | 1309435.0018 | 1304788.4944 | 1315864.3074 | 1313225.8596 | 1308169.0556 | 1322659.974 | 1319689.3125 | 1313970.538
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1294717.2419 | 1293333.1509 | 1290780.4992 | 1301665.9944 | 1299810.9605 | 1296324.9155 | 1307952.5308 | 1305729.7802 | 1301506.2142 | 1311868.512 | 1309435.0018 | 1304788.4944 | 1315864.3074 | 1313225.8596 | 1308169.0556 | 1322659.974 | 1319689.3125 | 1313970.538
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 7142856.0815 | 6983337.2339 | 6686510.5709 | 7929272.5663 | 7721622.0606 | 7326915.7396 | 8621245.0377 | 8378603.2414 | 7911450.7189 | 9043561.9082 | 8781884.791 | 8275191.8837 | 9467959.7046 | 9188451.6777 | 8644766.4055 | 10175411.8588 | 9868311.4143 | 9267623.3067
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1071428.4122 | 1047500.5851 | 1002976.5856 | 1189390.8849 | 1158243.3091 | 1099037.3609 | 1293186.7556 | 1256790.4862 | 1186717.6078 | 1356534.2862 | 1317282.7187 | 1241278.7826 | 1420193.9557 | 1378267.7517 | 1296714.9608 | 1526311.7788 | 1480246.7122 | 1390143.496
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 335703.4303 | 328206.2858 | 314255.8816 | 372663.8154 | 362904.5558 | 344353.9558 | 405185.4747 | 393781.6774 | 371826.2155 | 425033.7288 | 412735.3001 | 388921.5 | 444979.7832 | 431843.3288 | 406290.9435 | 478228.9642 | 463795.7079 | 435564.2756
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 913.5 |  |  |  | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054 | 203941640.1054
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 1920 |  |  |  | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 446596.9831 | 436623.2925 | 418064.6249 | 495766.5625 | 482783.5081 | 458105.0531 | 539031.1635 | 523860.328 | 494652.2767 | 565435.929 | 549074.9371 | 517394.679 | 591970.8015 | 574494.9571 | 540501.8038 | 636203.2478 | 617002.2265 | 579445.0514
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 7325335.2379 | 0 | 0 | 302433.4072 | 289075.9709 | 265023.8958 | 372694.2191 | 353429.7021 | 318220.6489 | 440581.1789 | 416130.1792 | 371020.7654 | 484802.6605 | 457152.8518 | 405921.5503 | 531372.1205 | 500461.4549 | 442988.5363 | 613747.8109 | 577260.2523 | 509122.9904
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 813926.1375 | 777977.8386 | 713247.5141 | 1003016.0656 | 951170.2923 | 856413.668 | 1185717.347 | 1119913.4137 | 998512.3711 | 1304728.7355 | 1230315.9838 | 1092439.3657 | 1430059.1379 | 1346870.5812 | 1192196.1652 | 1651753.3223 | 1553555.911 | 1370181.0025
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 122088.9206 | 0 | 0 | 67868.139 | 64870.6384 | 59473.1871 | 83635.149 | 79312.0587 | 71410.9048 | 98869.4502 | 93382.4775 | 83259.6145 | 108793.0552 | 102588.2477 | 91091.5909 | 119243.5627 | 112306.9965 | 99409.6778 | 137729.2348 | 129541.1754 | 114250.7047
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 78136.9092 | 0 | 0 | 534283.4821 | 510686.0309 | 468195.2671 | 658407.3067 | 624374.3165 | 562173.4646 | 778337.4482 | 735141.9382 | 655450.9579 | 856459.7938 | 807613.2189 | 717107.2181 | 938730.1139 | 884122.8593 | 782590.3225 | 1084256.2683 | 1019796.7892 | 899424.4604
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 258943448.3797 | 258666630.1827 | 258156099.8338 | 260333198.8762 | 259962192.1099 | 259264983.1024 | 261590506.1627 | 261145956.0484 | 260301242.8346 | 262373702.404 | 261887000.3559 | 260957698.8771 | 263172861.4866 | 262645171.9138 | 261633811.1221 | 264531994.7925 | 263937862.4955 | 262794107.5942
| Survey, Design, Supervision etc. | [5 empty] | 5010084.5768 | 5007316.3948 | 5002211.0913 | 5023982.0817 | 5020272.0141 | 5013299.924 | 5036555.1546 | 5032109.6535 | 5023662.5213 | 5044387.117 | 5039520.0965 | 5030227.0818 | 5052378.7079 | 5047101.8121 | 5036988.2042 | 5065970.0409 | 5060028.7179 | 5048591.1689
| TOTAL COST | [5 empty] | 263953532.9564 | 263673946.5775 | 263158310.9251 | 265357180.9579 | 264982464.124 | 264278283.0264 | 266627061.3173 | 266178065.7019 | 265324905.3559 | 267418089.5211 | 266926520.4524 | 265987925.9588 | 268225240.1945 | 267692273.7259 | 266670799.3263 | 269597964.8335 | 268997891.2135 | 267842698.7631
| TOTAL COST IN RS. LAKHS | [5 empty] | 2639.5353 | 2636.7395 | 2631.5831 | 2653.5718 | 2649.8246 | 2642.7828 | 2666.2706 | 2661.7807 | 2653.2491 | 2674.1809 | 2669.2652 | 2659.8793 | 2682.2524 | 2676.9227 | 2666.708 | 2695.9796 | 2689.9789 | 2678.427
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 26.3954 | 26.3674 | 26.3158 | 26.5357 | 26.4982 | 26.4278 | 26.6627 | 26.6178 | 26.5325 | 26.7418 | 26.6927 | 26.5988 | 26.8225 | 26.7692 | 26.6671 | 26.9598 | 26.8998 | 26.7843
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1779985.9137 | 1778341.6973 | 1775345.0901 | 1788164.5598 | 1785951.5701 | 1781839.741 | 1795592.0609 | 1792932.3594 | 1787934.0786 | 1800229.7196 | 1797313.0473 | 1791804.5996 | 1804969.4411 | 1801802.2966 | 1795797.7893 | 1813045.8783 | 1809471.5607 | 1802664.5581
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1779985.9137 | 1778341.6973 | 1775345.0901 | 1788164.5598 | 1785951.5701 | 1781839.741 | 1795592.0609 | 1792932.3594 | 1787934.0786 | 1800229.7196 | 1797313.0473 | 1791804.5996 | 1804969.4411 | 1801802.2966 | 1795797.7893 | 1813045.8783 | 1809471.5607 | 1802664.5581
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8111811.0163 | 7929102.5915 | 7592848.1894 | 9002736.6774 | 8764521.2587 | 8316329.7119 | 9787703.3704 | 9509126.779 | 8978022.3819 | 10267042.3324 | 9966516.4364 | 9390171.2997 | 10748868.8776 | 10427789.6464 | 9809137.8897 | 11552220.3544 | 11199351.082 | 10515553.7314
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1216771.6524 | 1189365.3887 | 1138927.2284 | 1350410.5016 | 1314678.1888 | 1247449.4568 | 1468155.5056 | 1426369.0169 | 1346703.3573 | 1540056.3499 | 1494977.4655 | 1408525.695 | 1612330.3316 | 1564168.447 | 1471370.6835 | 1732833.0532 | 1679902.6623 | 1577333.0597
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 381242.8464 | 372655.8268 | 356852.3786 | 423115.0047 | 411919.2404 | 390854.9157 | 460007.2518 | 446914.5734 | 421953.4702 | 482535.4579 | 468411.1954 | 441323.8458 | 505180.5766 | 490090.3385 | 461014.6418 | 542936.8807 | 526352.5587 | 494215.1177
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Moose Conductor (kM) | 223253.0269 | 1218 |  |  |  | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072 | 271922186.8072
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 3840 |  |  |  | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 163660.9478 | 100 |  |  |  | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 507179.5212 | 495755.9351 | 474732.1037 | 562883.3892 | 547989.3067 | 519966.7636 | 611962.3224 | 594544.7147 | 561338.1628 | 641932.3137 | 623142.3567 | 587107.1915 | 672057.8376 | 651982.8123 | 613302.4855 | 722286.2535 | 700223.6008 | 657470.1377
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 9447553.3584 | 0 | 0 | 390051.1935 | 372678.2408 | 341739.6703 | 480435.4639 | 455346.8748 | 409967.4353 | 567868.2148 | 536003.0215 | 477801.3034 | 624851.2861 | 588806.6921 | 522676.522 | 684875.2829 | 644570.5905 | 570358.1371 | 791073.6 | 743484.0933 | 655466.1317
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1049728.1509 | 1002973.064 | 919709.408 | 1292975.4852 | 1225455.6349 | 1103327.8837 | 1528279.521 | 1442522.0846 | 1285886.2816 | 1681635.6318 | 1584630.3523 | 1406657.0444 | 1843175.6559 | 1734705.3554 | 1534980.5426 | 2128982.6599 | 2000907.049 | 1764028.0608
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 157459.2226 | 0 | 0 | 87530.1736 | 83631.5634 | 76688.7351 | 107813.0262 | 102182.9741 | 91999.5154 | 127433.5375 | 120282.7688 | 107221.9025 | 140220.9311 | 132132.276 | 117292.2105 | 153690.7293 | 144646.0788 | 127992.2932 | 177522.3629 | 166842.9499 | 147091.1133
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 100773.9025 | 0 | 0 | 689070.4031 | 658379.0793 | 603722.5276 | 848744.6374 | 804422.7523 | 724254.7405 | 1003204.6723 | 946911.1345 | 844091.0893 | 1103871.8374 | 1040194.9064 | 923368.3367 | 1209911.1481 | 1138708.2622 | 1007603.407 | 1397522.719 | 1313450.3687 | 1157956.4918
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 355997182.7369 | 355668339.4692 | 355069018.0207 | 357632911.965 | 357190314.0101 | 356367948.2024 | 359118412.1753 | 358586471.8729 | 357586815.7284 | 360045943.9198 | 359462609.4602 | 358360919.9251 | 360993888.2191 | 360360459.3106 | 359159557.8598 | 362609175.6631 | 361894312.1444 | 360532911.6237
| Survey, Design, Supervision etc. | [5 empty] | 5980621.9204 | 5977333.4877 | 5971340.2732 | 5996979.2126 | 5992553.2331 | 5984329.575 | 6011834.2147 | 6006514.8117 | 5996518.2503 | 6021109.5322 | 6015276.1876 | 6004259.2922 | 6030588.9752 | 6024254.6861 | 6012245.6716 | 6046741.8496 | 6039593.2144 | 6025979.2092
| TOTAL COST | [5 empty] | 361977804.6573 | 361645672.9569 | 361040358.2939 | 363629891.1776 | 363182867.2432 | 362352277.7774 | 365130246.3901 | 364592986.6847 | 363583333.9787 | 366067053.4519 | 365477885.6478 | 364365179.2173 | 367024477.1943 | 366384713.9967 | 365171803.5314 | 368655917.5127 | 367933905.3588 | 366558890.8329
| TOTAL COST IN RS. LAKHS | [5 empty] | 3619.778 | 3616.4567 | 3610.4036 | 3636.2989 | 3631.8287 | 3623.5228 | 3651.3025 | 3645.9299 | 3635.8333 | 3660.6705 | 3654.7789 | 3643.6518 | 3670.2448 | 3663.8471 | 3651.718 | 3686.5592 | 3679.3391 | 3665.5889
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 36.1978 | 36.1646 | 36.104 | 36.363 | 36.3183 | 36.2352 | 36.513 | 36.4593 | 36.3583 | 36.6067 | 36.5478 | 36.4365 | 36.7024 | 36.6385 | 36.5172 | 36.8656 | 36.7934 | 36.6559
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 13309062.3407 | 13941842.3508 | 14341910.5814
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 12243.3706 | 13283.528 | 13922.4666 | 734602.2359 | 797011.6778 | 835347.9947
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 282821.8608 | 306849.4959 | 321608.978
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) x No. of Ckts. | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 2436 |  |  |  | 876960000 | 876960000 | 876960000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 21000 | 1680 |  |  |  | 35280000 | 35280000 | 35280000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 40 |  |  |  | 1240000 | 1240000 | 1240000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 840 |  |  |  | 49560000 | 49560000 | 49560000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 40 |  |  |  | 1800000 | 1800000 | 1800000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 812 |  |  |  | 1055600 | 1055600 | 1055600
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 5040 | 10080 |  |  |  | 50803200 | 50803200 | 50803200
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 1680 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 0 |  |  |  | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 380000 | 100 |  |  |  | 38000000 | 38000000 | 38000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 484837.4757 | 526027.7073 | 551329.6765
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 110476.1386 | 135501.5486 | 151914.4961 | 33142841.5799 | 40650464.5715 | 45574348.8348
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 12275.1265 | 15055.7276 | 16879.3885 | 69968221.113 | 85817647.4288 | 96212514.2067
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 1841.269 | 2258.3591 | 2531.9083 | 8653964.1903 | 10614287.9715 | 11899968.8624
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 1178.4121 | 1445.3499 | 1620.4213 | 63634255.8333 | 78048891.9773 | 87502749.7628
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 1565772040.0812 | 1640216747.1546 | 1687283597.8152
| Survey, Design, Supervision etc. | [5 empty] | 34966782.7415 | 36344009.8224 | 37214746.5596
| TOTAL COST | [5 empty] | 1600738822.8227 | 1676560756.9769 | 1724498344.3747
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 288132988.1081 | 301780936.2558 | 310409701.9875
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
v) | Contengency at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1984916140.3001 | 2078935338.6514 | 2138377947.0247
| TOTAL COST IN RS. LAKHS | [5 empty] | 19849.1614 | 20789.3534 | 21383.7795
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 198.4916 | 207.8935 | 213.8378
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 8411202.1434 | 8912246.9919 | 9223024.2025
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
III | Detailed survey (Rs. Per kM) | 50000 | 100 |  |  |  | 5000000 | 5000000 | 5000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 520753.4201 | 578395.2043 | 613278.8096 | 31245205.2042 | 34703712.2574 | 36796728.5749
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 12029404.0036 | 13360929.2191 | 14166740.5013
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 1218 |  |  |  | 438480000 | 438480000 | 438480000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of suspn.x1) | 24000 | 210 |  |  |  | 5040000 | 5040000 | 5040000
| b) Double 'I' Suspension Insulator Sring (No. Suspn. X 2) | 21000 | 420 |  |  |  | 8820000 | 8820000 | 8820000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'V' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
| f) Single 'I' Suspension Pilot strings (No. of Suspn x 1) | 15000 | 210 |  |  |  | 3150000 | 3150000 | 3150000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 406 |  |  |  | 527800 | 527800 | 527800
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 2700 | 5040 |  |  |  | 13608000 | 13608000 | 13608000
| f) Quad Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 1000 | 840 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190000 | 100 |  |  |  | 19000000 | 19000000 | 19000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 20621835.4348 | 22904450.0899 | 24285840.8595
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 48382.6073 | 59272.006 | 66421.8968 | 14514782.1992 | 17781601.804 | 19926569.0329
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 5375.8453 | 6585.7784 | 7380.2108 | 30642317.976 | 37538937.1417 | 42067201.2916
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 806.3768 | 987.8668 | 1107.0316 | 3789970.9076 | 4642973.8044 | 5203048.5808
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 516.0811 | 632.2347 | 708.5002 | 27868381.8224 | 34140675.4636 | 38259012.5431
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 989553193.3401 | 1048499646.1046 | 1085061670.8834
| Survey, Design, Supervision etc. | [5 empty] | 23306734.0768 | 24397243.4529 | 25073640.9113
| TOTAL COST | [5 empty] | 1012859927.4169 | 1072896889.5575 | 1110135311.7948
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 182314786.935 | 193121440.1204 | 199824356.1231
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
v) | Contengency at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1255946309.997 | 1330392143.0513 | 1376567786.6255
| TOTAL COST IN RS. LAKHS | [5 empty] | 12559.4631 | 13303.9214 | 13765.6779
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 125.5946 | 133.0392 | 137.6568
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 5050227.0344 | 5357651.6793 | 5546861.9223
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 10366.8386 | 11627.9013 | 12386.9423 | 130622166.4713 | 146511556.3957 | 156075473.2845
| b) 'B' Type towers | 60000 | 25 | 16898.4575 | 18612.4108 | 19653.708 | 25347686.3224 | 27918616.1635 | 29480562.0497
| c) 'C' Type towers | 60000 | 25 | 20290.3432 | 22180.6901 | 23333.1622 | 30435514.7251 | 33271035.0929 | 34999743.239
| d) 'D' Type towers | 60000 | 20 | 25560.0611 | 27781.5378 | 29139.1942 | 30672073.3304 | 33337845.351 | 34967032.9907
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 361795.7347 | 401731.755 | 425871.3526 | 21707744.0849 | 24103905.3003 | 25552281.1564
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 7163555.548 | 7954288.7491 | 8432252.7816
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 609 |  |  |  | 219240000 | 219240000 | 219240000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) | 21000 | 840 |  |  |  | 17640000 | 17640000 | 17640000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 203 |  |  |  | 263900 | 263900 | 263900
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 900 | 5040 |  |  |  | 4536000 | 4536000 | 4536000
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 840 |  |  |  | 420000 | 420000 | 420000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 3360 |  |  |  | 3024000 | 3024000 | 3024000
V | ERECTION
2 | Stringing of Conductor (Route kM) | 95000 | 100 |  |  |  | 9500000 | 9500000 | 9500000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 12280380.9395 | 13635923.5699 | 14455290.4828
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 21646.7931 | 26473.7232 | 29642.2493 | 6494037.9255 | 7942116.9663 | 8892674.7876
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 2405.1992 | 2941.5248 | 3293.5833 | 13709635.6204 | 16766691.3734 | 18773424.5515
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 360.7799 | 441.2287 | 494.0375 | 1695665.4583 | 2073774.9857 | 2321976.1945
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 230.8991 | 282.3864 | 316.184 | 12468552.8169 | 15248864.5753 | 17073935.5921
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 594144356.9927 | 630311962.2731 | 652571990.8604
| Survey, Design, Supervision etc. | [5 empty] | 16991670.6044 | 17660771.3021 | 18072581.8309
| TOTAL COST | [5 empty] | 611136027.5971 | 647972733.5751 | 670644572.6913
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 110004484.9675 | 116635092.0435 | 120716023.0844
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
v) | Contengency at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 757808674.2204 | 803486189.6332 | 831599270.1372
| TOTAL COST IN RS. LAKHS | [5 empty] | 7578.0867 | 8034.8619 | 8315.9927
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 75.7809 | 80.3486 | 83.1599

## Bersi-Antifog-Plain
CERC
Capital Cost Benchmarking
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1737658.031 | 1736722.0456 | 1733571.1739 | 1746597.6427 | 1744866.3507 | 1740524.9494 | 1754491.9344 | 1752391.8651 | 1747077.9284 | 1759465.6941 | 1757148.2192 | 1751261.5202 | 1764584.8558 | 1762051.8375 | 1755598.6414 | 1773390.3629 | 1770499.8734 | 1763110.8499
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1737658.031 | 1736722.0456 | 1733571.1739 | 1746597.6427 | 1744866.3507 | 1740524.9494 | 1754491.9344 | 1752391.8651 | 1747077.9284 | 1759465.6941 | 1757148.2192 | 1751261.5202 | 1764584.8558 | 1762051.8375 | 1755598.6414 | 1773390.3629 | 1770499.8734 | 1763110.8499
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 10366.8386 | 11627.9013 | 12386.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 16898.4575 | 18612.4108 | 19653.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 20290.3432 | 22180.6901 | 23333.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 25560.0611 | 27781.5378 | 29139.1942 | 6659322.9597 | 6598109.0913 | 6309276.5083 | 7467581.5258 | 7318955.0922 | 6939279.0957 | 8127742.3112 | 7955060.3041 | 7508853.8293 | 8529587.207 | 8343816.2595 | 7861380.4186 | 8932824.5617 | 8734772.7986 | 8218426.5393 | 9604040.2607 | 9386927.1116 | 8818212.4665
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 10224.0244 | 11112.6151 | 11655.6777 | 998898.444 | 989716.3637 | 946391.4763 | 1120137.2289 | 1097843.2638 | 1040891.8644 | 1219161.3467 | 1193259.0456 | 1126328.0744 | 1279438.0811 | 1251572.4389 | 1179207.0628 | 1339923.6842 | 1310215.9198 | 1232763.9809 | 1440606.0391 | 1408039.0667 | 1322731.87
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 312978.105 | 310101.1458 | 296526.4514 | 350965.0349 | 343979.8174 | 326135.6199 | 381991.5932 | 373875.8001 | 352904.7708 | 400877.6954 | 392146.7419 | 369472.9872 | 419829.241 | 410521.1078 | 386253.6147 | 451375.3635 | 441171.3739 | 414442.6459
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 416364.7579 | 412537.4473 | 394478.5982 | 466899.9826 | 457607.3249 | 433868.6197 | 508175.6029 | 497378.9044 | 469480.4751 | 533300.3871 | 521685.3211 | 491521.7019 | 558512.2329 | 546129.3263 | 513845.5061 | 600479.046 | 586904.3532 | 551346.2736
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 10143230.4626 | 2915.0868 | 3206.9634 | 502527.4584 | 484106.9277 | 439537.7847 | 631341.489 | 604728.8119 | 539465.4024 | 756385.7155 | 722502.1678 | 638715.5598 | 838137.6379 | 799737.4496 | 704419.5654 | 924461.6238 | 881436.8109 | 774308.618 | 1077667.6781 | 1026697.882 | 899290.4097
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 323.8985 | 356.3293 | 1127025.607 | 1085713.616 | 985757.7538 | 1415918.6987 | 1356234.0623 | 1209866.869 | 1696357.1958 | 1620366.0728 | 1432456.6339 | 1879703.4158 | 1793582.7576 | 1579811.9587 | 2073303.4689 | 1976811.098 | 1736553.1488 | 2416900.9052 | 2302590.2055 | 2016851.6227
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 169053.841 | 48.5848 | 53.4494 | 140963.2774 | 135796.1599 | 123294.1317 | 177096.7217 | 169631.6367 | 151324.6886 | 212172.7034 | 202668.0767 | 179165.212 | 235104.8213 | 224333.238 | 197595.7511 | 259319.4424 | 247250.612 | 217200.2319 | 302295.0593 | 287997.5927 | 252258.7002
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 108194.4583 | 31.0943 | 34.2076 | 1233017.6288 | 1187820.4187 | 1078464.1277 | 1549079.9016 | 1483782.1761 | 1323649.7633 | 1855892.4609 | 1772754.6921 | 1567173.1602 | 2056481.6223 | 1962261.6781 | 1728386.634 | 2268288.9468 | 2162721.8739 | 1899868.6743 | 2644200.2779 | 2519139.1373 | 2206528.0417
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 347531606.1947 | 347344409.1272 | 346714234.7888 | 349319528.5399 | 348973270.142 | 348104989.8796 | 350898386.8861 | 350478373.0202 | 349415585.672 | 351893138.8246 | 351429643.8414 | 350252304.0363 | 352916971.1584 | 352410367.5039 | 351119728.2705 | 354678072.5865 | 354099974.6796 | 352622169.987
| Survey, Design, Supervision etc. | [5 empty] | 5895966.1549 | 5894094.1843 | 5887792.4409 | 5913845.3784 | 5910382.7944 | 5901699.9918 | 5929633.9618 | 5925433.8232 | 5914805.9497 | 5939581.4812 | 5934946.5314 | 5923173.1334 | 5949819.8046 | 5944753.768 | 5931847.3757 | 5967430.8189 | 5961649.8398 | 5946871.7929
| TOTAL COST | [5 empty] | 353427572.3497 | 353238503.3114 | 352602027.2296 | 355233373.9183 | 354883652.9364 | 354006689.8714 | 356828020.848 | 356403806.8434 | 355330391.6217 | 357832720.3058 | 357364590.3728 | 356175477.1696 | 358866790.963 | 358355121.2719 | 357051575.6462 | 360645503.4053 | 360061624.5194 | 358569041.7798
| TOTAL COST IN RS. LAKHS | [5 empty] | 3534.2757 | 3532.385 | 3526.0203 | 3552.3337 | 3548.8365 | 3540.0669 | 3568.2802 | 3564.0381 | 3553.3039 | 3578.3272 | 3573.6459 | 3561.7548 | 3588.6679 | 3583.5512 | 3570.5158 | 3606.455 | 3600.6162 | 3585.6904
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 35.3428 | 35.3239 | 35.2602 | 35.5233 | 35.4884 | 35.4007 | 35.6828 | 35.6404 | 35.533 | 35.7833 | 35.7365 | 35.6175 | 35.8867 | 35.8355 | 35.7052 | 36.0646 | 36.0062 | 35.8569
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2486199.7936 | 2474256.115 | 2470438.7727 | 2486245.2432 | 2484126.5744 | 2478851.9018 | 2495890.6747 | 2493302.41 | 2486807.0979 | 2502004.8891 | 2499135.2439 | 2491908.9932 | 2508327.8512 | 2505176.3471 | 2497219.2552 | 2519272.4083 | 2515648.0987 | 2506468.8047
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2486199.7936 | 2474256.115 | 2470438.7727 | 2486245.2432 | 2484126.5744 | 2478851.9018 | 2495890.6747 | 2493302.41 | 2486807.0979 | 2502004.8891 | 2499135.2439 | 2491908.9932 | 2508327.8512 | 2505176.3471 | 2497219.2552 | 2519272.4083 | 2515648.0987 | 2506468.8047
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 39.6672 | 47.4027 | 52.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5.9501 | 7.1104 | 7.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4760.065 | 5688.3225 | 6294.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8004058.2809 | 6234738.0579 | 5934413.939 | 7127811.9379 | 6975502.7911 | 6586736.9443 | 7800585.6585 | 7624233.7352 | 7169720.8121 | 8209598.6457 | 8019954.3218 | 7529119.7562 | 8620124.1697 | 8417860.7571 | 7892646.3217 | 9304331.3352 | 9082196.2708 | 8503121.9901
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1200608.7421 | 935210.7087 | 890162.0909 | 1069171.7907 | 1046325.4187 | 988010.5417 | 1170087.8488 | 1143635.0603 | 1075458.1218 | 1231439.7968 | 1202993.1483 | 1129367.9634 | 1293018.6254 | 1262679.1136 | 1183896.9483 | 1395649.7003 | 1362329.4406 | 1275468.2985
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 376178.6308 | 293023.257 | 278908.4777 | 334996.3783 | 327838.0788 | 309566.6721 | 366615.7254 | 358327.4518 | 336966.032 | 385838.7171 | 376925.7207 | 353857.2387 | 405132.7956 | 395626.7212 | 370942.4373 | 437289.4974 | 426849.4854 | 399633.8702
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersmis Conductor (kM) | 240239.2008 | 1827 |  |  |  | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 609 |  |  |  | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 288 |  |  |  | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 500442.4336 | 389818.1869 | 371040.8457 | 445656.3693 | 436133.4551 | 411826.4199 | 487720.5954 | 476694.4406 | 448276.6624 | 513293.5545 | 501436.3111 | 470747.5735 | 538961.0828 | 526314.8487 | 493476.5583 | 581740.169 | 567851.488 | 531645.6868
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 14653339.8626 | 154.5809 | 171.1442 | 725972.4271 | 699162.7026 | 634713.4948 | 912147.5042 | 873348.3358 | 778770.952 | 1093131.1278 | 1043684.7572 | 922116.927 | 1211534.8617 | 1155473.9699 | 1017101.3487 | 1336605.0519 | 1273771.7456 | 1118188.3946 | 1558651.1448 | 1484184.2429 | 1299053.1201
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17.1757 | 19.016 | 1628148.8736 | 1568022.3163 | 1423481.1447 | 2045686.4147 | 1958670.9578 | 1746560.8898 | 2451581.0077 | 2340686.9164 | 2068044.9834 | 2717126.7762 | 2591398.2024 | 2281067.9214 | 2997623.5027 | 2856706.3369 | 2507777.3028 | 3495609.49 | 3328601.4911 | 2913405.2415
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 244222.331 | 2.5763 | 2.8524 | 203641.5143 | 196121.1558 | 178042.5983 | 255865.2258 | 244981.7251 | 218451.955 | 306632.69 | 292762.5574 | 258661.7347 | 339845.9565 | 324120.3938 | 285305.6826 | 374929.2213 | 357303.9381 | 313661.469 | 437215.0615 | 416326.4546 | 364395.5812
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 156302.2919 | 1.6489 | 1.8255 | 1781269.4326 | 1715488.2253 | 1557353.564 | 2238074.6247 | 2142875.7298 | 1910817.6013 | 2682141.8984 | 2560818.6838 | 2262535.9228 | 2972661.1303 | 2835108.3126 | 2495592.7729 | 3279537.3951 | 3125367.5621 | 2743623.2188 | 3824356.8717 | 3641642.4724 | 3187398.7604
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 497239958.7248 | 494851223.0001 | 494087754.5446 | 497249048.6353 | 496825314.8818 | 495770380.3656 | 499178134.9415 | 498660481.9923 | 497361419.5857 | 500400977.8284 | 499827048.7702 | 498381798.647 | 501665570.2342 | 501035269.4129 | 499443851.0404 | 503854481.6595 | 503129619.7354 | 501293760.9385
| Survey, Design, Supervision etc. | [5 empty] | 7393049.6802 | 7369162.323 | 7361527.6384 | 7393140.5793 | 7388903.2418 | 7378353.8966 | 7412431.4424 | 7407254.9129 | 7394264.2888 | 7424659.8713 | 7418920.5807 | 7404468.0795 | 7437305.7953 | 7431002.7871 | 7415088.6034 | 7459194.9096 | 7451946.2903 | 7433587.7024
| TOTAL COST | [5 empty] | 504633008.405 | 502220385.3231 | 501449282.183 | 504642189.2146 | 504214218.1236 | 503148734.2622 | 506590566.3839 | 506067736.9052 | 504755683.8745 | 507825637.6996 | 507245969.3509 | 505786266.7264 | 509102876.0295 | 508466272.2 | 506858939.6438 | 511313676.5691 | 510581566.0257 | 508727348.6409
| TOTAL COST IN RS. LAKHS | [5 empty] | 5046.3301 | 5022.2039 | 5014.4928 | 5046.4219 | 5042.1422 | 5031.4873 | 5065.9057 | 5060.6774 | 5047.5568 | 5078.2564 | 5072.4597 | 5057.8627 | 5091.0288 | 5084.6627 | 5068.5894 | 5113.1368 | 5105.8157 | 5087.2735
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 50.4633 | 50.222 | 50.1449 | 50.4642 | 50.4214 | 50.3149 | 50.6591 | 50.6068 | 50.4756 | 50.7826 | 50.7246 | 50.5786 | 50.9103 | 50.8466 | 50.6859 | 51.1314 | 51.0582 | 50.8727
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 3279035.1317 | 3277506.5272 | 3272657.6647 | 3292848.9057 | 3290111.251 | 3283336.7659 | 3305256.4098 | 3301901.3079 | 3293522.4199 | 3313135.5671 | 3309412.2493 | 3300077.1061 | 3321289.0069 | 3317197.9929 | 3306909.871 | 3335406.4718 | 3330700.7539 | 3318824.9666
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 3279035.1317 | 3277506.5272 | 3272657.6647 | 3292848.9057 | 3290111.251 | 3283336.7659 | 3305256.4098 | 3301901.3079 | 3293522.4199 | 3313135.5671 | 3309412.2493 | 3300077.1061 | 3321289.0069 | 3317197.9929 | 3306909.871 | 3335406.4718 | 3330700.7539 | 3318824.9666
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 4795.5834 | 6031.7 | 6844.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8543101.1457 | 8467404.143 | 8097622.1029 | 9580934.9506 | 9388165.7809 | 8900348.7823 | 10426848.0245 | 10202580.5495 | 9628258.4602 | 10942191.8119 | 10700798.4613 | 10079401.2181 | 11459515.8602 | 11202065.2527 | 10536641.663 | 12320881.171 | 12038530.5157 | 11305197.1335
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1281465.1719 | 1270110.6215 | 1214643.3154 | 1437140.2426 | 1408224.8671 | 1335052.3173 | 1564027.2037 | 1530387.0824 | 1444238.769 | 1641328.7718 | 1605119.7692 | 1511910.1827 | 1718927.379 | 1680309.7879 | 1580496.2495 | 1848132.1756 | 1805779.5774 | 1695779.57
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 401512.83 | 397955.1854 | 380575.9889 | 450289.4489 | 441229.5895 | 418302.9285 | 490046.0837 | 479505.8516 | 452513.5822 | 514266.4621 | 502921.3398 | 473716.6094 | 538579.9097 | 526480.1206 | 495206.2186 | 579062.7763 | 565792.7226 | 531327.163
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bsrsimis Conductor (kM) | 240239.2008 | 2436 |  |  |  | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 4608 |  |  |  | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078 | 4618377.0078
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 812 |  |  |  | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 384 |  |  |  | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 534145.327 | 529412.4789 | 506292.3794 | 599034.4192 | 586981.7992 | 556481.7307 | 651923.9388 | 637901.9318 | 601993.2547 | 684145.0808 | 669052.3027 | 630200.3182 | 716490.0359 | 700393.3005 | 658788.6309 | 770345.6848 | 752692.1091 | 706841.4756
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 19163449.2625 | 85.5822 | 93.9493 | 949417.3959 | 914218.4776 | 829889.2048 | 1192953.5194 | 1141967.8596 | 1018076.5015 | 1429876.5401 | 1364867.3465 | 1205518.2941 | 1584932.0856 | 1511210.4902 | 1329783.1321 | 1748748.4801 | 1666106.6804 | 1462068.1712 | 2039634.6114 | 1941670.6039 | 1698815.8306
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 9.5091 | 10.4388 | 2129272.1403 | 2050331.0166 | 1861204.5356 | 2675454.1308 | 2561107.8534 | 2283254.9106 | 3206804.8197 | 3061007.76 | 2703633.3329 | 3554550.1365 | 3389213.6472 | 2982323.8841 | 3921943.5364 | 3736601.5757 | 3279001.4568 | 4574318.0748 | 4354612.7768 | 3809958.8603
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 319390.821 | 1.4264 | 1.5658 | 266319.7512 | 256446.1517 | 232791.0649 | 334633.73 | 320331.8136 | 285579.2213 | 401092.6765 | 382857.0382 | 338158.2575 | 444587.0916 | 423907.5496 | 373015.6141 | 490539.0002 | 467357.2641 | 410122.7061 | 572135.0638 | 544655.3165 | 476532.4623
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 204410.1255 | 0.91288 | 1.0021 | 2329521.2365 | 2243156.0319 | 2036243.0002 | 2927069.3478 | 2801969.2835 | 2497985.4393 | 3508391.3358 | 3348882.6754 | 2957898.6854 | 3888840.6383 | 3707954.9471 | 3262798.9118 | 4290785.8434 | 4088013.2503 | 3587377.7633 | 5004513.4655 | 4764145.8075 | 4168269.4792
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 655807026.3416 | 655501305.4498 | 654531532.9353 | 658569781.1323 | 658022250.1901 | 656667353.1748 | 661051281.9659 | 660380261.5785 | 658704483.9792 | 662627113.4217 | 661882449.8502 | 660015421.2135 | 664257801.3882 | 663439598.5755 | 661381974.2026 | 667081294.3664 | 666140150.7725 | 663764993.3176
| Survey, Design, Supervision etc. | [5 empty] | 8978720.3564 | 8975663.1475 | 8965965.4223 | 9006347.9043 | 9000872.5949 | 8987323.6247 | 9031162.9126 | 9024452.7088 | 9007694.9328 | 9046921.2272 | 9039474.5915 | 9020804.3051 | 9063228.1069 | 9055046.0787 | 9034469.835 | 9091463.0367 | 9082051.6007 | 9058300.0262
| TOTAL COST | [5 empty] | 664785746.698 | 664476968.5973 | 663497498.3576 | 667576129.0366 | 667023122.785 | 665654676.7995 | 670082444.8786 | 669404714.2873 | 667712178.912 | 671674034.6489 | 670921924.4417 | 669036225.5186 | 673321029.4951 | 672494644.6543 | 670416444.0376 | 676172757.403 | 675222202.3732 | 672823293.3438
| TOTAL COST IN RS. LAKHS | [5 empty] | 6647.8575 | 6644.7697 | 6634.975 | 6675.7613 | 6670.2312 | 6656.5468 | 6700.8244 | 6694.0471 | 6677.1218 | 6716.7403 | 6709.2192 | 6690.3623 | 6733.2103 | 6724.9464 | 6704.1644 | 6761.7276 | 6752.222 | 6728.2329
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 66.4786 | 66.4477 | 66.3497 | 66.7576 | 66.7023 | 66.5655 | 67.0082 | 66.9405 | 66.7712 | 67.1674 | 67.0922 | 66.9036 | 67.3321 | 67.2495 | 67.0416 | 67.6173 | 67.5222 | 67.2823
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 966310.2275 | 965749.2578 | 964345.5972 | 970168.0679 | 969156.8829 | 967214.5862 | 973534.0525 | 972308.4896 | 969928.3486 | 975649.6795 | 974298.8959 | 971662.8506 | 977822.5144 | 976348.4615 | 973461.012 | 981548.4877 | 979871.8057 | 976572.8189
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 966310.2275 | 965749.2578 | 964345.5972 | 970168.0679 | 969156.8829 | 967214.5862 | 973534.0525 | 972308.4896 | 969928.3486 | 975649.6795 | 974298.8959 | 971662.8506 | 977822.5144 | 976348.4615 | 973461.012 | 981548.4877 | 979871.8057 | 976572.8189
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 12.9621 | 15.239 | 16.7289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 1.9443 | 2.2858 | 2.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 1555.4579 | 1828.6799 | 2007.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 3284960.7387 | 3239069.4172 | 3095630.46 | 3675264.3961 | 3577497.4891 | 3386322.1819 | 3993323.9735 | 3878993.5738 | 3652354.5296 | 4187540.3708 | 4064191.1802 | 3818167.0535 | 4382776.6055 | 4250976.547 | 3986807.2955 | 4708338.0976 | 4563459.2572 | 4271326.5244
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 492744.1108 | 485860.4126 | 464344.569 | 551289.6594 | 536624.6234 | 507948.3273 | 598998.596 | 581849.0361 | 547853.1794 | 628131.0556 | 609628.677 | 572725.058 | 657416.4908 | 637646.482 | 598021.0943 | 706250.7146 | 684518.8886 | 640698.9787
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 154388.1853 | 152231.3626 | 145489.9486 | 172731.8668 | 168136.97 | 159152.0198 | 187680.1857 | 182306.8299 | 171655.1377 | 196808.0626 | 191010.8373 | 179448.0755 | 205983.8703 | 199789.4669 | 187373.9117 | 221284.7679 | 214475.6816 | 200745.8851
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bsrsimis Conductor (kM) | 240239.2008 | 609 |  |  |  | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 1152 |  |  |  | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 96 |  |  |  | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 205387.5283 | 202518.2382 | 193549.9201 | 229790.7129 | 223677.9752 | 211725.0093 | 249676.9386 | 242528.5919 | 228358.3059 | 261820.0444 | 254107.8105 | 238725.4996 | 274026.914 | 265786.3016 | 249269.4925 | 294382.1863 | 285323.8415 | 267058.6552
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 3829030.9303 | 0 | 0 | 189702.2047 | 180601.6303 | 163859.1191 | 236544.8981 | 223310.9444 | 198604.0021 | 282153.14 | 265236.0615 | 233351.1837 | 312019.2712 | 292812.5684 | 256449.5948 | 343584.8052 | 322034.0915 | 281082.3071 | 399658.233 | 374083.1969 | 325253.2151
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 425447.8811 | 405037.8912 | 367489.219 | 530502.6678 | 500822.6883 | 445412.071 | 632788.9324 | 594848.7555 | 523340.0783 | 699770.1373 | 656694.9867 | 575143.2195 | 770562.6174 | 722230.5197 | 630387.36 | 896319.3057 | 838961.8021 | 729450.0949
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 63817.1822 | 0 | 0 | 53213.1012 | 50660.3117 | 45963.8933 | 66352.8799 | 62640.6419 | 55710.132 | 79146.3843 | 74400.9982 | 65457.0155 | 87524.0911 | 82136.4457 | 71936.3186 | 96378.4951 | 90333.3344 | 78846.0064 | 112107.5742 | 104933.5565 | 91236.3263
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 40842.9966 | 0 | 0 | 465459.4664 | 443130.0026 | 402050.0356 | 580394.2142 | 547922.9573 | 487301.2043 | 692300.0721 | 650791.781 | 572558.0133 | 765580.5778 | 718454.3903 | 629233.0221 | 843030.7931 | 790153.2648 | 689672.6419 | 980614.3695 | 917862.6337 | 798051.8107
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 193262045.5002 | 193149851.5502 | 192869119.4486 | 194033613.579 | 193831376.5734 | 193442917.2314 | 194706810.5065 | 194461697.9117 | 193985669.7272 | 195129935.8947 | 194859779.1798 | 194332570.1256 | 195564502.8752 | 195269692.2919 | 194692202.3934 | 196309697.5325 | 195974361.142 | 195314563.7741
| Survey, Design, Supervision etc. | [5 empty] | 4353270.548 | 4352148.6085 | 4349341.2875 | 4360986.2288 | 4358963.8587 | 4355079.2653 | 4367718.1981 | 4365267.0721 | 4360506.7903 | 4371949.4519 | 4369247.8848 | 4363975.7942 | 4376295.1217 | 4373347.0159 | 4367572.1169 | 4383747.0683 | 4380393.7044 | 4373795.7307
| TOTAL COST | [5 empty] | 197615316.0482 | 197502000.1587 | 197218460.7361 | 198394599.8078 | 198190340.4322 | 197797996.4967 | 199074528.7045 | 198826964.9838 | 198346176.5174 | 199501885.3466 | 199229027.0646 | 198696545.9198 | 199940797.997 | 199643039.3078 | 199059774.5103 | 200693444.6008 | 200354754.8464 | 199688359.5048
| TOTAL COST IN RS. LAKHS | [5 empty] | 1976.1532 | 1975.02 | 1972.1846 | 1983.946 | 1981.9034 | 1977.98 | 1990.7453 | 1988.2696 | 1983.4618 | 1995.0189 | 1992.2903 | 1986.9655 | 1999.408 | 1996.4304 | 1990.5977 | 2006.9344 | 2003.5475 | 1996.8836
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 19.7615 | 19.7502 | 19.7218 | 19.8395 | 19.819 | 19.7798 | 19.9075 | 19.8827 | 19.8346 | 19.9502 | 19.9229 | 19.8697 | 19.9941 | 19.9643 | 19.906 | 20.0693 | 20.0355 | 19.9688
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 25848918.3453 | 1338437.9944 | 1336666.6858 | 1344051.8006 | 1342746.9124 | 1340275.6486 | 1348349.942 | 1346759.8218 | 1343713.8455 | 1351062.7224 | 1349305.0728 | 1345921.2574 | 1353856.6084 | 1351933.4703 | 1348216.5689 | 1358663.513 | 1356467.2923 | 1352202.9711
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 25848918.3453 | 1338437.9944 | 1336666.6858 | 1344051.8006 | 1342746.9124 | 1340275.6486 | 1348349.942 | 1346759.8218 | 1343713.8455 | 1351062.7224 | 1349305.0728 | 1345921.2574 | 1353856.6084 | 1351933.4703 | 1348216.5689 | 1358663.513 | 1356467.2923 | 1352202.9711
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 26.1911 | 31.6347 | 35.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3.9287 | 4.7452 | 5.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 3142.9283 | 3796.1589 | 4225.0539 | 3895809972.3136 | 3842800.086 | 3673289.6566 | 4359709.4552 | 4242258.0967 | 4015396.5614 | 4736703.0264 | 4599136.5048 | 4329598.4627 | 4967148.6419 | 4818636.2898 | 4525778.1752 | 5198922.7469 | 5040161.1033 | 4725490.2715 | 5585579.1548 | 5410971.3232 | 5062725.6683
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 1257.1713 | 1518.4636 | 1690.0215 | 584371495.847 | 576420.0129 | 550993.4485 | 653956.4183 | 636338.7145 | 602309.4842 | 710505.454 | 689870.4757 | 649439.7694 | 745072.2963 | 722795.4435 | 678866.7263 | 779838.412 | 756024.1655 | 708823.5407 | 837836.8732 | 811645.6985 | 759408.8502
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 183097175.206 | 180605.7907 | 172639.057 | 204899.7491 | 199379.713 | 188717.564 | 222617.8767 | 216152.4583 | 203484.578 | 233448.472 | 226468.6161 | 212704.7277 | 244341.5043 | 236879.9472 | 222090.8941 | 262513.7705 | 254307.4666 | 237940.4476
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bsrsimis Conductor (kM) | 240239.2008 | 913.5 |  |  |  | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 1152 |  |  |  | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 144 |  |  |  | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 243580013.4282 | 240265.6452 | 229667.2451 | 272584.6731 | 265241.1928 | 251056.9959 | 296155.6634 | 287554.511 | 270702.0258 | 310563.9499 | 301278.4249 | 282967.8851 | 325055.2983 | 315128.9508 | 295454.6017 | 349230.4438 | 338313.3359 | 316539.7684
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 5385475.2928 | 21028.6958 | 23851.7409 | 266813.3413 | 253845.8335 | 230295.0538 | 332767.3468 | 313853.545 | 278966.3603 | 397148.4519 | 372929.0323 | 327803.9397 | 439362.0772 | 411843.3709 | 360327.6831 | 484009.7367 | 453113.2488 | 395048.3648 | 563379.0046 | 526683.8352 | 457376.2932
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 2336.5218 | 2650.1934 | 598386.1436 | 569303.7263 | 516486.0517 | 746302.1469 | 703883.8897 | 625641.8953 | 890690.5835 | 836373.3403 | 735170.6418 | 985363.692 | 923647.0909 | 808112.112 | 1085495.6446 | 1016203.6437 | 885980.6875 | 1263498.2509 | 1181201.4631 | 1025764.435
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 89757.9215 | 350.4783 | 397.529 | 74843.4387 | 71205.9412 | 64599.7448 | 93344.1049 | 88038.6207 | 78252.4651 | 111403.5591 | 104609.8034 | 91951.8265 | 123244.8443 | 115525.6103 | 101075.0165 | 135768.8971 | 127102.1663 | 110814.4665 | 158032.6598 | 147739.349 | 128297.9869
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 57445.0698 | 224.3061 | 254.4186 | 654661.8456 | 622844.3491 | 565059.3942 | 816488.7273 | 770081.2114 | 684480.8862 | 974456.2896 | 915030.738 | 804310.351 | 1078033.0061 | 1010512.218 | 884111.6599 | 1187581.948 | 1111773.3257 | 969303.4477 | 1382324.9513 | 1292288.4965 | 1122233.2692
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 5169783669.0644 | 267687598.8852 | 267333337.1519 | 268810360.1219 | 268549382.4842 | 268055129.7127 | 269669988.4048 | 269351964.364 | 268742769.0952 | 270212544.4798 | 269861014.5646 | 269184251.4861 | 270771321.688 | 270386694.0517 | 269643313.7749 | 271732702.6093 | 271293458.4682 | 270440594.2191
| Survey, Design, Supervision etc. | [5 empty] | 54118486.7836 | 5097526.0818 | 5093983.4645 | 5108753.6942 | 5106143.9178 | 5101201.3901 | 5117349.977 | 5114169.7366 | 5108077.7839 | 5122775.5378 | 5119260.2386 | 5112492.6078 | 5128363.3099 | 5124517.0335 | 5117083.2307 | 5137977.1191 | 5133584.6777 | 5125056.0352
| TOTAL COST | [5 empty] | 5223902155.848 | 272785124.9671 | 272427320.6164 | 273919113.8161 | 273655526.402 | 273156331.1028 | 274787338.3818 | 274466134.1006 | 273850846.8791 | 275335320.0176 | 274980274.8032 | 274296744.0939 | 275899684.9979 | 275511211.0852 | 274760397.0056 | 276870679.7283 | 276427043.1459 | 275565650.2542
| TOTAL COST IN RS. LAKHS | [5 empty] | 52239.0216 | 2727.8512 | 2724.2732 | 2739.1911 | 2736.5553 | 2731.5633 | 2747.8734 | 2744.6613 | 2738.5085 | 2753.3532 | 2749.8027 | 2742.9674 | 2758.9968 | 2755.1121 | 2747.604 | 2768.7068 | 2764.2704 | 2755.6565
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 522.3902 | 27.2785 | 27.2427 | 27.3919 | 27.3656 | 27.3156 | 27.4787 | 27.4466 | 27.3851 | 27.5335 | 27.498 | 27.4297 | 27.59 | 27.5511 | 27.476 | 27.6871 | 27.6427 | 27.5566
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1755076.7215 | 1754200.197 | 1752083.3164 | 1760939.7118 | 1759359.0435 | 1756389.6467 | 1766119.3678 | 1764185.9743 | 1760511.6052 | 1769398.0138 | 1767256.6024 | 1763166.0601 | 1772781.321 | 1770433.8967 | 1765931.9335 | 1778616.1617 | 1775927.8016 | 1770747.6333
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1755076.7215 | 1754200.197 | 1752083.3164 | 1760939.7118 | 1759359.0435 | 1756389.6467 | 1766119.3678 | 1764185.9743 | 1760511.6052 | 1769398.0138 | 1767256.6024 | 1763166.0601 | 1772781.321 | 1770433.8967 | 1765931.9335 | 1778616.1617 | 1775927.8016 | 1770747.6333
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 6.3189 | 7.4431 | 8.1777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5055.1374 | 5954.461 | 6542.1879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 4423087.5671 | 4363788.9858 | 4171712.5808 | 4950410.5574 | 4816120.7661 | 4558469.1697 | 5378296.6414 | 5220873.6849 | 4914382.1674 | 5640003.2716 | 5469996.4751 | 5136821.6372 | 5903292.6983 | 5721507.3444 | 5363383.6521 | 6342628.8988 | 6142642.8294 | 5746142.3674
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 663463.1351 | 654568.3479 | 625756.8871 | 742561.5836 | 722418.1149 | 683770.3754 | 806744.4962 | 783131.0527 | 737157.3251 | 846000.4907 | 820499.4713 | 770523.2456 | 885493.9047 | 858226.1017 | 804507.5478 | 951394.3348 | 921396.4244 | 861921.3551
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 207878.4245 | 205091.4809 | 196064.1804 | 232661.8073 | 226350.3903 | 214241.155 | 252771.806 | 245373.1652 | 230968.5275 | 265071.6217 | 257081.5594 | 241422.8461 | 277445.8265 | 268902.1898 | 252070.918 | 298093.9633 | 288694.9205 | 270059.9986
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bsrsimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 276547.3 | 272839.74 | 260830.4342 | 309517.4248 | 301121.1453 | 285011.8434 | 336270.3975 | 326427.7496 | 307264.8006 | 352633.2348 | 342003.8001 | 321172.5141 | 369095.0341 | 357729.1618 | 335337.984 | 396563.9093 | 384060.0629 | 359269.4318
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 6941919.6554 | 161099.2384 | 176969.7293 | 343924.4779 | 327090.0368 | 296730.9885 | 428989.7956 | 404396.1457 | 359328.7185 | 512143.7639 | 480622.003 | 422256.6957 | 566704.8831 | 530874.1733 | 464205.7713 | 624434.6683 | 584192.4061 | 509014.4224 | 727099.7763 | 679284.4735 | 589499.3712
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17899.9154 | 19663.3033 | 771324.4062 | 733569.5614 | 665482.8843 | 962101.6259 | 906945.0912 | 805871.7197 | 1148592.2346 | 1077897.9251 | 947001.2053 | 1270957.2467 | 1190599.1951 | 1041081.0046 | 1400428.6718 | 1310176.7677 | 1141574.0151 | 1630677.196 | 1523441.1241 | 1322078.7752
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 115698.6609 | 2684.9873 | 2949.4955 | 96473.7762 | 91751.5706 | 83235.5963 | 120335.33 | 113436.5995 | 100794.7983 | 143660.7338 | 134818.6086 | 118446.6375 | 158965.5974 | 148914.7749 | 130213.7143 | 175159.299 | 163870.9981 | 142782.9266 | 203957.7455 | 190545.1415 | 165359.6475
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 74047.143 | 1718.3919 | 1887.6771 | 843864.2249 | 802558.6957 | 728068.7528 | 1052583.2404 | 992239.4654 | 881660.5681 | 1256612.5071 | 1179269.6949 | 1036062.6887 | 1390485.4344 | 1302570.0457 | 1138990.2978 | 1532133.1028 | 1433393.3865 | 1248934.2535 | 1784035.5332 | 1666714.3593 | 1446414.7277
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 351015344.2972 | 350840039.4044 | 350416663.2899 | 352187942.3504 | 351871808.7039 | 351277929.3335 | 353223873.5659 | 352837194.8695 | 352102321.0331 | 353879602.7658 | 353451320.4803 | 352633212.0164 | 354556264.191 | 354086779.3416 | 353186386.7049 | 355723232.3426 | 355185560.3209 | 354149526.66
| Survey, Design, Supervision etc. | [5 empty] | 5930803.536 | 5929050.487 | 5924816.7259 | 5942529.5165 | 5939368.18 | 5933429.3863 | 5952888.8286 | 5949022.0417 | 5941673.3033 | 5959446.1206 | 5955163.2978 | 5946982.2132 | 5966212.7349 | 5961517.8864 | 5952513.96 | 5977882.4164 | 5972505.6962 | 5962145.3596
| TOTAL COST | [5 empty] | 356946147.8332 | 356769089.8914 | 356341480.0158 | 358130471.8669 | 357811176.884 | 357211358.7198 | 359176762.3946 | 358786216.9112 | 358043994.3365 | 359839048.8865 | 359406483.7781 | 358580194.2296 | 360522476.9259 | 360048297.228 | 359138900.6649 | 361701114.759 | 361158066.0171 | 360111672.0195
| TOTAL COST IN RS. LAKHS | [5 empty] | 3569.4615 | 3567.6909 | 3563.4148 | 3581.3047 | 3578.1118 | 3572.1136 | 3591.7676 | 3587.8622 | 3580.4399 | 3598.3905 | 3594.0648 | 3585.8019 | 3605.2248 | 3600.483 | 3591.389 | 3617.0111 | 3611.5807 | 3601.1167
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 35.6946 | 35.6769 | 35.6341 | 35.813 | 35.7811 | 35.7211 | 35.9177 | 35.8786 | 35.8044 | 35.9839 | 35.9406 | 35.858 | 36.0522 | 36.0048 | 35.9139 | 36.1701 | 36.1158 | 36.0112
ESTIMATE FOR A 765 KV, SC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1012489.7857 | 1011539.7595 | 1009166.961 | 1019322.7558 | 1017613.279 | 1014356.5665 | 1025261.4376 | 1023197.8212 | 1019228.5003 | 1028982.7006 | 1026712.907 | 1022328.645 | 1032797.2141 | 1030324.8282 | 1025533.6743 | 1039323.9702 | 1036519.1942 | 1031063.0766
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1012489.7857 | 1011539.7595 | 1009166.961 | 1019322.7558 | 1017613.279 | 1014356.5665 | 1025261.4376 | 1023197.8212 | 1019228.5003 | 1028982.7006 | 1026712.907 | 1022328.645 | 1032797.2141 | 1030324.8282 | 1025533.6743 | 1039323.9702 | 1036519.1942 | 1031063.0766
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 33.1275 | 39.4561 | 43.6035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 4.9691 | 5.9184 | 6.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3975.2993 | 4734.735 | 5232.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 5969732.8625 | 5887557.213 | 5636266.8142 | 6685615.8414 | 6513836.1661 | 6181104.1598 | 7269979.0049 | 7069546.8351 | 6676617.3372 | 7626261.5822 | 7410232.8633 | 6984431.5722 | 7984130.4966 | 7753482.5438 | 7296902.5122 | 8580455.5749 | 8327164.9246 | 7823094.8627
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 895459.9294 | 883133.582 | 845440.0221 | 1002842.3762 | 977075.4249 | 927165.624 | 1090496.8507 | 1060432.0253 | 1001492.6006 | 1143939.2373 | 1111534.9295 | 1047664.7358 | 1197619.5745 | 1163022.3816 | 1094535.3768 | 1287068.3362 | 1249074.7387 | 1173464.2294
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 280568.4137 | 276706.2825 | 264896.0139 | 314213.8307 | 306140.4458 | 290502.5449 | 341678.0154 | 332258.0066 | 313790.9146 | 358422.7575 | 348269.7345 | 328257.718 | 375242.0551 | 364401.9503 | 342943.3795 | 403268.4317 | 391364.1543 | 367673.6239
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bsrsimis Conductor (kM) | 240239.2008 | 609 |  |  |  | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 1920 |  |  |  | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 373249.1115 | 368111.1952 | 352399.6181 | 418008.6832 | 407268.4017 | 386464.8032 | 454545.1642 | 442013.426 | 417446.0644 | 476821.2289 | 463314.3385 | 436691.7145 | 499196.4771 | 484775.5398 | 456228.5185 | 536480.86 | 520644.22 | 489127.9516
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 7907691.8314 | 0 | 0 | 326476.5511 | 311253.2241 | 283437.9978 | 408296.4629 | 386204.0843 | 345329.7852 | 487792.3842 | 459586.3585 | 406973.527 | 539797.3642 | 507791.5849 | 447860.307 | 594732.8708 | 558836.8896 | 491406.5314 | 692275.8747 | 649699.6468 | 569391.0055
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 878632.4257 | 837662.5348 | 762804.6018 | 1098830.8667 | 1039374.59 | 929371.3311 | 1312774.8512 | 1236865.1766 | 1095270.5059 | 1452733.6374 | 1366597.8478 | 1205307.3541 | 1600579.2245 | 1503973.9006 | 1322501.4516 | 1863092.5532 | 1748508.9658 | 1532377.7428
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 131794.8639 | 0 | 0 | 73263.5861 | 69847.3667 | 63605.4384 | 91624.5376 | 86666.8558 | 77494.3816 | 109463.9698 | 103134.3434 | 91327.6617 | 121134.2454 | 113951.9281 | 100502.9367 | 133462.1513 | 125406.846 | 110275.0093 | 155351.4731 | 145797.0743 | 127775.2623
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 84348.7129 | 0 | 0 | 576758.4677 | 549864.7055 | 500725.9013 | 721302.7751 | 682274.0412 | 610064.8794 | 861741.4853 | 811912.289 | 718965.6564 | 953614.2784 | 897072.3792 | 791196.8672 | 1050664.1844 | 987249.7951 | 868126.2931 | 1222985.1467 | 1147769.3314 | 1005894.8577
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 202497957.1341 | 202307951.8902 | 201833392.1942 | 203864551.1603 | 203522655.7965 | 202871313.2956 | 205052287.5123 | 204639564.2471 | 203845700.0543 | 205796540.1179 | 205342581.3925 | 204465728.9921 | 206559442.8209 | 206064965.6332 | 205106734.8589 | 207864794.0371 | 207303838.8426 | 206212615.3224
| Survey, Design, Supervision etc. | [5 empty] | 4445629.6643 | 4443729.6119 | 4438984.0149 | 4459295.6046 | 4455876.651 | 4449363.2259 | 4471172.9681 | 4467045.7355 | 4459107.0935 | 4478615.4942 | 4474075.9069 | 4465307.3829 | 4486244.5212 | 4481299.7493 | 4471717.4416 | 4499298.0334 | 4493688.4814 | 4482776.2462
| TOTAL COST | [5 empty] | 206943586.7984 | 206751681.5021 | 206272376.2091 | 208323846.7649 | 207978532.4474 | 207320676.5216 | 209523460.4804 | 209106609.9825 | 208304807.1478 | 210275155.6121 | 209816657.2994 | 208931036.375 | 211045687.3421 | 210546265.3826 | 209578452.3005 | 212364092.0704 | 211797527.324 | 210695391.5686
| TOTAL COST IN RS. LAKHS | [5 empty] | 2069.4359 | 2067.5168 | 2062.7238 | 2083.2385 | 2079.7853 | 2073.2068 | 2095.2346 | 2091.0661 | 2083.0481 | 2102.7516 | 2098.1666 | 2089.3104 | 2110.4569 | 2105.4627 | 2095.7845 | 2123.6409 | 2117.9753 | 2106.9539
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 20.6944 | 20.6752 | 20.6272 | 20.8324 | 20.7979 | 20.7321 | 20.9523 | 20.9107 | 20.8305 | 21.0275 | 20.9817 | 20.8931 | 21.1046 | 21.0546 | 20.9578 | 21.2364 | 21.1798 | 21.0695
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1389785.5868 | 1388560.5855 | 1385580.3644 | 1398407.502 | 1396197.6356 | 1392073.1238 | 1405950.0925 | 1403268.4543 | 1398212.3518 | 1410695.6447 | 1407737.838 | 1402136.2508 | 1415573.2836 | 1412343.1726 | 1406204.8316 | 1423946.0683 | 1420267.4464 | 1413248.5306
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1389785.5868 | 1388560.5855 | 1385580.3644 | 1398407.502 | 1396197.6356 | 1392073.1238 | 1405950.0925 | 1403268.4543 | 1398212.3518 | 1410695.6447 | 1407737.838 | 1402136.2508 | 1415573.2836 | 1412343.1726 | 1406204.8316 | 1423946.0683 | 1420267.4464 | 1413248.5306
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 7079406.516 | 6983337.2339 | 6686510.5709 | 7929272.5663 | 7721622.0606 | 7326915.7396 | 8621245.0377 | 8378603.2414 | 7911450.7189 | 9043561.9082 | 8781884.791 | 8275191.8837 | 9467959.7046 | 9188451.6777 | 8644766.4055 | 10175411.8588 | 9868311.4143 | 9267623.3067
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1061910.9774 | 1047500.5851 | 1002976.5856 | 1189390.8849 | 1158243.3091 | 1099037.3609 | 1293186.7556 | 1256790.4862 | 1186717.6078 | 1356534.2862 | 1317282.7187 | 1241278.7826 | 1420193.9557 | 1378267.7517 | 1296714.9608 | 1526311.7788 | 1480246.7122 | 1390143.496
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 332721.3967 | 328206.2858 | 314255.8816 | 372663.8154 | 362904.5558 | 344353.9558 | 405185.4747 | 393781.6774 | 371826.2155 | 425033.7288 | 412735.3001 | 388921.5 | 444979.7832 | 431843.3288 | 406290.9435 | 478228.9642 | 463795.7079 | 435564.2756
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bsrsimis Conductor (kM) | 240239.2008 | 913.5 |  |  |  | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 1920 |  |  |  | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 442629.8886 | 436623.2925 | 418064.6249 | 495766.5625 | 482783.5081 | 458105.0531 | 539031.1635 | 523860.328 | 494652.2767 | 565435.929 | 549074.9371 | 517394.679 | 591970.8015 | 574494.9571 | 540501.8038 | 636203.2478 | 617002.2265 | 579445.0514
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 11120738.8878 | 0 | 0 | 459130.2436 | 437308.2116 | 398206.9181 | 574217.5016 | 542463.8932 | 484782.6359 | 686313.9757 | 645711.4427 | 571299.1282 | 759733.9861 | 713630.4398 | 628783.0607 | 837341.817 | 785606.2975 | 690066.3663 | 975227.5602 | 913821.8158 | 799923.298
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1235637.6542 | 1176908.9494 | 1071677.3051 | 1545367.0859 | 1459909.9532 | 1304674.8439 | 1847047.5484 | 1737775.6823 | 1537512.9918 | 2044639.693 | 1920563.1839 | 1692217.0493 | 2253502.3402 | 2114268.7419 | 1857146.1973 | 2624588.3635 | 2459329.7011 | 2152799.4749
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 185345.6481 | 0 | 0 | 103031.9881 | 98134.9738 | 89360.3743 | 128858.3612 | 121732.6329 | 108788.5615 | 154013.5819 | 144902.0939 | 128203.4581 | 170489.5377 | 160143.5845 | 141103.2484 | 187905.2694 | 176295.4626 | 154855.6441 | 218847.7796 | 205067.9077 | 179508.296
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 118621.2148 | 0 | 0 | 811106.5096 | 772555.374 | 703478.4311 | 1014421.4194 | 958325.0093 | 856424.4179 | 1212452.7647 | 1140723.7091 | 1009265.7762 | 1342157.6779 | 1260710.4479 | 1110817.7706 | 1479260.8588 | 1387864.0989 | 1219081.7953 | 1722851.9213 | 1614371.5942 | 1413156.7308
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 277957117.3686 | 277712117.1003 | 277116072.8861 | 279681500.3916 | 279239527.1165 | 278414624.7631 | 281190018.4965 | 280653690.8554 | 279642470.3677 | 282139128.9414 | 281547567.5973 | 280427250.1686 | 283114656.7247 | 282468634.5104 | 281240966.311 | 284789213.6687 | 284053489.2741 | 282649706.1236
| Survey, Design, Supervision etc. | [5 empty] | 5200221.2667 | 5197771.264 | 5191810.8218 | 5217465.0969 | 5213045.3642 | 5204796.3406 | 5232550.278 | 5227187.0015 | 5217074.7967 | 5242041.3824 | 5236125.769 | 5224922.5947 | 5251796.6602 | 5245336.4381 | 5233059.7561 | 5268542.2297 | 5261184.9857 | 5247147.1542
| TOTAL COST | [5 empty] | 283157338.6353 | 282909888.3643 | 282307883.7079 | 284898965.4885 | 284452572.4806 | 283619421.1037 | 286422568.7744 | 285880877.8569 | 284859545.1644 | 287381170.3238 | 286783693.3662 | 285652172.7633 | 288366453.3849 | 287713970.9485 | 286474026.067 | 290057755.8983 | 289314674.2598 | 287896853.2778
| TOTAL COST IN RS. LAKHS | [5 empty] | 2831.5734 | 2829.0989 | 2823.0788 | 2848.9897 | 2844.5257 | 2836.1942 | 2864.2257 | 2858.8088 | 2848.5955 | 2873.8117 | 2867.8369 | 2856.5217 | 2883.6645 | 2877.1397 | 2864.7403 | 2900.5776 | 2893.1467 | 2878.9685
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 28.3157 | 28.291 | 28.2308 | 28.4899 | 28.4453 | 28.3619 | 28.6423 | 28.5881 | 28.486 | 28.7381 | 28.6784 | 28.5652 | 28.8366 | 28.7714 | 28.6474 | 29.0058 | 28.9315 | 28.7897
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1906398.0938 | 1904909.1999 | 1901360.0254 | 1916692.9636 | 1914016.1223 | 1909077.2722 | 1925747.4228 | 1922487.2791 | 1916409.0789 | 1931460.5089 | 1927857.5104 | 1921109.3794 | 1937343.9641 | 1933402.0304 | 1925992.9474 | 1947466.879 | 1942965.0499 | 1934468.4092
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1906398.0938 | 1904909.1999 | 1901360.0254 | 1916692.9636 | 1914016.1223 | 1909077.2722 | 1925747.4228 | 1922487.2791 | 1916409.0789 | 1931460.5089 | 1927857.5104 | 1921109.3794 | 1937343.9641 | 1933402.0304 | 1925992.9474 | 1947466.879 | 1942965.0499 | 1934468.4092
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8037305.6921 | 7929102.5915 | 7592848.1894 | 9002736.6774 | 8764521.2587 | 8316329.7119 | 9787703.3704 | 9509126.779 | 8978022.3819 | 10267042.3324 | 9966516.4364 | 9390171.2997 | 10748868.8776 | 10427789.6464 | 9809137.8897 | 11552220.3544 | 11199351.082 | 10515553.7314
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1205595.8538 | 1189365.3887 | 1138927.2284 | 1350410.5016 | 1314678.1888 | 1247449.4568 | 1468155.5056 | 1426369.0169 | 1346703.3573 | 1540056.3499 | 1494977.4655 | 1408525.695 | 1612330.3316 | 1564168.447 | 1471370.6835 | 1732833.0532 | 1679902.6623 | 1577333.0597
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 377741.2089 | 372655.8268 | 356852.3786 | 423115.0047 | 411919.2404 | 390854.9157 | 460007.2518 | 446914.5734 | 421953.4702 | 482535.4579 | 468411.1954 | 441323.8458 | 505180.5766 | 490090.3385 | 461014.6418 | 542936.8807 | 526352.5587 | 494215.1177
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bsrsimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 3840 |  |  |  | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296 | 4614275.4296
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 163660.9478 | 100 |  |  |  | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 502521.181 | 495755.9351 | 474732.1037 | 562883.3892 | 547989.3067 | 519966.7636 | 611962.3224 | 594544.7147 | 561338.1628 | 641932.3137 | 623142.3567 | 587107.1915 | 672057.8376 | 651982.8123 | 613302.4855 | 722286.2535 | 700223.6008 | 657470.1377
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 14333785.9442 | 0 | 0 | 591783.9362 | 563363.199 | 512975.8385 | 740138.5403 | 698723.7022 | 624235.4866 | 884835.5671 | 831836.527 | 735624.7293 | 979670.608 | 919469.2946 | 809705.8144 | 1079950.7632 | 1012375.7054 | 888726.2012 | 1258179.2457 | 1177943.9849 | 1030455.5904
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1592642.8827 | 1516155.364 | 1380550.0084 | 1991903.305 | 1880445.3165 | 1679978.3568 | 2381320.2455 | 2238686.1879 | 1979755.4778 | 2636545.7485 | 2474528.5199 | 2179126.7444 | 2906425.4559 | 2724563.5832 | 2391790.943 | 3386084.1739 | 3170150.4363 | 2773221.2069
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 238896.4324 | 0 | 0 | 132800.3901 | 126422.581 | 115115.3103 | 166092.1848 | 156798.4099 | 140082.7414 | 198563.1939 | 186669.8444 | 165079.2545 | 219844.8301 | 206335.2408 | 181703.5601 | 242348.3874 | 227184.0792 | 199436.279 | 282344.0861 | 264338.7411 | 231241.3298
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 152893.7167 | 0 | 0 | 1045454.5515 | 995246.0424 | 906230.9608 | 1307540.0637 | 1234375.9774 | 1102783.9565 | 1563164.0441 | 1469535.1292 | 1299565.8961 | 1730701.0774 | 1624348.5166 | 1430438.674 | 1907857.5332 | 1788478.4027 | 1570037.2976 | 2222718.6959 | 2080973.8571 | 1820418.6039
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 381279618.7524 | 380981839.9846 | 380272005.0743 | 383338592.7228 | 382803224.4566 | 381815454.4453 | 385149484.5569 | 384497455.8285 | 383281815.7859 | 386292101.7739 | 385571502.082 | 384221875.8809 | 387468792.8191 | 386680406.0706 | 385198589.4772 | 389493375.7995 | 388593009.9793 | 386893681.8337
| Survey, Design, Supervision etc. | [5 empty] | 6233446.2805 | 6230468.4928 | 6223370.1437 | 6254036.0202 | 6248682.3376 | 6238804.6374 | 6272144.9386 | 6265624.6513 | 6253468.2508 | 6283571.1107 | 6276365.1138 | 6262868.8518 | 6295338.0212 | 6287454.1537 | 6272635.9878 | 6315583.851 | 6306580.1928 | 6289586.9113
| TOTAL COST | [5 empty] | 387513065.0329 | 387212308.4774 | 386495375.2181 | 389592628.743 | 389051906.7942 | 388054259.0828 | 391421629.4954 | 390763080.4798 | 389535284.0367 | 392575672.8846 | 391847867.1958 | 390484744.7327 | 393764130.8403 | 392967860.2243 | 391471225.465 | 395808959.6505 | 394899590.1721 | 393183268.745
| TOTAL COST IN RS. LAKHS | [5 empty] | 3875.1307 | 3872.1231 | 3864.9538 | 3895.9263 | 3890.5191 | 3880.5426 | 3914.2163 | 3907.6308 | 3895.3528 | 3925.7567 | 3918.4787 | 3904.8474 | 3937.6413 | 3929.6786 | 3914.7123 | 3958.0896 | 3948.9959 | 3931.8327
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 38.7513 | 38.7212 | 38.6495 | 38.9593 | 38.9052 | 38.8054 | 39.1422 | 39.0763 | 38.9535 | 39.2576 | 39.1848 | 39.0485 | 39.3764 | 39.2968 | 39.1471 | 39.5809 | 39.49 | 39.3183
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 13309062.3407 | 13941842.3508 | 14341910.5814
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 12243.3706 | 13283.528 | 13922.4666 | 734602.2359 | 797011.6778 | 835347.9947
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 282821.8608 | 306849.4959 | 321608.978
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) x No. of Ckts. | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 2436 |  |  |  | 876960000 | 876960000 | 876960000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 21000 | 1680 |  |  |  | 35280000 | 35280000 | 35280000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 40 |  |  |  | 1240000 | 1240000 | 1240000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 840 |  |  |  | 49560000 | 49560000 | 49560000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 40 |  |  |  | 1800000 | 1800000 | 1800000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 812 |  |  |  | 1055600 | 1055600 | 1055600
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 5040 | 10080 |  |  |  | 50803200 | 50803200 | 50803200
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 1680 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 0 |  |  |  | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 380000 | 100 |  |  |  | 38000000 | 38000000 | 38000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 484837.4757 | 526027.7073 | 551329.6765
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 110476.1386 | 135501.5486 | 151914.4961 | 33142841.5799 | 40650464.5715 | 45574348.8348
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 12275.1265 | 15055.7276 | 16879.3885 | 69968221.113 | 85817647.4288 | 96212514.2067
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 1841.269 | 2258.3591 | 2531.9083 | 8653964.1903 | 10614287.9715 | 11899968.8624
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 1178.4121 | 1445.3499 | 1620.4213 | 63634255.8333 | 78048891.9773 | 87502749.7628
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 1565772040.0812 | 1640216747.1546 | 1687283597.8152
| Survey, Design, Supervision etc. | [5 empty] | 34966782.7415 | 36344009.8224 | 37214746.5596
| TOTAL COST | [5 empty] | 1600738822.8227 | 1676560756.9769 | 1724498344.3747
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 288132988.1081 | 301780936.2558 | 310409701.9875
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
v) | Contengency at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1984916140.3001 | 2078935338.6514 | 2138377947.0247
| TOTAL COST IN RS. LAKHS | [5 empty] | 19849.1614 | 20789.3534 | 21383.7795
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 198.4916 | 207.8935 | 213.8378
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 8411202.1434 | 8912246.9919 | 9223024.2025
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
III | Detailed survey (Rs. Per kM) | 50000 | 100 |  |  |  | 5000000 | 5000000 | 5000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 520753.4201 | 578395.2043 | 613278.8096 | 31245205.2042 | 34703712.2574 | 36796728.5749
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 12029404.0036 | 13360929.2191 | 14166740.5013
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 1218 |  |  |  | 438480000 | 438480000 | 438480000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of suspn.x1) | 24000 | 210 |  |  |  | 5040000 | 5040000 | 5040000
| b) Double 'I' Suspension Insulator Sring (No. Suspn. X 2) | 21000 | 420 |  |  |  | 8820000 | 8820000 | 8820000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'V' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
| f) Single 'I' Suspension Pilot strings (No. of Suspn x 1) | 15000 | 210 |  |  |  | 3150000 | 3150000 | 3150000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 406 |  |  |  | 527800 | 527800 | 527800
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 2700 | 5040 |  |  |  | 13608000 | 13608000 | 13608000
| f) Quad Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 1000 | 840 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190000 | 100 |  |  |  | 19000000 | 19000000 | 19000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 20621835.4348 | 22904450.0899 | 24285840.8595
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 48382.6073 | 59272.006 | 66421.8968 | 14514782.1992 | 17781601.804 | 19926569.0329
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 5375.8453 | 6585.7784 | 7380.2108 | 30642317.976 | 37538937.1417 | 42067201.2916
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 806.3768 | 987.8668 | 1107.0316 | 3789970.9076 | 4642973.8044 | 5203048.5808
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 516.0811 | 632.2347 | 708.5002 | 27868381.8224 | 34140675.4636 | 38259012.5431
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 989553193.3401 | 1048499646.1046 | 1085061670.8834
| Survey, Design, Supervision etc. | [5 empty] | 23306734.0768 | 24397243.4529 | 25073640.9113
| TOTAL COST | [5 empty] | 1012859927.4169 | 1072896889.5575 | 1110135311.7948
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 182314786.935 | 193121440.1204 | 199824356.1231
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
v) | Contengency at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1255946309.997 | 1330392143.0513 | 1376567786.6255
| TOTAL COST IN RS. LAKHS | [5 empty] | 12559.4631 | 13303.9214 | 13765.6779
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 125.5946 | 133.0392 | 137.6568
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 5050227.0344 | 5357651.6793 | 5546861.9223
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 10366.8386 | 11627.9013 | 12386.9423 | 130622166.4713 | 146511556.3957 | 156075473.2845
| b) 'B' Type towers | 60000 | 25 | 16898.4575 | 18612.4108 | 19653.708 | 25347686.3224 | 27918616.1635 | 29480562.0497
| c) 'C' Type towers | 60000 | 25 | 20290.3432 | 22180.6901 | 23333.1622 | 30435514.7251 | 33271035.0929 | 34999743.239
| d) 'D' Type towers | 60000 | 20 | 25560.0611 | 27781.5378 | 29139.1942 | 30672073.3304 | 33337845.351 | 34967032.9907
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 361795.7347 | 401731.755 | 425871.3526 | 21707744.0849 | 24103905.3003 | 25552281.1564
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 7163555.548 | 7954288.7491 | 8432252.7816
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 609 |  |  |  | 219240000 | 219240000 | 219240000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) | 21000 | 840 |  |  |  | 17640000 | 17640000 | 17640000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 203 |  |  |  | 263900 | 263900 | 263900
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 900 | 5040 |  |  |  | 4536000 | 4536000 | 4536000
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 840 |  |  |  | 420000 | 420000 | 420000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 3360 |  |  |  | 3024000 | 3024000 | 3024000
V | ERECTION
2 | Stringing of Conductor (Route kM) | 95000 | 100 |  |  |  | 9500000 | 9500000 | 9500000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 12280380.9395 | 13635923.5699 | 14455290.4828
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 21646.7931 | 26473.7232 | 29642.2493 | 6494037.9255 | 7942116.9663 | 8892674.7876
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 2405.1992 | 2941.5248 | 3293.5833 | 13709635.6204 | 16766691.3734 | 18773424.5515
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 360.7799 | 441.2287 | 494.0375 | 1695665.4583 | 2073774.9857 | 2321976.1945
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 230.8991 | 282.3864 | 316.184 | 12468552.8169 | 15248864.5753 | 17073935.5921
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 594144356.9927 | 630311962.2731 | 652571990.8604
| Survey, Design, Supervision etc. | [5 empty] | 16991670.6044 | 17660771.3021 | 18072581.8309
| TOTAL COST | [5 empty] | 611136027.5971 | 647972733.5751 | 670644572.6913
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 110004484.9675 | 116635092.0435 | 120716023.0844
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
v) | Contengency at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 757808674.2204 | 803486189.6332 | 831599270.1372
| TOTAL COST IN RS. LAKHS | [5 empty] | 7578.0867 | 8034.8619 | 8315.9927
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 75.7809 | 80.3486 | 83.1599

## Bersi-Std-Plain
CERC
Capital Cost Benchmarking
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1730916.4179 | 1729590.1263 | 1726317.6844 | 1739834.6342 | 1738037.9439 | 1733534.2597 | 1748016.418 | 1745838.2026 | 1740328.7242 | 1753168.6856 | 1750765.8635 | 1744664.5593 | 1758469.2116 | 1755844.0344 | 1749158.0448 | 1767580.3893 | 1764587.2689 | 1756937.2611
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1730916.4179 | 1729590.1263 | 1726317.6844 | 1739834.6342 | 1738037.9439 | 1733534.2597 | 1748016.418 | 1745838.2026 | 1740328.7242 | 1753168.6856 | 1750765.8635 | 1744664.5593 | 1758469.2116 | 1755844.0344 | 1749158.0448 | 1767580.3893 | 1764587.2689 | 1756937.2611
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 10736.956 | 12057.6633 | 12852.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 17132.487 | 18950.123 | 20054.3624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 20389.7437 | 22403.5518 | 23631.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 25511.93 | 27885.7649 | 29338.4186 | 6659322.9597 | 6536132.2035 | 6227995.4502 | 7464184.13 | 7305173.0713 | 6899728.1175 | 8169995.8962 | 7984905.0528 | 7507648.4307 | 8600186.1385 | 8400862.8735 | 7884349.8016 | 9032222.4043 | 8819536.6843 | 8266225.064 | 9751975.6427 | 9518565.7067 | 8908409.2488
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 10204.772 | 11154.306 | 11735.3675 | 998898.444 | 980419.8305 | 934199.3175 | 1119627.6195 | 1095775.9607 | 1034959.2176 | 1225499.3844 | 1197735.7579 | 1126147.2646 | 1290027.9208 | 1260129.431 | 1182652.4702 | 1354833.3606 | 1322930.5026 | 1239933.7596 | 1462796.3464 | 1427784.856 | 1336261.3873
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 312978.105 | 307188.3259 | 292706.3646 | 350805.3625 | 343332.0833 | 324276.7838 | 383977.4477 | 375278.4581 | 352848.1188 | 404195.7383 | 394827.8464 | 370552.5134 | 424500.7893 | 414504.8822 | 388500.0731 | 458328.1026 | 447358.1887 | 418681.7583
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 416364.7579 | 408662.4299 | 389396.6149 | 466687.5652 | 456745.6235 | 431395.7507 | 510817.4486 | 499244.9051 | 469405.1092 | 537714.4856 | 525252.0801 | 492957.8301 | 564726.9426 | 551429.0685 | 516834.0413 | 609728.4967 | 595134.8703 | 556985.7
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 10143230.4626 | 2937.0007 | 3250.9652 | 502527.4584 | 484106.9277 | 439537.7847 | 631341.489 | 604728.8119 | 539465.4024 | 756385.7155 | 722502.1678 | 638715.5598 | 838137.6379 | 799737.4496 | 704419.5654 | 924461.6238 | 881436.8109 | 774308.618 | 1077667.6781 | 1026697.882 | 899290.4097
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 326.3334 | 361.2184 | 1127025.607 | 1085713.616 | 985757.7538 | 1415918.6987 | 1356234.0623 | 1209866.869 | 1696357.1958 | 1620366.0728 | 1432456.6339 | 1879703.4158 | 1793582.7576 | 1579811.9587 | 2073303.4689 | 1976811.098 | 1736553.1488 | 2416900.9052 | 2302590.2055 | 2016851.6227
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 169053.841 | 48.95 | 54.1828 | 140963.2774 | 135796.1599 | 123294.1317 | 177096.7217 | 169631.6367 | 151324.6886 | 212172.7034 | 202668.0767 | 179165.212 | 235104.8213 | 224333.238 | 197595.7511 | 259319.4424 | 247250.612 | 217200.2319 | 302295.0593 | 287997.5927 | 252258.7002
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 108194.4583 | 31.328 | 34.677 | 1233017.6288 | 1187820.4187 | 1078464.1277 | 1549079.9016 | 1483782.1761 | 1323649.7633 | 1855892.4609 | 1772754.6921 | 1567173.1602 | 2056481.6223 | 1962261.6781 | 1728386.634 | 2268288.9468 | 2162721.8739 | 1899868.6743 | 2644200.2779 | 2519139.1373 | 2206528.0417
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 346183283.5827 | 345918025.2567 | 345263536.8898 | 347966926.8329 | 347607588.7703 | 346706851.9374 | 349603283.5972 | 349167640.5279 | 348065744.8338 | 350633737.1252 | 350153172.6989 | 348932911.8692 | 351693842.3233 | 351168806.877 | 349831608.9555 | 353516077.8536 | 352917453.7839 | 351387452.2133
| Survey, Design, Supervision etc. | [5 empty] | 5882482.9288 | 5879830.3456 | 5873285.4619 | 5900319.3613 | 5896725.9807 | 5887718.6124 | 5916682.929 | 5912326.4983 | 5901307.5413 | 5926987.4642 | 5922181.82 | 5909979.2117 | 5937588.5162 | 5932338.1618 | 5918966.1825 | 5955810.8715 | 5949824.6308 | 5934524.6151
| TOTAL COST | [5 empty] | 352065766.5115 | 351797855.6023 | 351136822.3517 | 353867246.1942 | 353504314.751 | 352594570.5498 | 355519966.5261 | 355079967.0261 | 353967052.3751 | 356560724.5895 | 356075354.5189 | 354842891.0809 | 357631430.8395 | 357101145.0387 | 355750575.1381 | 359471888.7251 | 358867278.4147 | 357321976.8284
| TOTAL COST IN RS. LAKHS | [5 empty] | 3520.6577 | 3517.9786 | 3511.3682 | 3538.6725 | 3535.0431 | 3525.9457 | 3555.1997 | 3550.7997 | 3539.6705 | 3565.6072 | 3560.7535 | 3548.4289 | 3576.3143 | 3571.0115 | 3557.5058 | 3594.7189 | 3588.6728 | 3573.2198
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 35.2066 | 35.1798 | 35.1137 | 35.3867 | 35.3504 | 35.2595 | 35.552 | 35.508 | 35.3967 | 35.6561 | 35.6075 | 35.4843 | 35.7631 | 35.7101 | 35.5751 | 35.9472 | 35.8867 | 35.7322
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2479458.1806 | 2477717.4962 | 2473456.4204 | 2491116.756 | 2488742.5413 | 2482836.8384 | 2501877.2018 | 2498984.4204 | 2491722.6147 | 2508679.3536 | 2505479.6054 | 2497415.329 | 2515695.5527 | 2512190.8503 | 2503330.9174 | 2527794.2324 | 2523782.9 | 2513605.7095
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2479458.1806 | 2477717.4962 | 2473456.4204 | 2491116.756 | 2488742.5413 | 2482836.8384 | 2501877.2018 | 2498984.4204 | 2491722.6147 | 2508679.3536 | 2505479.6054 | 2497415.329 | 2515695.5527 | 2512190.8503 | 2503330.9174 | 2527794.2324 | 2523782.9 | 2513605.7095
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 40.0568 | 48.36 | 53.8088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 6.0085 | 7.254 | 8.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4806.8175 | 5803.2042 | 6457.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8004058.2809 | 7854875.4913 | 7484090.7527 | 8971864.7131 | 8778977.332 | 8290009.9376 | 9821691.9756 | 9596985.7401 | 9020760.9936 | 10339942.8136 | 10097881.3234 | 9473976.3061 | 10860547.7226 | 10602199.8115 | 9933622.9023 | 11728018.4514 | 11444427.8991 | 10706897.2347
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1200608.7421 | 1178231.3237 | 1122613.6129 | 1345779.707 | 1316846.5998 | 1243501.4906 | 1473253.7963 | 1439547.861 | 1353114.149 | 1550991.422 | 1514682.1985 | 1421096.4459 | 1629082.1584 | 1590329.9717 | 1490043.4353 | 1759202.7677 | 1716664.1849 | 1606034.5852
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 376178.6308 | 369167.2654 | 351740.9436 | 421664.0691 | 412598.654 | 389617.9261 | 461604.6648 | 451043.8117 | 423962.1203 | 485961.6702 | 474585.1464 | 445262.5544 | 510429.3134 | 498287.3524 | 466865.2491 | 551199.1253 | 537870.7984 | 503207.9729
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1827 |  |  |  | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 609 |  |  |  | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 288 |  |  |  | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 500442.4336 | 491114.9905 | 467932.1987 | 560953.1632 | 548893.1523 | 518321.1569 | 614087.4119 | 600037.9721 | 564010.3341 | 646490.3133 | 631355.7606 | 592346.9811 | 679040.3995 | 662887.5615 | 621085.735 | 733277.781 | 715546.6825 | 669433.6199
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 14653339.8626 | 158.0273 | 176.0122 | 725972.4271 | 699162.7026 | 634713.4948 | 912147.5042 | 873348.3358 | 778770.952 | 1093131.1278 | 1043684.7572 | 922116.927 | 1211534.8617 | 1155473.9699 | 1017101.3487 | 1336605.0519 | 1273771.7456 | 1118188.3946 | 1558651.1448 | 1484184.2429 | 1299053.1201
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17.5586 | 19.5569 | 1628148.8736 | 1568022.3163 | 1423481.1447 | 2045686.4147 | 1958670.9578 | 1746560.8898 | 2451581.0077 | 2340686.9164 | 2068044.9834 | 2717126.7762 | 2591398.2024 | 2281067.9214 | 2997623.5027 | 2856706.3369 | 2507777.3028 | 3495609.49 | 3328601.4911 | 2913405.2415
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 244222.331 | 2.6338 | 2.9335 | 203641.5143 | 196121.1558 | 178042.5983 | 255865.2258 | 244981.7251 | 218451.955 | 306632.69 | 292762.5574 | 258661.7347 | 339845.9565 | 324120.3938 | 285305.6826 | 374929.2213 | 357303.9381 | 313661.469 | 437215.0615 | 416326.4546 | 364395.5812
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 156302.2919 | 1.6856 | 1.8775 | 1781269.4326 | 1715488.2253 | 1557353.564 | 2238074.6247 | 2142875.7298 | 1910817.6013 | 2682141.8984 | 2560818.6838 | 2262535.9228 | 2972661.1303 | 2835108.3126 | 2495592.7729 | 3279537.3951 | 3125367.5621 | 2743623.2188 | 3824356.8717 | 3641642.4724 | 3187398.7604
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 495891636.1127 | 495543499.2486 | 494691284.0872 | 498223351.1995 | 497748508.2641 | 496567367.6868 | 500375440.3502 | 499796884.0771 | 498344522.9424 | 501735870.7214 | 501095921.0852 | 499483065.7906 | 503139110.5424 | 502438170.0573 | 500666183.4845 | 505558846.471 | 504756580.0035 | 502721141.8935
| Survey, Design, Supervision etc. | [5 empty] | 7379566.4541 | 7376085.0855 | 7367562.9339 | 7402883.605 | 7398135.1756 | 7386323.7699 | 7424404.4965 | 7418618.9338 | 7404095.3224 | 7438008.8002 | 7431609.3038 | 7415480.7509 | 7452041.1984 | 7445031.7936 | 7427311.9278 | 7476238.5577 | 7468215.893 | 7447861.5119
| TOTAL COST | [5 empty] | 503271202.5669 | 502919584.3341 | 502058847.0211 | 505626234.8045 | 505146643.4398 | 503953691.4567 | 507799844.8467 | 507215503.0109 | 505748618.2648 | 509173879.5216 | 508527530.389 | 506898546.5415 | 510591151.7408 | 509883201.8509 | 508093495.4123 | 513035085.0287 | 512224795.8965 | 510169003.4055
| TOTAL COST IN RS. LAKHS | [5 empty] | 5032.712 | 5029.1958 | 5020.5885 | 5056.2623 | 5051.4664 | 5039.5369 | 5077.9984 | 5072.155 | 5057.4862 | 5091.7388 | 5085.2753 | 5068.9855 | 5105.9115 | 5098.832 | 5080.935 | 5130.3509 | 5122.248 | 5101.69
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 50.3271 | 50.292 | 50.2059 | 50.5626 | 50.5147 | 50.3954 | 50.78 | 50.7216 | 50.5749 | 50.9174 | 50.8528 | 50.6899 | 51.0591 | 50.9883 | 50.8093 | 51.3035 | 51.2225 | 51.0169
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 3268704.6378 | 3266646.0068 | 3261632.0596 | 3282489.3579 | 3279662.8649 | 3272667.882 | 3295287.2375 | 3291826.1033 | 3283181.6117 | 3303408.7391 | 3299569.6998 | 3289943.1539 | 3311808.3561 | 3307592.4689 | 3296988.3599 | 3326340.629 | 3321495.9911 | 3309266.1592
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 3268704.6378 | 3266646.0068 | 3261632.0596 | 3282489.3579 | 3279662.8649 | 3272667.882 | 3295287.2375 | 3291826.1033 | 3283181.6117 | 3303408.7391 | 3299569.6998 | 3289943.1539 | 3311808.3561 | 3307592.4689 | 3296988.3599 | 3326340.629 | 3321495.9911 | 3309266.1592
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 5171.2716 | 6521.2975 | 7409.1895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8543101.1457 | 8383241.0339 | 7987245.1339 | 9576321.4822 | 9369445.649 | 8846615.7148 | 10484222.4281 | 10243118.0431 | 9626620.6551 | 11038048.1566 | 10778279.3545 | 10110610.1655 | 11594462.7805 | 11317183.5237 | 10601584.2045 | 12521695.6098 | 12217285.8025 | 11427733.5408
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1281465.1719 | 1257486.1551 | 1198086.7701 | 1436448.2223 | 1405416.8474 | 1326992.3572 | 1572633.3642 | 1536467.7065 | 1443993.0983 | 1655707.2235 | 1616741.9032 | 1516591.5248 | 1739169.4171 | 1697577.5286 | 1590237.6307 | 1878254.3415 | 1832592.8704 | 1714160.0311
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 401512.83 | 393999.6466 | 375388.4384 | 450072.6228 | 440349.7716 | 415777.5556 | 492742.5938 | 481411.0525 | 452436.6079 | 518771.5653 | 506562.8245 | 475183.3827 | 544922.2108 | 531890.5052 | 498258.4198 | 588500.7511 | 574193.9507 | 537086.1888
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 2436 |  |  |  | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 4608 |  |  |  | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519 | 3182824.6519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 812 |  |  |  | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 384 |  |  |  | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 534145.327 | 524150.2995 | 499391.2154 | 598745.9686 | 585811.3494 | 553122.1466 | 655511.1923 | 640436.4813 | 601890.8533 | 690138.3633 | 673896.6861 | 632151.6135 | 724927.4015 | 707590.9077 | 662849.0715 | 782901.3238 | 763868.5308 | 714502.8913
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 19163449.2625 | 85.8156 | 94.7378 | 949417.3959 | 914218.4776 | 829889.2048 | 1192953.5194 | 1141967.8596 | 1018076.5015 | 1429876.5401 | 1364867.3465 | 1205518.2941 | 1584932.0856 | 1511210.4902 | 1329783.1321 | 1748748.4801 | 1666106.6804 | 1462068.1712 | 2039634.6114 | 1941670.6039 | 1698815.8306
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 9.5351 | 10.5264 | 2129272.1403 | 2050331.0166 | 1861204.5356 | 2675454.1308 | 2561107.8534 | 2283254.9106 | 3206804.8197 | 3061007.76 | 2703633.3329 | 3554550.1365 | 3389213.6472 | 2982323.8841 | 3921943.5364 | 3736601.5757 | 3279001.4568 | 4574318.0748 | 4354612.7768 | 3809958.8603
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 319390.821 | 1.4303 | 1.579 | 266319.7512 | 256446.1517 | 232791.0649 | 334633.73 | 320331.8136 | 285579.2213 | 401092.6765 | 382857.0382 | 338158.2575 | 444587.0916 | 423907.5496 | 373015.6141 | 490539.0002 | 467357.2641 | 410122.7061 | 572135.0638 | 544655.3165 | 476532.4623
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 204410.1255 | 0.91537 | 1.0105 | 2329521.2365 | 2243156.0319 | 2036243.0002 | 2927069.3478 | 2801969.2835 | 2497985.4393 | 3508391.3358 | 3348882.6754 | 2957898.6854 | 3888840.6383 | 3707954.9471 | 3262798.9118 | 4290785.8434 | 4088013.2503 | 3587377.7633 | 5004513.4655 | 4764145.8075 | 4168269.4792
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 653740927.5517 | 653329201.3661 | 652326411.9164 | 656497871.5771 | 655932572.9807 | 654533576.4002 | 659057447.5037 | 658365220.6566 | 656636322.3376 | 660681747.814 | 659913939.9556 | 657988630.7817 | 662361671.2232 | 661518493.789 | 659397671.9771 | 665268125.7949 | 664299198.2121 | 661853231.8376
| Survey, Design, Supervision etc. | [5 empty] | 8958059.3685 | 8953942.1066 | 8943914.2122 | 8985628.8088 | 8979975.8228 | 8965985.857 | 9011224.568 | 9004302.2996 | 8987013.3164 | 9027467.5711 | 9019789.4925 | 9000536.4008 | 9044266.8052 | 9035835.0309 | 9014626.8128 | 9073331.3509 | 9063642.0751 | 9039182.4114
| TOTAL COST | [5 empty] | 662698986.9202 | 662283143.4728 | 661270326.1286 | 665483500.3859 | 664912548.8035 | 663499562.2572 | 668068672.0718 | 667369522.9562 | 665623335.6539 | 669709215.3851 | 668933729.4482 | 666989167.1825 | 671405938.0284 | 670554328.8199 | 668412298.7899 | 674341457.1459 | 673362840.2872 | 670892414.249
| TOTAL COST IN RS. LAKHS | [5 empty] | 6626.9899 | 6622.8314 | 6612.7033 | 6654.835 | 6649.1255 | 6634.9956 | 6680.6867 | 6673.6952 | 6656.2334 | 6697.0922 | 6689.3373 | 6669.8917 | 6714.0594 | 6705.5433 | 6684.123 | 6743.4146 | 6733.6284 | 6708.9241
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 66.2699 | 66.2283 | 66.127 | 66.5484 | 66.4913 | 66.35 | 66.8069 | 66.737 | 66.5623 | 66.9709 | 66.8934 | 66.6989 | 67.1406 | 67.0554 | 66.8412 | 67.4341 | 67.3363 | 67.0892
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 961363.0549 | 960588.7745 | 959130.0652 | 965176.2884 | 964125.2925 | 962108.8937 | 968668.1895 | 967394.5948 | 964924.3689 | 970862.429 | 969458.8958 | 966723.4348 | 973115.4458 | 971584.1386 | 968588.2668 | 976977.1897 | 975236.2629 | 971814.7231
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 961363.0549 | 960588.7745 | 959130.0652 | 965176.2884 | 964125.2925 | 962108.8937 | 968668.1895 | 967394.5948 | 964924.3689 | 970862.429 | 969458.8958 | 966723.4348 | 973115.4458 | 971584.1386 | 968588.2668 | 976977.1897 | 975236.2629 | 971814.7231
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 12.8652 | 15.2805 | 16.8693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 1.9298 | 2.2921 | 2.5304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 1543.8232 | 1833.6656 | 2024.3112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 3284960.7387 | 3205197.7366 | 3053017.5594 | 3668181.2522 | 3564092.7577 | 3361150.7555 | 4006235.1596 | 3884277.7708 | 3643334.0973 | 4212934.4634 | 4081209.1455 | 3819398.7606 | 4420902.8243 | 4280011.3345 | 3998625.6635 | 4768023.3781 | 4612943.0683 | 4301350.1076
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 492744.1108 | 480779.6605 | 457952.6339 | 550227.1878 | 534613.9137 | 504172.6133 | 600935.2739 | 582641.6656 | 546500.1146 | 631940.1695 | 612181.3718 | 572909.8141 | 663135.4236 | 642001.7002 | 599793.8495 | 715203.5067 | 691941.4602 | 645202.5161
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 154388.1853 | 150639.4449 | 143487.2068 | 172398.9697 | 167506.9679 | 157969.0008 | 188286.992 | 182555.1792 | 171231.191 | 198001.5465 | 191810.6559 | 179505.9638 | 207775.7449 | 201154.058 | 187929.3572 | 224089.8858 | 216801.3459 | 202156.9481
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 609 |  |  |  | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 1152 |  |  |  | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 96 |  |  |  | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 205387.5283 | 200400.4593 | 190885.6087 | 229347.8494 | 222839.8633 | 210151.2014 | 250484.1922 | 242858.9788 | 227794.3161 | 263407.7741 | 255171.8347 | 238802.5104 | 276410.702 | 267601.6607 | 250008.4192 | 298113.9241 | 288417.7469 | 268935.8373
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 3829030.9303 | 0 | 0 | 189702.2047 | 180601.6303 | 163859.1191 | 236544.8981 | 223310.9444 | 198604.0021 | 282153.14 | 265236.0615 | 233351.1837 | 312019.2712 | 292812.5684 | 256449.5948 | 343584.8052 | 322034.0915 | 281082.3071 | 399658.233 | 374083.1969 | 325253.2151
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 425447.8811 | 405037.8912 | 367489.219 | 530502.6678 | 500822.6883 | 445412.071 | 632788.9324 | 594848.7555 | 523340.0783 | 699770.1373 | 656694.9867 | 575143.2195 | 770562.6174 | 722230.5197 | 630387.36 | 896319.3057 | 838961.8021 | 729450.0949
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 63817.1822 | 0 | 0 | 53213.1012 | 50660.3117 | 45963.8933 | 66352.8799 | 62640.6419 | 55710.132 | 79146.3843 | 74400.9982 | 65457.0155 | 87524.0911 | 82136.4457 | 71936.3186 | 96378.4951 | 90333.3344 | 78846.0064 | 112107.5742 | 104933.5565 | 91236.3263
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 40842.9966 | 0 | 0 | 465459.4664 | 443130.0026 | 402050.0356 | 580394.2142 | 547922.9573 | 487301.2043 | 692300.0721 | 650791.781 | 572558.0133 | 765580.5778 | 718454.3903 | 629233.0221 | 843030.7931 | 790153.2648 | 689672.6419 | 980614.3695 | 917862.6337 | 798051.8107
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 192272610.9771 | 192117754.8978 | 191826013.0366 | 193035257.6799 | 192825058.4952 | 192421778.7412 | 193733637.9072 | 193478918.9514 | 192984873.7704 | 194172485.7917 | 193891779.1597 | 193344686.9647 | 194623089.1663 | 194316827.7246 | 193717653.3657 | 195395437.9378 | 195047252.5713 | 194362944.6168
| Survey, Design, Supervision etc. | [5 empty] | 4343376.2028 | 4341827.642 | 4338910.2234 | 4351002.6698 | 4348900.6779 | 4344867.8804 | 4357986.4721 | 4355439.2825 | 4350498.8307 | 4362374.9509 | 4359567.8846 | 4354096.9626 | 4366880.9847 | 4363818.3702 | 4357826.6266 | 4374604.4724 | 4371122.6187 | 4364279.5392
| TOTAL COST | [5 empty] | 196615987.1799 | 196459582.5398 | 196164923.26 | 197386260.3497 | 197173959.1731 | 196766646.6216 | 198091624.3793 | 197834358.2339 | 197335372.6011 | 198534860.7426 | 198251347.0443 | 197698783.9273 | 198989970.1509 | 198680646.0948 | 198075479.9923 | 199770042.4102 | 199418375.19 | 198727224.156
| TOTAL COST IN RS. LAKHS | [5 empty] | 1966.1599 | 1964.5958 | 1961.6492 | 1973.8626 | 1971.7396 | 1967.6665 | 1980.9162 | 1978.3436 | 1973.3537 | 1985.3486 | 1982.5135 | 1976.9878 | 1989.8997 | 1986.8065 | 1980.7548 | 1997.7004 | 1994.1838 | 1987.2722
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 19.6616 | 19.646 | 19.6165 | 19.7386 | 19.7174 | 19.6767 | 19.8092 | 19.7834 | 19.7335 | 19.8535 | 19.8251 | 19.7699 | 19.899 | 19.8681 | 19.8075 | 19.977 | 19.9418 | 19.8727
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1334212.182 | 1333221.031 | 1331380.1223 | 1339048.2185 | 1337692.9421 | 1335127.8979 | 1343505.5818 | 1341854.7479 | 1338694.7849 | 1346317.7423 | 1344493.4703 | 1340983.9007 | 1349212.9669 | 1347217.574 | 1343363.5764 | 1354191.4074 | 1351914.2079 | 1347495.0228
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1334212.182 | 1333221.031 | 1331380.1223 | 1339048.2185 | 1337692.9421 | 1335127.8979 | 1343505.5818 | 1341854.7479 | 1338694.7849 | 1346317.7423 | 1344493.4703 | 1340983.9007 | 1349212.9669 | 1347217.574 | 1343363.5764 | 1354191.4074 | 1351914.2079 | 1347495.0228
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 26.8371 | 32.7017 | 36.5643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4.0256 | 4.9053 | 5.4846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 3220.4572 | 3924.209 | 4387.7149 | 3895809.9723 | 3799959.9029 | 3619397.6448 | 4350752.1776 | 4225299.6474 | 3983546.6946 | 4753028.6402 | 4605821.3787 | 4318183.3507 | 4999254.8728 | 4840163.5204 | 4527336.8503 | 5247120.5665 | 5076885.5687 | 4740445.1778 | 5661015.23 | 5473548.73 | 5100712.1952
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 1288.1829 | 1569.6836 | 1755.086 | 584371.4958 | 569993.9854 | 542909.6467 | 652612.8266 | 633794.9471 | 597532.0042 | 712954.296 | 690873.2068 | 647727.5026 | 749888.2309 | 726024.5281 | 679100.5275 | 787068.085 | 761532.8353 | 711066.7767 | 849152.2845 | 821032.3095 | 765106.8293
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 183097.1752 | 178592.3669 | 170106.214 | 204478.7706 | 198582.6915 | 187220.6684 | 223385.1558 | 216466.6372 | 202948.085 | 234957.4163 | 227480.3634 | 212777.9831 | 246606.7289 | 238605.9415 | 222793.7521 | 266059.152 | 257248.51 | 239725.7569
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 913.5 |  |  |  | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 1152 |  |  |  | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 144 |  |  |  | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 243580.0134 | 237587.1233 | 226297.7232 | 272024.6319 | 264180.8898 | 249065.628 | 297176.3993 | 287972.4733 | 269988.3121 | 312571.3466 | 302624.3846 | 283065.3391 | 328068.7988 | 317425.0961 | 296389.6361 | 353946.9778 | 342225.8998 | 318914.8223
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 5385475.2928 | 22535.8691 | 25593.0982 | 266813.3413 | 253845.8335 | 230295.0538 | 332767.3468 | 313853.545 | 278966.3603 | 397148.4519 | 372929.0323 | 327803.9397 | 439362.0772 | 411843.3709 | 360327.6831 | 484009.7367 | 453113.2488 | 395048.3648 | 563379.0046 | 526683.8352 | 457376.2932
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 2503.9855 | 2843.6776 | 598386.1436 | 569303.7263 | 516486.0517 | 746302.1469 | 703883.8897 | 625641.8953 | 890690.5835 | 836373.3403 | 735170.6418 | 985363.692 | 923647.0909 | 808112.112 | 1085495.6446 | 1016203.6437 | 885980.6875 | 1263498.2509 | 1181201.4631 | 1025764.435
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 89757.9215 | 375.5978 | 426.5516 | 74843.4387 | 71205.9412 | 64599.7448 | 93344.1049 | 88038.6207 | 78252.4651 | 111403.5591 | 104609.8034 | 91951.8265 | 123244.8443 | 115525.6103 | 101075.0165 | 135768.8971 | 127102.1663 | 110814.4665 | 158032.6598 | 147739.349 | 128297.9869
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 57445.0698 | 240.3826 | 272.993 | 654661.8456 | 622844.3491 | 565059.3942 | 816488.7273 | 770081.2114 | 684480.8862 | 974456.2896 | 915030.738 | 804310.351 | 1078033.0061 | 1010512.218 | 884111.6599 | 1187581.948 | 1111773.3257 | 969303.4477 | 1382324.9513 | 1292288.4965 | 1122233.2692
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 266842436.4033 | 266644206.2058 | 266276024.4504 | 267809643.71 | 267538588.4198 | 267025579.5794 | 268701116.3527 | 268370949.5872 | 267738956.9865 | 269263548.4633 | 268898694.0636 | 268196780.1488 | 269842593.3827 | 269443514.8034 | 268672715.2864 | 270838281.4881 | 270382841.5703 | 269499004.5651
| Survey, Design, Supervision etc. | [5 empty] | 5089074.457 | 5087092.155 | 5083410.3375 | 5098746.5301 | 5096035.9772 | 5090905.8888 | 5107661.2565 | 5104359.5889 | 5098039.6629 | 5113285.5776 | 5109637.0336 | 5102617.8945 | 5119076.0268 | 5115085.241 | 5107377.2459 | 5129032.9079 | 5124478.5087 | 5115640.1386
| TOTAL COST | [5 empty] | 271931510.8603 | 271731298.3609 | 271359434.7879 | 272908390.2401 | 272634624.397 | 272116485.4681 | 273808777.6092 | 273475309.176 | 272836996.6494 | 274376834.0409 | 274008331.0972 | 273299398.0433 | 274961669.4096 | 274558600.0444 | 273780092.5323 | 275967314.396 | 275507320.079 | 274614644.7037
| TOTAL COST IN RS. LAKHS | [5 empty] | 2719.3151 | 2717.313 | 2713.5943 | 2729.0839 | 2726.3462 | 2721.1649 | 2738.0878 | 2734.7531 | 2728.37 | 2743.7683 | 2740.0833 | 2732.994 | 2749.6167 | 2745.586 | 2737.8009 | 2759.6731 | 2755.0732 | 2746.1464
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 27.1932 | 27.1731 | 27.1359 | 27.2908 | 27.2635 | 27.2116 | 27.3809 | 27.3475 | 27.2837 | 27.4377 | 27.4008 | 27.3299 | 27.4962 | 27.4559 | 27.378 | 27.5967 | 27.5507 | 27.4615
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1710513.5383 | 1709320.1789 | 1707121.5777 | 1716310.2883 | 1714670.422 | 1711590.8547 | 1721676.9077 | 1719672.2371 | 1715863.9732 | 1725072.2325 | 1722852.6424 | 1718614.4079 | 1728574.501 | 1726142.3259 | 1721479.3828 | 1734610.6701 | 1731827.3895 | 1726465.4431
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1710513.5383 | 1709320.1789 | 1707121.5777 | 1716310.2883 | 1714670.422 | 1711590.8547 | 1721676.9077 | 1719672.2371 | 1715863.9732 | 1725072.2325 | 1722852.6424 | 1718614.4079 | 1728574.501 | 1726142.3259 | 1721479.3828 | 1734610.6701 | 1731827.3895 | 1726465.4431
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 6.2783 | 7.4713 | 8.2549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5022.6622 | 5977.0135 | 6603.9322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 4423087.5671 | 4313478.6421 | 4108425.7817 | 4939892.238 | 4796202.3555 | 4521056.7497 | 5397466.2904 | 5228725.2122 | 4900972.5112 | 5677700.3949 | 5495279.5851 | 5138652.6464 | 5959879.7553 | 5764636.7737 | 5380951.0098 | 6431184.9557 | 6216126.4182 | 5790761.353
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 663463.1351 | 647021.7963 | 616263.8673 | 740983.8357 | 719430.3533 | 678158.5125 | 809619.9436 | 784308.7818 | 735145.8767 | 851655.0592 | 824291.9378 | 770797.897 | 893981.9633 | 864695.5161 | 807142.6515 | 964677.7434 | 932418.9627 | 868614.2029
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 207878.4245 | 202726.9708 | 193089.7966 | 232167.4622 | 225414.2551 | 212482.8279 | 253672.7505 | 245742.1751 | 230338.2939 | 266843.3295 | 258269.8274 | 241508.9007 | 280105.3325 | 270929.2078 | 252896.5573 | 302255.964 | 292148.538 | 272157.0235
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 276547.3 | 269694.1568 | 256873.5165 | 308859.7817 | 299875.7749 | 282672.6847 | 337468.9528 | 326918.6553 | 306426.3808 | 354990.1941 | 343584.5908 | 321286.9954 | 372633.0599 | 360425.7684 | 336436.3582 | 402100.7516 | 388654.5204 | 362059.1708
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 6941919.6554 | 161773.7303 | 178816.3574 | 343924.4779 | 327090.0368 | 296730.9885 | 428989.7956 | 404396.1457 | 359328.7185 | 512143.7639 | 480622.003 | 422256.6957 | 566704.8831 | 530874.1733 | 464205.7713 | 624434.6683 | 584192.4061 | 509014.4224 | 727099.7763 | 679284.4735 | 589499.3712
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17974.8589 | 19868.4842 | 771324.4062 | 733569.5614 | 665482.8843 | 962101.6259 | 906945.0912 | 805871.7197 | 1148592.2346 | 1077897.9251 | 947001.2053 | 1270957.2467 | 1190599.1951 | 1041081.0046 | 1400428.6718 | 1310176.7677 | 1141574.0151 | 1630677.196 | 1523441.1241 | 1322078.7752
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 115698.6609 | 2696.2288 | 2980.2726 | 96473.7762 | 91751.5706 | 83235.5963 | 120335.33 | 113436.5995 | 100794.7983 | 143660.7338 | 134818.6086 | 118446.6375 | 158965.5974 | 148914.7749 | 130213.7143 | 175159.299 | 163870.9981 | 142782.9266 | 203957.7455 | 190545.1415 | 165359.6475
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 74047.143 | 1725.5865 | 1907.3745 | 843864.2249 | 802558.6957 | 728068.7528 | 1052583.2404 | 992239.4654 | 881660.5681 | 1256612.5071 | 1179269.6949 | 1036062.6887 | 1390485.4344 | 1302570.0457 | 1138990.2978 | 1532133.1028 | 1433393.3865 | 1248934.2535 | 1784035.5332 | 1666714.3593 | 1446414.7277
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 342102707.6684 | 341864035.7871 | 341424315.5406 | 343262057.6662 | 342934084.3973 | 342318170.936 | 344335381.5332 | 343934447.4127 | 343172794.6464 | 345014446.496 | 344570528.4866 | 343722881.5841 | 345714900.2096 | 345228465.1811 | 344295876.551 | 346922134.0223 | 346365477.8944 | 345293088.6284
| Survey, Design, Supervision etc. | [5 empty] | 5841677.1697 | 5839290.4509 | 5834893.2484 | 5853270.6696 | 5849990.937 | 5843831.8023 | 5864003.9083 | 5859994.5671 | 5852378.0395 | 5870794.5579 | 5866355.3779 | 5857878.9088 | 5877799.0951 | 5872934.7448 | 5863608.8585 | 5889871.4332 | 5884304.8719 | 5873580.9793
| TOTAL COST | [5 empty] | 347944384.8381 | 347703326.238 | 347259208.789 | 349115328.3358 | 348784075.3343 | 348162002.7383 | 350199385.4415 | 349794441.9798 | 349025172.6859 | 350885241.0539 | 350436883.8645 | 349580760.4929 | 351592699.3047 | 351101399.9259 | 350159485.4095 | 352812005.4555 | 352249782.7663 | 351166669.6077
| TOTAL COST IN RS. LAKHS | [5 empty] | 3479.4438 | 3477.0333 | 3472.5921 | 3491.1533 | 3487.8408 | 3481.62 | 3501.9939 | 3497.9444 | 3490.2517 | 3508.8524 | 3504.3688 | 3495.8076 | 3515.927 | 3511.014 | 3501.5949 | 3528.1201 | 3522.4978 | 3511.6667
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 34.7944 | 34.7703 | 34.7259 | 34.9115 | 34.8784 | 34.8162 | 35.0199 | 34.9794 | 34.9025 | 35.0885 | 35.0437 | 34.9581 | 35.1593 | 35.1101 | 35.0159 | 35.2812 | 35.225 | 35.1167
ESTIMATE FOR A 765 KV, SC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 999058.1853 | 997738.6933 | 995269.831 | 1005830.6355 | 1004049.7007 | 1000664.1092 | 1012000.2231 | 1009850.4531 | 1005724.8815 | 1015865.3702 | 1013501.0066 | 1008944.5827 | 1019826.4462 | 1017251.4631 | 1012272.8324 | 1026600.982 | 1023681.162 | 1018013.6139
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 999058.1853 | 997738.6933 | 995269.831 | 1005830.6355 | 1004049.7007 | 1000664.1092 | 1012000.2231 | 1009850.4531 | 1005724.8815 | 1015865.3702 | 1013501.0066 | 1008944.5827 | 1019826.4462 | 1017251.4631 | 1012272.8324 | 1026600.982 | 1023681.162 | 1018013.6139
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 33.3523 | 40.1376 | 44.6039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5.0029 | 6.0206 | 6.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4002.281 | 4816.5159 | 5352.4685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 5969732.8625 | 5828889.6017 | 5562345.1813 | 6676005.8618 | 6492879.3319 | 6139682.5939 | 7297034.6461 | 7082922.0989 | 6665181.5049 | 7676164.6287 | 7445119.1126 | 6991980.1598 | 8057306.2644 | 7810366.8671 | 7324017.3222 | 8692976.3697 | 8421417.8379 | 7883774.6479
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 895459.9294 | 874333.4403 | 834351.7772 | 1001400.8793 | 973931.8998 | 920952.3891 | 1094555.1969 | 1062438.3148 | 999777.2257 | 1151424.6943 | 1116767.8669 | 1048797.024 | 1208595.9397 | 1171555.0301 | 1098602.5983 | 1303946.4555 | 1263212.6757 | 1182566.1972
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 280568.4137 | 273948.9935 | 261421.8089 | 313762.1762 | 305155.5063 | 288555.7939 | 342949.5896 | 332886.6238 | 313253.4478 | 360768.1252 | 349909.3355 | 328612.4902 | 378681.2055 | 367075.4274 | 344217.7345 | 408556.7388 | 395793.8987 | 370525.4821
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 609 |  |  |  | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 1920 |  |  |  | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 373249.1115 | 364443.0857 | 347777.7724 | 417407.8328 | 405958.1053 | 383874.9783 | 456236.78 | 442849.6955 | 416731.0552 | 479941.3464 | 465495.552 | 437163.6793 | 503771.6886 | 488332.1517 | 457923.8337 | 543516.0636 | 526537.2502 | 492921.8695
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 7907691.8314 | 0 | 0 | 326476.5511 | 311253.2241 | 283437.9978 | 408296.4629 | 386204.0843 | 345329.7852 | 487792.3842 | 459586.3585 | 406973.527 | 539797.3642 | 507791.5849 | 447860.307 | 594732.8708 | 558836.8896 | 491406.5314 | 692275.8747 | 649699.6468 | 569391.0055
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 878632.4257 | 837662.5348 | 762804.6018 | 1098830.8667 | 1039374.59 | 929371.3311 | 1312774.8512 | 1236865.1766 | 1095270.5059 | 1452733.6374 | 1366597.8478 | 1205307.3541 | 1600579.2245 | 1503973.9006 | 1322501.4516 | 1863092.5532 | 1748508.9658 | 1532377.7428
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 131794.8639 | 0 | 0 | 73263.5861 | 69847.3667 | 63605.4384 | 91624.5376 | 86666.8558 | 77494.3816 | 109463.9698 | 103134.3434 | 91327.6617 | 121134.2454 | 113951.9281 | 100502.9367 | 133462.1513 | 125406.846 | 110275.0093 | 155351.4731 | 145797.0743 | 127775.2623
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 84348.7129 | 0 | 0 | 576758.4677 | 549864.7055 | 500725.9013 | 721302.7751 | 682274.0412 | 610064.8794 | 861741.4853 | 811912.289 | 718965.6564 | 953614.2784 | 897072.3792 | 791196.8672 | 1050664.1844 | 987249.7951 | 868126.2931 | 1222985.1467 | 1147769.3314 | 1005894.8577
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 199811637.0633 | 199547738.668 | 199053966.1951 | 201166127.1082 | 200809940.1304 | 200132821.8483 | 202400044.619 | 201970090.6164 | 201144976.3004 | 203173074.0358 | 202700201.3228 | 201788916.5341 | 203965289.2451 | 203450292.6234 | 202454566.4899 | 205320196.3912 | 204736232.3966 | 203602722.7807
| Survey, Design, Supervision etc. | [5 empty] | 4418766.4636 | 4416127.4797 | 4411189.7549 | 4432311.3641 | 4428749.4943 | 4421978.3115 | 4444650.5392 | 4440350.9992 | 4432099.856 | 4452380.8333 | 4447652.1062 | 4438539.2583 | 4460302.9854 | 4455153.0192 | 4445195.7579 | 4473852.0569 | 4468012.417 | 4456677.3208
| TOTAL COST | [5 empty] | 204230403.527 | 203963866.1477 | 203465155.95 | 205598438.4723 | 205238689.6247 | 204554800.1598 | 206844695.1581 | 206410441.6155 | 205577076.1564 | 207625454.8692 | 207147853.4291 | 206227455.7924 | 208425592.2305 | 207905445.6426 | 206899762.2478 | 209794048.4481 | 209204244.8136 | 208059400.1015
| TOTAL COST IN RS. LAKHS | [5 empty] | 2042.304 | 2039.6387 | 2034.6516 | 2055.9844 | 2052.3869 | 2045.548 | 2068.447 | 2064.1044 | 2055.7708 | 2076.2545 | 2071.4785 | 2062.2746 | 2084.2559 | 2079.0545 | 2068.9976 | 2097.9405 | 2092.0424 | 2080.594
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 20.423 | 20.3964 | 20.3465 | 20.5598 | 20.5239 | 20.4555 | 20.6845 | 20.641 | 20.5577 | 20.7625 | 20.7148 | 20.6227 | 20.8426 | 20.7905 | 20.69 | 20.9794 | 20.9204 | 20.8059
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1376353.9865 | 1374661.592 | 1371559.8925 | 1384899.3563 | 1382599.0153 | 1378311.3536 | 1392733.9857 | 1389943.455 | 1384689.5797 | 1397661.4849 | 1394584.2706 | 1388764.8329 | 1402724.4223 | 1399364.8939 | 1392989.4053 | 1411410.3918 | 1407586.8648 | 1400300.6639
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1376353.9865 | 1374661.592 | 1371559.8925 | 1384899.3563 | 1382599.0153 | 1378311.3536 | 1392733.9857 | 1389943.455 | 1384689.5797 | 1397661.4849 | 1394584.2706 | 1388764.8329 | 1402724.4223 | 1399364.8939 | 1392989.4053 | 1411410.3918 | 1407586.8648 | 1400300.6639
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 7079406.516 | 6909119.698 | 6593003.4193 | 7917117.9139 | 7695100.9009 | 7274487.9431 | 8655463.3523 | 8395530.4648 | 7896973.51 | 9106671.6487 | 8826033.7497 | 8284748.2741 | 9560493.065 | 9260434.806 | 8679092.7753 | 10317675.9463 | 9987565.9822 | 9344435.5613
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1061910.9774 | 1036367.9547 | 988950.5129 | 1187567.6871 | 1154265.1351 | 1091173.1915 | 1298319.5028 | 1259329.5697 | 1184546.0265 | 1366000.7473 | 1323905.0625 | 1242712.2411 | 1434073.9597 | 1389065.2209 | 1301863.9163 | 1547651.3919 | 1498134.8973 | 1401665.3342
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 332721.3967 | 324718.1738 | 309861.187 | 372092.5651 | 361658.1014 | 341889.9286 | 406793.6838 | 394577.2313 | 371145.8086 | 427999.7911 | 414810.2344 | 389370.6359 | 449328.7112 | 435226.4269 | 407904.2309 | 484915.1611 | 469400.4922 | 439174.3353
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 913.5 |  |  |  | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 1920 |  |  |  | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 442629.8886 | 431982.946 | 412218.2224 | 495006.61 | 481125.31 | 454827.0792 | 541170.6152 | 524918.6788 | 493747.1097 | 569381.7764 | 551835.2883 | 517992.1788 | 597756.3191 | 578995.6005 | 542648.0115 | 645098.1088 | 624458.4498 | 584247.629
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 11120738.8878 | 0 | 0 | 459130.2436 | 437308.2116 | 398206.9181 | 574217.5016 | 542463.8932 | 484782.6359 | 686313.9757 | 645711.4427 | 571299.1282 | 759733.9861 | 713630.4398 | 628783.0607 | 837341.817 | 785606.2975 | 690066.3663 | 975227.5602 | 913821.8158 | 799923.298
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1235637.6542 | 1176908.9494 | 1071677.3051 | 1545367.0859 | 1459909.9532 | 1304674.8439 | 1847047.5484 | 1737775.6823 | 1537512.9918 | 2044639.693 | 1920563.1839 | 1692217.0493 | 2253502.3402 | 2114268.7419 | 1857146.1973 | 2624588.3635 | 2459329.7011 | 2152799.4749
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 185345.6481 | 0 | 0 | 103031.9881 | 98134.9738 | 89360.3743 | 128858.3612 | 121732.6329 | 108788.5615 | 154013.5819 | 144902.0939 | 128203.4581 | 170489.5377 | 160143.5845 | 141103.2484 | 187905.2694 | 176295.4626 | 154855.6441 | 218847.7796 | 205067.9077 | 179508.296
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 118621.2148 | 0 | 0 | 811106.5096 | 772555.374 | 703478.4311 | 1014421.4194 | 958325.0093 | 856424.4179 | 1212452.7647 | 1140723.7091 | 1009265.7762 | 1342157.6779 | 1260710.4479 | 1110817.7706 | 1479260.8588 | 1387864.0989 | 1219081.7953 | 1722851.9213 | 1614371.5942 | 1413156.7308
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 275270797.2979 | 274932318.4048 | 274311978.4939 | 276979871.2679 | 276519803.0597 | 275662270.7253 | 278546797.1483 | 277988690.9962 | 276937915.9328 | 279532296.9819 | 278916854.1145 | 277752966.5826 | 280544884.464 | 279872978.7788 | 278597881.0607 | 282282078.3565 | 281517372.964 | 280060132.7831
| Survey, Design, Supervision etc. | [5 empty] | 5173358.066 | 5169973.277 | 5163769.8779 | 5190448.8057 | 5185848.1236 | 5177272.8002 | 5206118.0645 | 5200537.0029 | 5190029.2523 | 5215973.0628 | 5209818.6341 | 5198179.7588 | 5226098.9376 | 5219379.8808 | 5206628.9036 | 5243470.8766 | 5235823.8226 | 5221251.4208
| TOTAL COST | [5 empty] | 280444155.3638 | 280102291.6819 | 279475748.3718 | 282170320.0736 | 281705651.1833 | 280839543.5256 | 283752915.2128 | 283189227.9991 | 282127945.1851 | 284748270.0447 | 284126672.7487 | 282951146.3414 | 285770983.4017 | 285092358.6596 | 283804509.9643 | 287525549.233 | 286753196.7866 | 285281384.2039
| TOTAL COST IN RS. LAKHS | [5 empty] | 2804.4416 | 2801.0229 | 2794.7575 | 2821.7032 | 2817.0565 | 2808.3954 | 2837.5292 | 2831.8923 | 2821.2795 | 2847.4827 | 2841.2667 | 2829.5115 | 2857.7098 | 2850.9236 | 2838.0451 | 2875.2555 | 2867.532 | 2852.8138
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 28.0444 | 28.0102 | 27.9476 | 28.217 | 28.1706 | 28.084 | 28.3753 | 28.3189 | 28.2128 | 28.4748 | 28.4127 | 28.2951 | 28.5771 | 28.5092 | 28.3805 | 28.7526 | 28.6753 | 28.5281
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
PLAIN AREA, PREDOMINANTLY NORMAL SOIL
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1888694.0162 | 1886656.1633 | 1882964.3414 | 1898898.9927 | 1896115.8381 | 1890985.2941 | 1908296.4106 | 1904908.4337 | 1898597.8768 | 1914223.1478 | 1910480.0515 | 1903476.0156 | 1920324.1668 | 1916230.4727 | 1908542.8701 | 1930814.7468 | 1926143.134 | 1917332.6839
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1888694.0162 | 1886656.1633 | 1882964.3414 | 1898898.9927 | 1896115.8381 | 1890985.2941 | 1908296.4106 | 1904908.4337 | 1898597.8768 | 1914223.1478 | 1910480.0515 | 1903476.0156 | 1920324.1668 | 1916230.4727 | 1908542.8701 | 1930814.7468 | 1926143.134 | 1917332.6839
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8037305.6921 | 7841933.1808 | 7483027.7467 | 8988462.4858 | 8733365.5444 | 8254734.8422 | 9827887.7211 | 9529012.4415 | 8961012.0379 | 10341152.4323 | 10018380.3532 | 9401399.9689 | 10857526.0097 | 10512348.6907 | 9849470.6999 | 11719259.1788 | 11339429.8841 | 10605802.6202
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1205595.8538 | 1176289.9771 | 1122454.162 | 1348269.3729 | 1310004.8317 | 1238210.2263 | 1474183.1582 | 1429351.8662 | 1344151.8057 | 1551172.8649 | 1502757.053 | 1410209.9953 | 1628628.9015 | 1576852.3036 | 1477420.605 | 1757888.8768 | 1700914.4826 | 1590870.393
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 377741.2089 | 368558.9964 | 351690.9839 | 422444.1393 | 410454.9689 | 387960.05 | 461895.8555 | 447849.1695 | 421154.0098 | 486018.5205 | 470848.721 | 441851.5763 | 510287.2974 | 494064.4856 | 462910.2228 | 550787.4528 | 532936.0505 | 498456.6789
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 3840 |  |  |  | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298 | 2905284.5298
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 163660.9478 | 100 |  |  |  | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 502521.181 | 490305.7909 | 467865.7357 | 561990.9155 | 546041.3397 | 516115.6314 | 614474.7922 | 595788.0377 | 560274.615 | 646565.943 | 626385.0748 | 587809.2481 | 678851.4712 | 657269.7471 | 615824.2374 | 732730.1199 | 708981.83 | 663112.822
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 14333785.9442 | 0 | 0 | 591783.9362 | 563363.199 | 512975.8385 | 740138.5403 | 698723.7022 | 624235.4866 | 884835.5671 | 831836.527 | 735624.7293 | 979670.608 | 919469.2946 | 809705.8144 | 1079950.7632 | 1012375.7054 | 888726.2012 | 1258179.2457 | 1177943.9849 | 1030455.5904
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1592642.8827 | 1516155.364 | 1380550.0084 | 1991903.305 | 1880445.3165 | 1679978.3568 | 2381320.2455 | 2238686.1879 | 1979755.4778 | 2636545.7485 | 2474528.5199 | 2179126.7444 | 2906425.4559 | 2724563.5832 | 2391790.943 | 3386084.1739 | 3170150.4363 | 2773221.2069
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 238896.4324 | 0 | 0 | 132800.3901 | 126422.581 | 115115.3103 | 166092.1848 | 156798.4099 | 140082.7414 | 198563.1939 | 186669.8444 | 165079.2545 | 219844.8301 | 206335.2408 | 181703.5601 | 242348.3874 | 227184.0792 | 199436.279 | 282344.0861 | 264338.7411 | 231241.3298
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 152893.7167 | 0 | 0 | 1045454.5515 | 995246.0424 | 906230.9608 | 1307540.0637 | 1234375.9774 | 1102783.9565 | 1563164.0441 | 1469535.1292 | 1299565.8961 | 1730701.0774 | 1624348.5166 | 1430438.674 | 1907857.5332 | 1788478.4027 | 1570037.2976 | 2222718.6959 | 2080973.8571 | 1820418.6039
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 1500 | 1500 | 1500 | 1500 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885 | 190133.0885
| b) Fissured rock | 752.9865 | 4000 | 4000 | 4000 | 4000 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207 | 3011946.1207
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 1500 | 1500 | 1500 | 1500 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717 | 4580584.2717
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 100 | 100 | 100 | 100 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177 | 492742.7177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 377738803.2317 | 377331232.6669 | 376592868.2819 | 379779798.5428 | 379223167.6261 | 378197058.8267 | 381659282.1129 | 380981686.7388 | 379719575.3615 | 382844629.56 | 382096010.3094 | 380695203.117 | 384064833.3549 | 383246094.5327 | 381708574.0212 | 386162949.3654 | 385228626.8019 | 383466536.7806
| Survey, Design, Supervision etc. | [5 empty] | 6198038.1253 | 6193962.4197 | 6186578.7758 | 6218448.0784 | 6212881.7692 | 6202620.6813 | 6237242.9141 | 6230466.9604 | 6217845.8466 | 6249096.3886 | 6241610.1961 | 6227602.1242 | 6261298.4265 | 6253111.0383 | 6237735.8332 | 6282279.5866 | 6272936.361 | 6255315.4608
| TOTAL COST | [5 empty] | 383936841.3571 | 383525195.0866 | 382779447.0577 | 385998246.6212 | 385436049.3953 | 384399679.5079 | 387896525.0271 | 387212153.6992 | 385937421.2081 | 389093725.9486 | 388337620.5054 | 386922805.2412 | 390326131.7815 | 389499205.571 | 387946309.8544 | 392445228.952 | 391501563.1629 | 389721852.2414
| TOTAL COST IN RS. LAKHS | [5 empty] | 3839.3684 | 3835.252 | 3827.7945 | 3859.9825 | 3854.3605 | 3843.9968 | 3878.9653 | 3872.1215 | 3859.3742 | 3890.9373 | 3883.3762 | 3869.2281 | 3903.2613 | 3894.9921 | 3879.4631 | 3924.4523 | 3915.0156 | 3897.2185
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 38.3937 | 38.3525 | 38.2779 | 38.5998 | 38.5436 | 38.44 | 38.7897 | 38.7212 | 38.5937 | 38.9094 | 38.8338 | 38.6923 | 39.0326 | 38.9499 | 38.7946 | 39.2445 | 39.1502 | 38.9722
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 13440252.5658 | 14117921.7674 | 14547211.5918
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 7906030.9211 | 8304659.8632 | 8557183.2893
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 7906030.9211 | 8304659.8632 | 8557183.2893
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 16508.0925 | 18532.0288 | 19750.7674 | 208001965.4743 | 233503562.6456 | 248859669.4525
| b) 'B' Type towers | 60000 | 25 | 22935.8387 | 25336.28 | 26798.9755 | 34403758.1069 | 38004420.0232 | 40198463.2127
| c) 'C' Type towers | 60000 | 25 | 27367.7998 | 30022.8969 | 31649.2306 | 41051699.6895 | 45034345.3439 | 47473845.9071
| d) 'D' Type towers | 60000 | 20 | 30499.6211 | 33278.2668 | 34987.2913 | 36599545.2934 | 39933920.1689 | 41984749.5951
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 12199.8484 | 13311.3067 | 13994.9165 | 731990.9059 | 798678.4034 | 839694.9919
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 281816.4988 | 307491.1853 | 323282.5719
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) x No. of Ckts. | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 2436 |  |  |  | 876960000 | 876960000 | 876960000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 21000 | 1680 |  |  |  | 35280000 | 35280000 | 35280000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 40 |  |  |  | 1240000 | 1240000 | 1240000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 840 |  |  |  | 49560000 | 49560000 | 49560000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 40 |  |  |  | 1800000 | 1800000 | 1800000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 812 |  |  |  | 1055600 | 1055600 | 1055600
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 5040 | 10080 |  |  |  | 50803200 | 50803200 | 50803200
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 1680 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 0 |  |  |  | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 380000 | 100 |  |  |  | 38000000 | 38000000 | 38000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 483113.9979 | 527127.7462 | 554198.6947
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 115410.7813 | 142601.7111 | 160477.2053 | 34623234.3997 | 42780513.3387 | 48143161.6025
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 12823.4201 | 15844.6346 | 17830.8006 | 73093494.8437 | 90314417.0484 | 101635563.383
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 1923.513 | 2376.6952 | 2674.6201 | 9040511.2044 | 11170467.3718 | 12570714.4184
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 1231.0483 | 1521.0849 | 1711.7569 | 66476610.0474 | 82138585.6103 | 92434870.2767
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 1581206184.2118 | 1660931972.6358 | 1711436657.8564
| Survey, Design, Supervision etc. | [5 empty] | 35252314.4079 | 36727241.4938 | 37661578.1703
| TOTAL COST | [5 empty] | 1616458498.6197 | 1697659214.1296 | 1749098236.0267
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 290962529.7515 | 305578658.5433 | 314837682.4848
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 48493754.9586 | 50929776.4239 | 52472947.0808
v) | Contengency at 3% | [5 empty] | 48493754.9586 | 50929776.4239 | 52472947.0808
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 2004408538.2884 | 2105097425.5207 | 2168881812.6732
| TOTAL COST IN RS. LAKHS | [5 empty] | 20044.0854 | 21050.9743 | 21688.8181
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 200.4409 | 210.5097 | 216.8882
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 8515676.9446 | 9047312.8003 | 9377441.1242
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 5009221.7321 | 5321948.706 | 5516141.8378
III | Detailed survey (Rs. Per kM) | 50000 | 100 |  |  |  | 5000000 | 5000000 | 5000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 5009221.7321 | 5321948.706 | 5516141.8378
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 16508.0925 | 18532.0288 | 19750.7674 | 208001965.4743 | 233503562.6456 | 248859669.4525
| b) 'B' Type towers | 60000 | 25 | 22935.8387 | 25336.28 | 26798.9755 | 34403758.1069 | 38004420.0232 | 40198463.2127
| c) 'C' Type towers | 60000 | 25 | 27367.7998 | 30022.8969 | 31649.2306 | 41051699.6895 | 45034345.3439 | 47473845.9071
| d) 'D' Type towers | 60000 | 20 | 30499.6211 | 33278.2668 | 34987.2913 | 36599545.2934 | 39933920.1689 | 41984749.5951
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 533428.2809 | 594127.0803 | 630861.2136 | 32005696.8564 | 35647624.8182 | 37851672.8167
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 12322193.2897 | 13724335.555 | 14572894.0344
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 1218 |  |  |  | 438480000 | 438480000 | 438480000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of suspn.x1) | 24000 | 210 |  |  |  | 5040000 | 5040000 | 5040000
| b) Double 'I' Suspension Insulator Sring (No. Suspn. X 2) | 21000 | 420 |  |  |  | 8820000 | 8820000 | 8820000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'V' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
| f) Single 'I' Suspension Pilot strings (No. of Suspn x 1) | 15000 | 210 |  |  |  | 3150000 | 3150000 | 3150000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 406 |  |  |  | 527800 | 527800 | 527800
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 2700 | 5040 |  |  |  | 13608000 | 13608000 | 13608000
| f) Quad Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 1000 | 840 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190000 | 100 |  |  |  | 19000000 | 19000000 | 19000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 21123759.9252 | 23527432.38 | 24982104.059
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 50354.7034 | 62119.3722 | 69860.8386 | 15106411.0092 | 18635811.6465 | 20958251.5755
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 5594.967 | 6902.1525 | 7762.3154 | 31891312.1305 | 39342269.0315 | 44245197.7704
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 839.2451 | 1035.3229 | 1164.3473 | 3944451.7635 | 4866017.4855 | 5472432.3558
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 537.1168 | 662.6066 | 745.1823 | 29004309.1376 | 35780758.3613 | 40239843.0249
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 1001844346.4263 | 1064389741.2095 | 1103228367.5542
| Survey, Design, Supervision etc. | [5 empty] | 23534120.4089 | 24691210.2124 | 25409724.7998
| TOTAL COST | [5 empty] | 1025378466.8352 | 1089080951.4219 | 1128638092.354
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 184568124.0303 | 196034571.2559 | 203154856.6237
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 30761354.0051 | 32672428.5427 | 33859142.7706
v) | Contengency at 3% | [5 empty] | 30761354.0051 | 32672428.5427 | 33859142.7706
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1271469298.8756 | 1350460379.7632 | 1399511234.5189
| TOTAL COST IN RS. LAKHS | [5 empty] | 12714.693 | 13504.6038 | 13995.1123
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 127.1469 | 135.046 | 139.9511
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 5112135.9979 | 5437165.8013 | 5637373.8804
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 3007138.8223 | 3198332.8243 | 3316102.2826
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 3007138.8223 | 3198332.8243 | 3316102.2826
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 10736.956 | 12057.6633 | 12852.409 | 135285646.115 | 151926557.0846 | 161940353.7345
| b) 'B' Type towers | 60000 | 25 | 17132.487 | 18950.123 | 20054.3624 | 25698730.4451 | 28425184.472 | 30081543.5696
| c) 'C' Type towers | 60000 | 25 | 20389.7437 | 22403.5518 | 23631.9916 | 30584615.5102 | 33605327.7254 | 35447987.415
| d) 'D' Type towers | 60000 | 20 | 25511.93 | 27885.7649 | 29338.4186 | 30614316.0205 | 33462917.8931 | 35206102.353
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 370305.5135 | 412366.6453 | 437793.3118 | 22218330.8091 | 24741998.7175 | 26267598.7072
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 7332049.167 | 8164859.5768 | 8668307.5734
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 609 |  |  |  | 219240000 | 219240000 | 219240000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) | 21000 | 840 |  |  |  | 17640000 | 17640000 | 17640000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 203 |  |  |  | 263900 | 263900 | 263900
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 900 | 5040 |  |  |  | 4536000 | 4536000 | 4536000
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 840 |  |  |  | 420000 | 420000 | 420000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 3360 |  |  |  | 3024000 | 3024000 | 3024000
V | ERECTION
2 | Stringing of Conductor (Route kM) | 95000 | 100 |  |  |  | 9500000 | 9500000 | 9500000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 12569227.1434 | 13996902.1316 | 14859955.8401
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 22408.6745 | 27584.8038 | 30989.6684 | 6722602.3397 | 8275441.1414 | 9296900.5279
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 2489.8527 | 3064.9782 | 3443.2965 | 14192160.4949 | 17470375.7429 | 19626790.0033
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 373.4779 | 459.7467 | 516.4945 | 1755346.1665 | 2160809.6314 | 2427524.0267
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 239.0259 | 294.2379 | 330.5565 | 12907396.4922 | 15888846.9915 | 17850049.0136
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 601427764.4534 | 639666564.8581 | 663220456.5143
| Survey, Design, Supervision etc. | [5 empty] | 17126413.6424 | 17833831.4499 | 18269578.4455
| TOTAL COST | [5 empty] | 618554178.0958 | 657500396.308 | 681490034.9598
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 111339752.0572 | 118350071.3354 | 122668206.2928
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 18556625.3429 | 19725011.8892 | 20444701.0488
v) | Contengency at 3% | [5 empty] | 18556625.3429 | 19725011.8892 | 20444701.0488
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 767007180.8388 | 815300491.4219 | 845047643.3502
| TOTAL COST IN RS. LAKHS | [5 empty] | 7670.0718 | 8153.0049 | 8450.4764
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 76.7007 | 81.53 | 84.5048

## Bersi-Antifog-Hilly
CERC
Capital Cost Benchmarking
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1809937.4823 | 1808476.9262 | 1804879.6267 | 1819794.6044 | 1817803.9384 | 1812824.5591 | 1828887.8166 | 1826462.6293 | 1820342.4429 | 1834635.9616 | 1831953.2463 | 1825157.1846 | 1840565.69 | 1837626.9115 | 1830160.0807 | 1850793.5633 | 1847428.9319 | 1838850.2703
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1809937.4823 | 1808476.9262 | 1804879.6267 | 1819794.6044 | 1817803.9384 | 1812824.5591 | 1828887.8166 | 1826462.6293 | 1820342.4429 | 1834635.9616 | 1831953.2463 | 1825157.1846 | 1840565.69 | 1837626.9115 | 1830160.0807 | 1850793.5633 | 1847428.9319 | 1838850.2703
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 10366.8386 | 11627.9013 | 12386.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 16898.4575 | 18612.4108 | 19653.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 20290.3432 | 22180.6901 | 23333.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 25560.0611 | 27781.5378 | 29139.1942 | 6659322.9597 | 6536132.2035 | 6227995.4502 | 7464184.13 | 7305173.0713 | 6899728.1175 | 8169995.8962 | 7984905.0528 | 7507648.4307 | 8600186.1385 | 8400862.8735 | 7884349.8016 | 9032222.4043 | 8819536.6843 | 8266225.064 | 9751975.6427 | 9518565.7067 | 8908409.2488
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 10224.0244 | 11112.6151 | 11655.6777 | 998898.444 | 980419.8305 | 934199.3175 | 1119627.6195 | 1095775.9607 | 1034959.2176 | 1225499.3844 | 1197735.7579 | 1126147.2646 | 1290027.9208 | 1260129.431 | 1182652.4702 | 1354833.3606 | 1322930.5026 | 1239933.7596 | 1462796.3464 | 1427784.856 | 1336261.3873
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 312978.105 | 307188.3259 | 292706.3646 | 350805.3625 | 343332.0833 | 324276.7838 | 383977.4477 | 375278.4581 | 352848.1188 | 404195.7383 | 394827.8464 | 370552.5134 | 424500.7893 | 414504.8822 | 388500.0731 | 458328.1026 | 447358.1887 | 418681.7583
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 416364.7579 | 408662.4299 | 389396.6149 | 466687.5652 | 456745.6235 | 431395.7507 | 510817.4486 | 499244.9051 | 469405.1092 | 537714.4856 | 525252.0801 | 492957.8301 | 564726.9426 | 551429.0685 | 516834.0413 | 609728.4967 | 595134.8703 | 556985.7
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 12617189.112 | 2915.0868 | 3206.9634 | 625095.1311 | 602181.7881 | 546742.1224 | 785327.2181 | 752223.6441 | 671042.3299 | 940870.0363 | 898722.2087 | 794499.8427 | 1042561.452 | 994795.3641 | 876229.2156 | 1149940.0686 | 1096421.3989 | 963164.3785 | 1340513.4532 | 1277111.9995 | 1118629.534
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 323.8985 | 356.3293 | 1401909.9013 | 1350521.8151 | 1226186.4742 | 1761264.7227 | 1687022.858 | 1504956.3492 | 2110102.8533 | 2015577.31 | 1781836.3007 | 2338167.6636 | 2231041.9668 | 1965131.9486 | 2578987.2419 | 2458960.1463 | 2160102.6973 | 3006388.9309 | 2864197.5727 | 2508766.6526
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 210286.4852 | 48.5848 | 53.4494 | 175344.5645 | 168917.1746 | 153365.8712 | 220291.044 | 211005.2066 | 188233.1492 | 263922.1433 | 252099.3149 | 222864.0442 | 292447.4607 | 279048.6619 | 245789.8367 | 322568.0869 | 307555.6393 | 270175.8982 | 376025.5615 | 358240.9081 | 313785.2124
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 134583.3505 | 31.0943 | 34.2076 | 1533753.6358 | 1477532.716 | 1341504.1589 | 1926904.2679 | 1845680.2678 | 1646491.169 | 2308549.1586 | 2205133.8853 | 1949410.5163 | 2558062.5058 | 2440862.0874 | 2149944.3496 | 2821530.1534 | 2690215.0139 | 2363251.2778 | 3289127.175 | 3133563.3171 | 2744705.6128
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 361987496.4567 | 361695385.2407 | 360975925.3312 | 363958920.8872 | 363560787.6725 | 362564911.8241 | 365777563.3258 | 365292525.8501 | 364068488.5844 | 366927192.3226 | 366390649.2685 | 365031436.9231 | 368113138.0047 | 367525382.2932 | 366032016.1469 | 370158712.6664 | 369485786.3764 | 367770054.0635
| Survey, Design, Supervision etc. | [5 empty] | 6040525.0576 | 6037603.9454 | 6030409.3463 | 6060239.3019 | 6056257.9697 | 6046299.2112 | 6078425.7262 | 6073575.3515 | 6061334.9788 | 6089922.0162 | 6084556.5857 | 6070964.4622 | 6101781.473 | 6095903.9159 | 6080970.2545 | 6122237.2197 | 6115507.9568 | 6098350.6336
| TOTAL COST | [5 empty] | 368028021.5142 | 367732989.1861 | 367006334.6775 | 370019160.1891 | 369617045.6422 | 368611211.0353 | 371855989.0521 | 371366101.2016 | 370129823.5632 | 373017114.3388 | 372475205.8541 | 371102401.3853 | 374214919.4777 | 373621286.2091 | 372112986.4014 | 376280949.886 | 375601294.3332 | 373868404.6972
| TOTAL COST IN RS. LAKHS | [5 empty] | 3680.2802 | 3677.3299 | 3670.0633 | 3700.1916 | 3696.1705 | 3686.1121 | 3718.5599 | 3713.661 | 3701.2982 | 3730.1711 | 3724.7521 | 3711.024 | 3742.1492 | 3736.2129 | 3721.1299 | 3762.8095 | 3756.0129 | 3738.684
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 36.8028 | 36.7733 | 36.7006 | 37.0019 | 36.9617 | 36.8611 | 37.1856 | 37.1366 | 37.013 | 37.3017 | 37.2475 | 37.1102 | 37.4215 | 37.3621 | 37.2113 | 37.6281 | 37.5601 | 37.3868
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2560107.9014 | 2558171.805 | 2553440.9687 | 2573123.4787 | 2570466.4627 | 2563871.3997 | 2585203.0866 | 2581949.8981 | 2573802.003 | 2592868.2652 | 2589259.8977 | 2580187.0442 | 2600796.082 | 2596833.3971 | 2586839.4408 | 2614513.2218 | 2609959.1116 | 2598432.5284
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2560107.9014 | 2558171.805 | 2553440.9687 | 2573123.4787 | 2570466.4627 | 2563871.3997 | 2585203.0866 | 2581949.8981 | 2573802.003 | 2592868.2652 | 2589259.8977 | 2580187.0442 | 2600796.082 | 2596833.3971 | 2586839.4408 | 2614513.2218 | 2609959.1116 | 2598432.5284
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 39.6672 | 47.4027 | 52.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5.9501 | 7.1104 | 7.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4760.065 | 5688.3225 | 6294.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8004058.2809 | 7854875.4913 | 7484090.7527 | 8971864.7131 | 8778977.332 | 8290009.9376 | 9821691.9756 | 9596985.7401 | 9020760.9936 | 10339942.8136 | 10097881.3234 | 9473976.3061 | 10860547.7226 | 10602199.8115 | 9933622.9023 | 11728018.4514 | 11444427.8991 | 10706897.2347
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1200608.7421 | 1178231.3237 | 1122613.6129 | 1345779.707 | 1316846.5998 | 1243501.4906 | 1473253.7963 | 1439547.861 | 1353114.149 | 1550991.422 | 1514682.1985 | 1421096.4459 | 1629082.1584 | 1590329.9717 | 1490043.4353 | 1759202.7677 | 1716664.1849 | 1606034.5852
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 376178.6308 | 369167.2654 | 351740.9436 | 421664.0691 | 412598.654 | 389617.9261 | 461604.6648 | 451043.8117 | 423962.1203 | 485961.6702 | 474585.1464 | 445262.5544 | 510429.3134 | 498287.3524 | 466865.2491 | 551199.1253 | 537870.7984 | 503207.9729
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1827 |  |  |  | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'v'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 609 |  |  |  | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 288 |  |  |  | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 500442.4336 | 491114.9905 | 467932.1987 | 560953.1632 | 548893.1523 | 518321.1569 | 614087.4119 | 600037.9721 | 564010.3341 | 646490.3133 | 631355.7606 | 592346.9811 | 679040.3995 | 662887.5615 | 621085.735 | 733277.781 | 715546.6825 | 669433.6199
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 18227325.1949 | 154.5809 | 171.1442 | 903038.8727 | 869690.1911 | 789521.6642 | 1134622.5053 | 1086360.125 | 968715.0866 | 1359748.476 | 1298242.015 | 1147023.4945 | 1507031.1695 | 1437296.8894 | 1265174.8484 | 1662606.2841 | 1584447.7812 | 1390917.2713 | 1938809.9606 | 1846180.3998 | 1615895.3446
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17.1757 | 19.016 | 2025258.355 | 1950466.7837 | 1770671.6678 | 2544634.3207 | 2436395.5817 | 2172551.3507 | 3049527.595 | 2911586.1643 | 2572446.1988 | 3379840.624 | 3223446.5445 | 2837425.951 | 3728751.1862 | 3553463.98 | 3119430.3035 | 4348197.1705 | 4140455.5133 | 3623991.8858
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 303788.7532 | 2.5763 | 2.8524 | 253310.1763 | 243955.5841 | 221467.6223 | 318271.3785 | 304733.3654 | 271732.9196 | 381421.151 | 364168.0593 | 321749.9627 | 422735.2141 | 403174.1484 | 354892.4344 | 466375.3728 | 444451.2401 | 390164.2663 | 543852.8814 | 517869.4923 | 453272.5523
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 194424.8021 | 1.6489 | 1.8255 | 2215725.3918 | 2133899.9876 | 1937195.8966 | 2783946.4844 | 2665528.3468 | 2376870.6748 | 3336322.8492 | 3185408.6066 | 2814373.9527 | 3697700.4304 | 3526598.1449 | 3104273.937 | 4079424.5646 | 3887652.3333 | 3412799.6136 | 4757126.8404 | 4529847.9535 | 3964813.0922
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 512021580.2736 | 511634361.0076 | 510688193.7491 | 514624695.7315 | 514093292.5472 | 512774279.9331 | 517040617.3101 | 516389979.6202 | 514760400.596 | 518573653.0474 | 517851979.5463 | 516037408.8485 | 520159216.3919 | 519366679.4218 | 517367888.1667 | 522902644.3685 | 521991822.3139 | 519686505.6777
| Survey, Design, Supervision etc. | [5 empty] | 7540865.8957 | 7536993.7031 | 7527532.0305 | 7566897.0503 | 7561583.0185 | 7548392.8923 | 7591056.2661 | 7584549.8892 | 7568254.0989 | 7606386.6235 | 7599169.8885 | 7581024.1815 | 7622242.2569 | 7614316.8872 | 7594328.9747 | 7649676.5367 | 7640568.3161 | 7617515.1498
| TOTAL COST | [5 empty] | 519562446.1693 | 519171354.7107 | 518215725.7795 | 522191592.7818 | 521654875.5656 | 520322672.8254 | 524631673.5762 | 523974529.5094 | 522328654.6949 | 526180039.6708 | 525451149.4347 | 523618433.03 | 527781458.6488 | 526980996.309 | 524962217.1413 | 530552320.9052 | 529632390.63 | 527304020.8275
| TOTAL COST IN RS. LAKHS | [5 empty] | 5195.6245 | 5191.7135 | 5182.1573 | 5221.9159 | 5216.5488 | 5203.2267 | 5246.3167 | 5239.7453 | 5223.2865 | 5261.8004 | 5254.5115 | 5236.1843 | 5277.8146 | 5269.81 | 5249.6222 | 5305.5232 | 5296.3239 | 5273.0402
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 51.9562 | 51.9171 | 51.8216 | 52.2192 | 52.1655 | 52.0323 | 52.4632 | 52.3975 | 52.2329 | 52.618 | 52.5451 | 52.3618 | 52.7781 | 52.6981 | 52.4962 | 53.0552 | 52.9632 | 52.7304
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 3343025.9534 | 3340710.7629 | 3335082.1524 | 3358585.7713 | 3355387.6516 | 3347489.6434 | 3373110.5468 | 3369175.5705 | 3359369.6078 | 3382362.2247 | 3377985.8399 | 3367036.8976 | 3391955.8746 | 3387137.6239 | 3375046.3091 | 3408608.3723 | 3403049.6896 | 3389049.7261
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 3343025.9534 | 3340710.7629 | 3335082.1524 | 3358585.7713 | 3355387.6516 | 3347489.6434 | 3373110.5468 | 3369175.5705 | 3359369.6078 | 3382362.2247 | 3377985.8399 | 3367036.8976 | 3391955.8746 | 3387137.6239 | 3375046.3091 | 3408608.3723 | 3403049.6896 | 3389049.7261
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 4795.5834 | 6031.7 | 6844.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8543101.1457 | 8383241.0339 | 7987245.1339 | 9576321.4822 | 9369445.649 | 8846615.7148 | 10484222.4281 | 10243118.0431 | 9626620.6551 | 11038048.1566 | 10778279.3545 | 10110610.1655 | 11594462.7805 | 11317183.5237 | 10601584.2045 | 12521695.6098 | 12217285.8025 | 11427733.5408
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1281465.1719 | 1257486.1551 | 1198086.7701 | 1436448.2223 | 1405416.8474 | 1326992.3572 | 1572633.3642 | 1536467.7065 | 1443993.0983 | 1655707.2235 | 1616741.9032 | 1516591.5248 | 1739169.4171 | 1697577.5286 | 1590237.6307 | 1878254.3415 | 1832592.8704 | 1714160.0311
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 401512.83 | 393999.6466 | 375388.4384 | 450072.6228 | 440349.7716 | 415777.5556 | 492742.5938 | 481411.0525 | 452436.6079 | 518771.5653 | 506562.8245 | 475183.3827 | 544922.2108 | 531890.5052 | 498258.4198 | 588500.7511 | 574193.9507 | 537086.1888
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 2436 |  |  |  | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 2304 |  |  |  | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039 | 2309188.5039
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 812 |  |  |  | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 384 |  |  |  | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 534145.327 | 524150.2995 | 499391.2154 | 598745.9686 | 585811.3494 | 553122.1466 | 655511.1923 | 640436.4813 | 601890.8533 | 690138.3633 | 673896.6861 | 632151.6135 | 724927.4015 | 707590.9077 | 662849.0715 | 782901.3238 | 763868.5308 | 714502.8913
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 23837461.2777 | 85.5822 | 93.9493 | 1180982.6144 | 1137198.5941 | 1032301.206 | 1483917.7925 | 1420496.6059 | 1266387.8433 | 1778626.9158 | 1697761.8213 | 1499547.1463 | 1971500.8869 | 1879798.4147 | 1654120.4813 | 2175272.4996 | 2072474.1635 | 1818670.1642 | 2537106.4679 | 2415248.8 | 2113161.1551
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 9.5091 | 10.4388 | 2648606.8086 | 2550411.7524 | 2315156.8614 | 3328003.9188 | 3185768.3054 | 2840146.3523 | 3988952.3366 | 3807595.0185 | 3363056.097 | 4421513.5845 | 4215851.1222 | 3709719.9534 | 4878515.1306 | 4647967.8137 | 4078757.9097 | 5690005.4102 | 5416713.454 | 4739217.1189
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 397291.0213 | 1.4264 | 1.5658 | 331275.7881 | 318993.9936 | 289569.3734 | 416251.713 | 398461.5243 | 355232.6899 | 498920.1586 | 476236.8036 | 420635.8812 | 553022.9676 | 527299.6349 | 463995.0321 | 610182.6588 | 581346.8408 | 510152.6345 | 711680.2013 | 677498.0766 | 592759.8921
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 254266.2536 | 0.91288 | 1.0021 | 2897697.1478 | 2790267.2592 | 2532887.6344 | 3640988.7009 | 3485376.4258 | 3107250.1805 | 4364096.5397 | 4165683.328 | 3679337.3892 | 4837338.355 | 4612334.2024 | 4058603.5244 | 5337318.9759 | 5085089.6528 | 4462347.9495 | 6225126.5058 | 5926132.5898 | 5184920.5716
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 668605190.6734 | 668142152.5742 | 667016430.4727 | 671717154.2609 | 671077530.3187 | 669497928.6803 | 674622109.369 | 673835114.0946 | 671873921.5681 | 676472444.9426 | 675597167.9824 | 673407379.5176 | 678391174.9148 | 677427524.7758 | 675009261.8242 | 681721674.4512 | 680609937.9146 | 677809945.2298
| Survey, Design, Supervision etc. | [5 empty] | 9106701.9997 | 9102071.6187 | 9090814.3977 | 9137821.6356 | 9131425.3962 | 9115629.3798 | 9166871.1867 | 9159001.2339 | 9139389.3087 | 9185374.5424 | 9176621.7728 | 9154723.8882 | 9204561.8421 | 9194925.3407 | 9170742.7112 | 9237866.8375 | 9226749.4721 | 9198749.5453
| TOTAL COST | [5 empty] | 677711892.6732 | 677244224.1929 | 676107244.8705 | 680854975.8965 | 680208955.7148 | 678613558.06 | 683788980.5557 | 682994115.3285 | 681013310.8768 | 685657819.485 | 684773789.7552 | 682562103.4058 | 687595736.757 | 686622450.1166 | 684180004.5354 | 690959541.2887 | 689836687.3867 | 687008694.775
| TOTAL COST IN RS. LAKHS | [5 empty] | 6777.1189 | 6772.4422 | 6761.0724 | 6808.5498 | 6802.0896 | 6786.1356 | 6837.8898 | 6829.9412 | 6810.1331 | 6856.5782 | 6847.7379 | 6825.621 | 6875.9574 | 6866.2245 | 6841.8 | 6909.5954 | 6898.3669 | 6870.0869
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 67.7712 | 67.7244 | 67.6107 | 68.0855 | 68.0209 | 67.8614 | 68.3789 | 68.2994 | 68.1013 | 68.5658 | 68.4774 | 68.2562 | 68.7596 | 68.6622 | 68.418 | 69.096 | 68.9837 | 68.7009
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1036309.5431 | 1035468.93 | 1033888.187 | 1040464.2058 | 1039316.7496 | 1037120.2657 | 1044288.5385 | 1042891.6377 | 1040189.0078 | 1046700.4676 | 1045156.9397 | 1042156.4346 | 1049183.5609 | 1047495.1738 | 1044200.8107 | 1053454.0155 | 1051526.6761 | 1047749.222
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1036309.5431 | 1035468.93 | 1033888.187 | 1040464.2058 | 1039316.7496 | 1037120.2657 | 1044288.5385 | 1042891.6377 | 1040189.0078 | 1046700.4676 | 1045156.9397 | 1042156.4346 | 1049183.5609 | 1047495.1738 | 1044200.8107 | 1053454.0155 | 1051526.6761 | 1047749.222
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 12.9621 | 15.239 | 16.7289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 1.9443 | 2.2858 | 2.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 1555.4579 | 1828.6799 | 2007.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 3284960.7387 | 3205197.7366 | 3053017.5594 | 3668181.2522 | 3564092.7577 | 3361150.7555 | 4006235.1596 | 3884277.7708 | 3643334.0973 | 4212934.4634 | 4081209.1455 | 3819398.7606 | 4420902.8243 | 4280011.3345 | 3998625.6635 | 4768023.3781 | 4612943.0683 | 4301350.1076
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 492744.1108 | 480779.6605 | 457952.6339 | 550227.1878 | 534613.9137 | 504172.6133 | 600935.2739 | 582641.6656 | 546500.1146 | 631940.1695 | 612181.3718 | 572909.8141 | 663135.4236 | 642001.7002 | 599793.8495 | 715203.5067 | 691941.4602 | 645202.5161
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 154388.1853 | 150639.4449 | 143487.2068 | 172398.9697 | 167506.9679 | 157969.0008 | 188286.992 | 182555.1792 | 171231.191 | 198001.5465 | 191810.6559 | 179505.9638 | 207775.7449 | 201154.058 | 187929.3572 | 224089.8858 | 216801.3459 | 202156.9481
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 609 |  |  |  | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 1152 |  |  |  | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 96 |  |  |  | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 205387.5283 | 200400.4593 | 190885.6087 | 229347.8494 | 222839.8633 | 210151.2014 | 250484.1922 | 242858.9788 | 227794.3161 | 263407.7741 | 255171.8347 | 238802.5104 | 276410.702 | 267601.6607 | 250008.4192 | 298113.9241 | 288417.7469 | 268935.8373
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 4762940.9133 | 0 | 0 | 235971.0351 | 224650.8084 | 203824.758 | 294238.7757 | 277777.0284 | 247044.0026 | 350970.979 | 329927.7838 | 290266.1065 | 388121.5325 | 364230.268 | 318998.2765 | 427385.9772 | 400578.9919 | 349638.9674 | 497135.8507 | 465323.0011 | 404583.2676
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 529215.657 | 503827.6207 | 457120.7358 | 659893.5624 | 622974.5634 | 554049.1615 | 787127.6964 | 739933.8178 | 650983.9999 | 870445.7805 | 816864.4957 | 715422.0535 | 958504.7191 | 898384.305 | 784140.3747 | 1114933.7705 | 1043586.6319 | 907364.7521
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 79382.3486 | 0 | 0 | 66191.9064 | 63016.4853 | 57174.5989 | 82536.5091 | 77918.8473 | 69297.969 | 98450.3805 | 92547.5831 | 81422.1412 | 108871.4305 | 102169.7251 | 89481.7622 | 119885.4451 | 112365.855 | 98076.7397 | 139450.885 | 130527.1069 | 113489.0888
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 50804.7031 | 0 | 0 | 578986.1655 | 551210.4911 | 500111.0199 | 721953.7787 | 681562.703 | 606155.1566 | 861153.7482 | 809521.4837 | 712206.3092 | 952307.548 | 893687.1685 | 782704.4909 | 1048648.0597 | 982873.5733 | 857885.4814 | 1219788.6059 | 1141731.5688 | 992698.5937
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 207261908.6114 | 207093785.9912 | 206777637.4059 | 208092841.1694 | 207863349.9291 | 207424053.1452 | 208857707.7062 | 208578327.5473 | 208037801.5602 | 209340093.5294 | 209031387.9495 | 208431286.9164 | 209836712.1804 | 209499034.763 | 208840162.1371 | 210690803.0913 | 210305335.2143 | 209549844.3958
| Survey, Design, Supervision etc. | [5 empty] | 4493269.1791 | 4491587.9529 | 4488426.467 | 4501578.5047 | 4499283.5923 | 4494890.6244 | 4509227.1701 | 4506433.3685 | 4501028.1086 | 4514051.0283 | 4510963.9725 | 4504962.9622 | 4519017.2148 | 4515640.4406 | 4509051.7144 | 4527558.1239 | 4523703.4451 | 4516148.5369
| TOTAL COST | [5 empty] | 211755177.7905 | 211585373.9441 | 211266063.8729 | 212594419.6741 | 212362633.5213 | 211918943.7696 | 213366934.8763 | 213084760.9157 | 212538829.6687 | 213854144.5577 | 213542351.922 | 212936249.8786 | 214355729.3952 | 214014675.2036 | 213349213.8514 | 215218361.2152 | 214829038.6594 | 214065992.9328
| TOTAL COST IN RS. LAKHS | [5 empty] | 2117.5518 | 2115.8537 | 2112.6606 | 2125.9442 | 2123.6263 | 2119.1894 | 2133.6693 | 2130.8476 | 2125.3883 | 2138.5414 | 2135.4235 | 2129.3625 | 2143.5573 | 2140.1468 | 2133.4921 | 2152.1836 | 2148.2904 | 2140.6599
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 21.1755 | 21.1585 | 21.1266 | 21.2594 | 21.2363 | 21.1919 | 21.3367 | 21.3085 | 21.2539 | 21.3854 | 21.3542 | 21.2936 | 21.4356 | 21.4015 | 21.3349 | 21.5218 | 21.4829 | 21.4066
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1409720.7215 | 1408635.0524 | 1406622.4855 | 1415037.4868 | 1413544.3505 | 1410725.0189 | 1419964.1141 | 1418136.7486 | 1414647.8757 | 1423083.9634 | 1421059.1117 | 1417174.0521 | 1426304.618 | 1424084.0253 | 1419806.8016 | 1431861.569 | 1429316.9039 | 1424392.5468
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1409720.7215 | 1408635.0524 | 1406622.4855 | 1415037.4868 | 1413544.3505 | 1410725.0189 | 1419964.1141 | 1418136.7486 | 1414647.8757 | 1423083.9634 | 1421059.1117 | 1417174.0521 | 1426304.618 | 1424084.0253 | 1419806.8016 | 1431861.569 | 1429316.9039 | 1424392.5468
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 26.1911 | 31.6347 | 35.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3.9287 | 4.7452 | 5.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 3142.9283 | 3796.1589 | 4225.0539 | 3895809.9723 | 3799959.9029 | 3619397.6448 | 4350752.1776 | 4225299.6474 | 3983546.6946 | 4753028.6402 | 4605821.3787 | 4318183.3507 | 4999254.8728 | 4840163.5204 | 4527336.8503 | 5247120.5665 | 5076885.5687 | 4740445.1778 | 5661015.23 | 5473548.73 | 5100712.1952
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 1257.1713 | 1518.4636 | 1690.0215 | 584371.4958 | 569993.9854 | 542909.6467 | 652612.8266 | 633794.9471 | 597532.0042 | 712954.296 | 690873.2068 | 647727.5026 | 749888.2309 | 726024.5281 | 679100.5275 | 787068.085 | 761532.8353 | 711066.7767 | 849152.2845 | 821032.3095 | 765106.8293
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 183097.1752 | 178592.3669 | 170106.214 | 204478.7706 | 198582.6915 | 187220.6684 | 223385.1558 | 216466.6372 | 202948.085 | 234957.4163 | 227480.3634 | 212777.9831 | 246606.7289 | 238605.9415 | 222793.7521 | 266059.152 | 257248.51 | 239725.7569
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 913.5 |  |  |  | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'v'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 1152 |  |  |  | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 144 |  |  |  | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 243580.0134 | 237587.1233 | 226297.7232 | 272024.6319 | 264180.8898 | 249065.628 | 297176.3993 | 287972.4733 | 269988.3121 | 312571.3466 | 302624.3846 | 283065.3391 | 328068.7988 | 317425.0961 | 296389.6361 | 353946.9778 | 342225.8998 | 318914.8223
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 6699005.8521 | 21028.6958 | 23851.7409 | 331889.766 | 315759.4515 | 286464.5792 | 413930.1143 | 390403.1902 | 347006.9359 | 494013.928 | 463887.3328 | 407756.1201 | 546523.5594 | 512292.9735 | 448212.4838 | 602060.892 | 563628.6754 | 491401.6245 | 700788.518 | 655143.3072 | 568931.4866
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 2336.5218 | 2650.1934 | 744333.9836 | 708158.2937 | 642458.2594 | 928327.0607 | 875562.8872 | 778237.4796 | 1107932.1892 | 1040366.8379 | 914480.5544 | 1225696.2998 | 1148926.8691 | 1005212.6272 | 1350250.6798 | 1264058.191 | 1102073.5382 | 1571668.556 | 1469299.3809 | 1275950.8826
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 111650.0975 | 350.4783 | 397.529 | 93097.9359 | 88573.2439 | 80355.7801 | 116110.9598 | 109511.4551 | 97338.4322 | 138575.1588 | 130124.3896 | 114379.1013 | 153304.5624 | 143702.5884 | 125727.4595 | 168883.2622 | 158102.6946 | 137842.3852 | 196577.211 | 183773.3365 | 159590.1788
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 71456.0624 | 224.3061 | 254.4186 | 814335.4665 | 774757.605 | 702878.7587 | 1015632.3193 | 957905.8971 | 851427.4438 | 1212128.5554 | 1138208.9668 | 1000483.6073 | 1340967.8856 | 1256978.6126 | 1099748.6502 | 1477236.0816 | 1382937.5515 | 1205718.9228 | 1719477.3785 | 1607480.8127 | 1395948.7007
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 281944144.3097 | 281727010.4734 | 281324497.1068 | 283007497.3619 | 282708870.1061 | 282145003.7877 | 283992822.8237 | 283627349.724 | 282929575.1343 | 284616792.6747 | 284211822.3409 | 283434810.4216 | 285260923.5958 | 284816805.055 | 283961360.3141 | 286372313.8085 | 285863380.7876 | 284878509.3532
| Survey, Design, Supervision etc. | [5 empty] | 5240091.5361 | 5237920.1977 | 5233895.0641 | 5250725.0666 | 5247738.794 | 5242100.1309 | 5260578.3212 | 5256923.5902 | 5249945.8443 | 5266818.0197 | 5262768.3164 | 5254998.1972 | 5273259.3289 | 5268818.1435 | 5260263.6961 | 5284373.2311 | 5279283.9009 | 5269435.1865
| TOTAL COST | [5 empty] | 287184235.8458 | 286964930.6711 | 286558392.1709 | 288258222.4285 | 287956608.9002 | 287387103.9185 | 289253401.1449 | 288884273.3142 | 288179520.9786 | 289883610.6944 | 289474590.6573 | 288689808.6188 | 290534182.9247 | 290085623.1986 | 289221624.0103 | 291656687.0396 | 291142664.6884 | 290147944.5398
| TOTAL COST IN RS. LAKHS | [5 empty] | 2871.8424 | 2869.6493 | 2865.5839 | 2882.5822 | 2879.5661 | 2873.871 | 2892.534 | 2888.8427 | 2881.7952 | 2898.8361 | 2894.7459 | 2886.8981 | 2905.3418 | 2900.8562 | 2892.2162 | 2916.5669 | 2911.4266 | 2901.4794
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 28.7184 | 28.6965 | 28.6558 | 28.8258 | 28.7957 | 28.7387 | 28.9253 | 28.8884 | 28.818 | 28.9884 | 28.9475 | 28.869 | 29.0534 | 29.0086 | 28.9222 | 29.1657 | 29.1143 | 29.0148
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1820427.1685 | 1819111.1054 | 1816691.2217 | 1826843.9467 | 1825024.8209 | 1821616.764 | 1832816.6626 | 1830582.2347 | 1826348.555 | 1836609.6752 | 1834128.9205 | 1829404.7502 | 1840532.7274 | 1837807.2325 | 1832596.3284 | 1847317.2068 | 1844185.4077 | 1838169.0314
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1820427.1685 | 1819111.1054 | 1816691.2217 | 1826843.9467 | 1825024.8209 | 1821616.764 | 1832816.6626 | 1830582.2347 | 1826348.555 | 1836609.6752 | 1834128.9205 | 1829404.7502 | 1840532.7274 | 1837807.2325 | 1832596.3284 | 1847317.2068 | 1844185.4077 | 1838169.0314
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 6.3189 | 7.4431 | 8.1777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5055.1374 | 5954.461 | 6542.1879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 4423087.5671 | 4313478.6421 | 4108425.7817 | 4939892.238 | 4796202.3555 | 4521056.7497 | 5397466.2904 | 5228725.2122 | 4900972.5112 | 5677700.3949 | 5495279.5851 | 5138652.6464 | 5959879.7553 | 5764636.7737 | 5380951.0098 | 6431184.9557 | 6216126.4182 | 5790761.353
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 663463.1351 | 647021.7963 | 616263.8673 | 740983.8357 | 719430.3533 | 678158.5125 | 809619.9436 | 784308.7818 | 735145.8767 | 851655.0592 | 824291.9378 | 770797.897 | 893981.9633 | 864695.5161 | 807142.6515 | 964677.7434 | 932418.9627 | 868614.2029
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 207878.4245 | 202726.9708 | 193089.7966 | 232167.4622 | 225414.2551 | 212482.8279 | 253672.7505 | 245742.1751 | 230338.2939 | 266843.3295 | 258269.8274 | 241508.9007 | 280105.3325 | 270929.2078 | 252896.5573 | 302255.964 | 292148.538 | 272157.0235
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 887.4291 | 2024 |  |  |  | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566 | 1796156.5566
| Insulators 160 kN | 1002.252 | 1152 |  |  |  | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519 | 1154594.2519
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 276547.3 | 269694.1568 | 256873.5165 | 308859.7817 | 299875.7749 | 282672.6847 | 337468.9528 | 326918.6553 | 306426.3808 | 354990.1941 | 343584.5908 | 321286.9954 | 372633.0599 | 360425.7684 | 336436.3582 | 402100.7516 | 388654.5204 | 362059.1708
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 8635070.7908 | 161099.2384 | 176969.7293 | 427808.4968 | 406868.0945 | 369104.4004 | 533621.453 | 503029.352 | 446969.8693 | 637056.877 | 597846.8818 | 525246.1337 | 704925.5863 | 660355.679 | 577426.6912 | 776735.8069 | 726678.3589 | 633164.2815 | 904441.1852 | 844963.6134 | 733279.7057
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17899.9154 | 19663.3033 | 959452.3101 | 912488.9666 | 827795.7829 | 1196760.559 | 1128151.211 | 1002425.7976 | 1428736.682 | 1340799.8581 | 1177977.109 | 1580946.8191 | 1480989.2426 | 1295003.2008 | 1741996.6405 | 1629732.077 | 1420006.7017 | 2028403.3414 | 1895012.1299 | 1644537.013
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 143917.8465 | 2684.9873 | 2949.4955 | 120003.9655 | 114130.0024 | 103536.9612 | 149685.4105 | 141104.0628 | 125378.8954 | 178699.9372 | 167701.1961 | 147336.0613 | 197737.6943 | 185235.4517 | 161973.1568 | 217881.0792 | 203839.5342 | 177608.0306 | 253703.537 | 237019.5662 | 205691.2688
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 92107.4218 | 1718.3919 | 1887.6771 | 1049684.7676 | 998304.719 | 905646.4974 | 1309310.86 | 1234249.0912 | 1096699.7311 | 1563103.3625 | 1466896.4498 | 1288760.9054 | 1729628.2232 | 1620270.0568 | 1416792.8094 | 1905824.1035 | 1783001.5296 | 1553552.3642 | 2219166.151 | 2073230.0567 | 1799198.8077
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 364085433.7008 | 363822221.0827 | 363338244.338 | 365368789.3343 | 365004964.1898 | 364323352.8023 | 366563332.53 | 366116446.9442 | 365269711.0061 | 367321935.0348 | 366825784.1053 | 365880950.0318 | 368106545.4753 | 367561446.4996 | 366519265.6888 | 369463441.3634 | 368837081.5397 | 367633806.2794
| Survey, Design, Supervision etc. | [5 empty] | 6061504.43 | 6058872.3038 | 6054032.5364 | 6074337.9863 | 6070699.7349 | 6063883.621 | 6086283.4183 | 6081814.5624 | 6073347.203 | 6093869.4433 | 6088907.934 | 6079459.5933 | 6101715.5477 | 6096264.558 | 6085842.7499 | 6115284.5066 | 6109020.9084 | 6096988.1558
| TOTAL COST | [5 empty] | 370146938.1308 | 369881093.3865 | 369392276.8744 | 371443127.3206 | 371075663.9247 | 370387236.4233 | 372649615.9482 | 372198261.5066 | 371343058.2091 | 373415804.4781 | 372914692.0393 | 371960409.6251 | 374208261.023 | 373657711.0576 | 372605108.4386 | 375578725.87 | 374946102.4481 | 373730794.4352
| TOTAL COST IN RS. LAKHS | [5 empty] | 3701.4694 | 3698.8109 | 3693.9228 | 3714.4313 | 3710.7566 | 3703.8724 | 3726.4962 | 3721.9826 | 3713.4306 | 3734.158 | 3729.1469 | 3719.6041 | 3742.0826 | 3736.5771 | 3726.0511 | 3755.7873 | 3749.461 | 3737.3079
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 37.0147 | 36.9881 | 36.9392 | 37.1443 | 37.1076 | 37.0387 | 37.265 | 37.2198 | 37.1343 | 37.3416 | 37.2915 | 37.196 | 37.4208 | 37.3658 | 37.2605 | 37.5579 | 37.4946 | 37.3731
ESTIMATE FOR A 765 KV, SC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1083493.5078 | 1082062.7066 | 1079390.466 | 1090864.2053 | 1088921.7363 | 1085237.282 | 1097615.0477 | 1095259.0421 | 1090748.7783 | 1101860.4426 | 1099262.0605 | 1094267.4337 | 1106223.1937 | 1103385.7479 | 1097914.0828 | 1113710.9401 | 1110479.8131 | 1104225.0678
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1083493.5078 | 1082062.7066 | 1079390.466 | 1090864.2053 | 1088921.7363 | 1085237.282 | 1097615.0477 | 1095259.0421 | 1090748.7783 | 1101860.4426 | 1099262.0605 | 1094267.4337 | 1106223.1937 | 1103385.7479 | 1097914.0828 | 1113710.9401 | 1110479.8131 | 1104225.0678
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 33.1275 | 39.4561 | 43.6035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 4.9691 | 5.9184 | 6.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 3975.2993 | 4734.735 | 5232.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 5969732.8625 | 5828889.6017 | 5562345.1813 | 6676005.8618 | 6492879.3319 | 6139682.5939 | 7297034.6461 | 7082922.0989 | 6665181.5049 | 7676164.6287 | 7445119.1126 | 6991980.1598 | 8057306.2644 | 7810366.8671 | 7324017.3222 | 8692976.3697 | 8421417.8379 | 7883774.6479
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 895459.9294 | 874333.4403 | 834351.7772 | 1001400.8793 | 973931.8998 | 920952.3891 | 1094555.1969 | 1062438.3148 | 999777.2257 | 1151424.6943 | 1116767.8669 | 1048797.024 | 1208595.9397 | 1171555.0301 | 1098602.5983 | 1303946.4555 | 1263212.6757 | 1182566.1972
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 280568.4137 | 273948.9935 | 261421.8089 | 313762.1762 | 305155.5063 | 288555.7939 | 342949.5896 | 332886.6238 | 313253.4478 | 360768.1252 | 349909.3355 | 328612.4902 | 378681.2055 | 367075.4274 | 344217.7345 | 408556.7388 | 395793.8987 | 370525.4821
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 609 |  |  |  | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 1920 |  |  |  | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 373249.1115 | 364443.0857 | 347777.7724 | 417407.8328 | 405958.1053 | 383874.9783 | 456236.78 | 442849.6955 | 416731.0552 | 479941.3464 | 465495.552 | 437163.6793 | 503771.6886 | 488332.1517 | 457923.8337 | 543516.0636 | 526537.2502 | 492921.8695
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 9942759.5821 | 0 | 0 | 410496.2517 | 391355.1568 | 356381.6002 | 513372.7584 | 485594.8413 | 434201.4211 | 613327.1889 | 577862.2596 | 511709.3612 | 678715.8036 | 638473.2428 | 563118.4743 | 747789.1243 | 702655.2068 | 617871.4476 | 870435.1072 | 816901.7618 | 715925.4555
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1104751.0647 | 1053237.4518 | 959114.6097 | 1381618.2222 | 1306860.6977 | 1168547.7766 | 1650621.3203 | 1555176.0677 | 1377141.592 | 1826598.9117 | 1718295.8233 | 1515496.7467 | 2012492.9956 | 1891026.0073 | 1662851.0899 | 2342564.9015 | 2198492.8909 | 1926739.6619
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 165712.6597 | 0 | 0 | 92118.1854 | 87822.7919 | 79974.485 | 115204.3819 | 108970.826 | 97437.7886 | 137634.8443 | 129676.27 | 114831.1041 | 152308.4997 | 143277.792 | 126367.6631 | 167809.0285 | 157680.6666 | 138654.6073 | 195331.6316 | 183318.3802 | 160658.6018
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 106056.1022 | 0 | 0 | 725188.9557 | 691374.0047 | 629589.1847 | 906932.1657 | 857859.2724 | 767066.8704 | 1083513.1911 | 1020860.3046 | 903993.5826 | 1199029.7177 | 1127936.5945 | 994813.708 | 1321055.7024 | 1241321.4336 | 1091541.1479 | 1537723.9713 | 1443151.1447 | 1264764.8578
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 216698701.5616 | 216412541.3135 | 215878093.2067 | 218172841.0654 | 217784347.2679 | 217047456.3991 | 219523009.5445 | 219051808.422 | 218149755.6606 | 220372088.5144 | 219852412.1067 | 218853486.7325 | 221244638.7361 | 220677149.5778 | 219582816.5685 | 222742188.0263 | 222095962.6271 | 220845013.5608
| Survey, Design, Supervision etc. | [5 empty] | 4587637.1086 | 4584775.5061 | 4579431.0251 | 4602378.5036 | 4598493.5657 | 4591124.657 | 4615880.1884 | 4611168.1772 | 4602147.6496 | 4624370.9781 | 4619174.2141 | 4609184.9603 | 4633096.4803 | 4627421.5888 | 4616478.2587 | 4648071.9733 | 4641609.7193 | 4629100.2286
| TOTAL COST | [5 empty] | 221286338.6702 | 220997316.8197 | 220457524.2317 | 222775219.5691 | 222382840.8336 | 221638581.056 | 224138889.7329 | 223662976.5992 | 222751903.3102 | 224996459.4926 | 224471586.3207 | 223462671.6928 | 225877735.2165 | 225304571.1666 | 224199294.8272 | 227390259.9995 | 226737572.3464 | 225474113.7894
| TOTAL COST IN RS. LAKHS | [5 empty] | 2212.8634 | 2209.9732 | 2204.5752 | 2227.7522 | 2223.8284 | 2216.3858 | 2241.3889 | 2236.6298 | 2227.519 | 2249.9646 | 2244.7159 | 2234.6267 | 2258.7774 | 2253.0457 | 2241.9929 | 2273.9026 | 2267.3757 | 2254.7411
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 22.1286 | 22.0997 | 22.0458 | 22.2775 | 22.2383 | 22.1639 | 22.4139 | 22.3663 | 22.2752 | 22.4996 | 22.4472 | 22.3463 | 22.5878 | 22.5305 | 22.4199 | 22.739 | 22.6738 | 22.5474
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1461759.2405 | 1459907.2887 | 1456519.69 | 1471146.1004 | 1468613.5847 | 1463904.1717 | 1479800.352 | 1476712.9454 | 1470914.9853 | 1485264.6804 | 1481850.3681 | 1475410.5471 | 1490895.0674 | 1487157.2614 | 1480083.2081 | 1500589.2239 | 1496316.713 | 1488197.7139
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1461759.2405 | 1459907.2887 | 1456519.69 | 1471146.1004 | 1468613.5847 | 1463904.1717 | 1479800.352 | 1476712.9454 | 1470914.9853 | 1485264.6804 | 1481850.3681 | 1475410.5471 | 1490895.0674 | 1487157.2614 | 1480083.2081 | 1500589.2239 | 1496316.713 | 1488197.7139
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 7079406.516 | 6909119.698 | 6593003.4193 | 7917117.9139 | 7695100.9009 | 7274487.9431 | 8655463.3523 | 8395530.4648 | 7896973.51 | 9106671.6487 | 8826033.7497 | 8284748.2741 | 9560493.065 | 9260434.806 | 8679092.7753 | 10317675.9463 | 9987565.9822 | 9344435.5613
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1061910.9774 | 1036367.9547 | 988950.5129 | 1187567.6871 | 1154265.1351 | 1091173.1915 | 1298319.5028 | 1259329.5697 | 1184546.0265 | 1366000.7473 | 1323905.0625 | 1242712.2411 | 1434073.9597 | 1389065.2209 | 1301863.9163 | 1547651.3919 | 1498134.8973 | 1401665.3342
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 332721.3967 | 324718.1738 | 309861.187 | 372092.5651 | 361658.1014 | 341889.9286 | 406793.6838 | 394577.2313 | 371145.8086 | 427999.7911 | 414810.2344 | 389370.6359 | 449328.7112 | 435226.4269 | 407904.2309 | 484915.1611 | 469400.4922 | 439174.3353
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 913.5 |  |  |  | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 1920 |  |  |  | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 442629.8886 | 431982.946 | 412218.2224 | 495006.61 | 481125.31 | 454827.0792 | 541170.6152 | 524918.6788 | 493747.1097 | 569381.7764 | 551835.2883 | 517992.1788 | 597756.3191 | 578995.6005 | 542648.0115 | 645098.1088 | 624458.4498 | 584247.629
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 13982693.7486 | 0 | 0 | 577288.7622 | 549850.766 | 500686.6397 | 721994.0645 | 682068.5717 | 609542.873 | 862938.8959 | 811887.1817 | 718324.6391 | 955253.7619 | 897285.3323 | 790602.2307 | 1052834.1964 | 987784.3888 | 867656.9752 | 1226205.2412 | 1148996.5478 | 1005785.9114
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1553632.6387 | 1479789.929 | 1347476.6116 | 1943071.8506 | 1835622.0736 | 1640436.7523 | 2322390.6675 | 2184997.3652 | 1933196.4824 | 2570833.7316 | 2414825.7679 | 2127714.084 | 2833447.7954 | 2658382.021 | 2335088.2334 | 3300033.8983 | 3092245.433 | 2706828.7515
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 233044.8958 | 0 | 0 | 129547.5733 | 123390.298 | 112357.5295 | 162020.4395 | 153060.884 | 136785.6178 | 193649.4301 | 182193.0739 | 161196.9951 | 214365.5217 | 201357.007 | 177416.5844 | 236263.2431 | 221665.6184 | 194708.1996 | 275168.8993 | 257842.7369 | 225705.284
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 149148.7333 | 0 | 0 | 1019847.1554 | 971374.7717 | 884520.6744 | 1275485.7553 | 1204952.7691 | 1076827.7608 | 1524481.0497 | 1434292.3108 | 1269003.2922 | 1687565.9038 | 1585157.9896 | 1396689.9909 | 1859952.9915 | 1745035.0067 | 1532816.0809 | 2166232.9305 | 2029834.8722 | 1776836.7718
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 292351848.1033 | 291981457.7321 | 291303937.9917 | 294229220.081 | 293722716.9406 | 292780834.3413 | 295960070.3922 | 295342589.071 | 294182997.0585 | 297052936.0776 | 296370073.6267 | 295082109.415 | 298179013.4764 | 297431452.2842 | 296016641.6181 | 300117844.7724 | 299263342.6064 | 297639542.7735
| Survey, Design, Supervision etc. | [5 empty] | 5344168.574 | 5340464.6703 | 5333689.4729 | 5362942.2938 | 5357877.2624 | 5348458.4364 | 5380250.7969 | 5374075.9837 | 5362480.0636 | 5391179.4538 | 5384350.8293 | 5371471.1871 | 5402440.2278 | 5394964.6158 | 5380816.5092 | 5421828.5407 | 5413283.5191 | 5397045.5207
| TOTAL COST | [5 empty] | 297696016.6773 | 297321922.4024 | 296637627.4646 | 299592162.3748 | 299080594.203 | 298129292.7777 | 301340321.1891 | 300716665.0547 | 299545477.1221 | 302444115.5314 | 301754424.456 | 300453580.6021 | 303581453.7042 | 302826416.9 | 301397458.1273 | 305539673.3131 | 304676626.1254 | 303036588.2942
| TOTAL COST IN RS. LAKHS | [5 empty] | 2976.9602 | 2973.2192 | 2966.3763 | 2995.9216 | 2990.8059 | 2981.2929 | 3013.4032 | 3007.1667 | 2995.4548 | 3024.4412 | 3017.5442 | 3004.5358 | 3035.8145 | 3028.2642 | 3013.9746 | 3055.3967 | 3046.7663 | 3030.3659
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 29.7696 | 29.7322 | 29.6638 | 29.9592 | 29.9081 | 29.8129 | 30.134 | 30.0717 | 29.9545 | 30.2444 | 30.1754 | 30.0454 | 30.3581 | 30.2826 | 30.1397 | 30.554 | 30.4677 | 30.3037
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1981290.6426 | 1979044.9843 | 1974984.7422 | 1992580.352 | 1989494.3822 | 1983819.1984 | 2003035.7593 | 1999260.2663 | 1992246.2322 | 2009655.9073 | 2005472.6337 | 1997666.0338 | 2016490.1503 | 2011902.3638 | 2003310.6662 | 2028283.8937 | 2023025.6202 | 2013136.7708
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1981290.6426 | 1979044.9843 | 1974984.7422 | 1992580.352 | 1989494.3822 | 1983819.1984 | 2003035.7593 | 1999260.2663 | 1992246.2322 | 2009655.9073 | 2005472.6337 | 1997666.0338 | 2016490.1503 | 2011902.3638 | 2003310.6662 | 2028283.8937 | 2023025.6202 | 2013136.7708
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8037305.6921 | 7841933.1808 | 7483027.7467 | 8988462.4858 | 8733365.5444 | 8254734.8422 | 9827887.7211 | 9529012.4415 | 8961012.0379 | 10341152.4323 | 10018380.3532 | 9401399.9689 | 10857526.0097 | 10512348.6907 | 9849470.6999 | 11719259.1788 | 11339429.8841 | 10605802.6202
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1205595.8538 | 1176289.9771 | 1122454.162 | 1348269.3729 | 1310004.8317 | 1238210.2263 | 1474183.1582 | 1429351.8662 | 1344151.8057 | 1551172.8649 | 1502757.053 | 1410209.9953 | 1628628.9015 | 1576852.3036 | 1477420.605 | 1757888.8768 | 1700914.4826 | 1590870.393
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 377741.2089 | 368558.9964 | 351690.9839 | 422444.1393 | 410454.9689 | 387960.05 | 461895.8555 | 447849.1695 | 421154.0098 | 486018.5205 | 470848.721 | 441851.5763 | 510287.2974 | 494064.4856 | 462910.2228 | 550787.4528 | 532936.0505 | 498456.6789
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 1002.252 | 5880 |  |  |  | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943 | 5893241.4943
| Insulators 210 kN | 1201.6342 | 1920 |  |  |  | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148 | 2307137.7148
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 502521.181 | 490305.7909 | 467865.7357 | 561990.9155 | 546041.3397 | 516115.6314 | 614474.7922 | 595788.0377 | 560274.615 | 646565.943 | 626385.0748 | 587809.2481 | 678851.4712 | 657269.7471 | 615824.2374 | 732730.1199 | 708981.83 | 663112.822
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 18022627.9152 | 0 | 0 | 744081.2728 | 708346.3752 | 644991.6793 | 930615.3706 | 878542.302 | 784884.325 | 1112550.6028 | 1045912.1038 | 924939.917 | 1231791.7203 | 1156097.4219 | 1018085.9872 | 1357879.2685 | 1272913.5707 | 1117442.5029 | 1581975.3752 | 1481091.3339 | 1295646.3673
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 2002514.2128 | 1906342.4062 | 1735838.6135 | 2504525.4791 | 2364383.4494 | 2112325.728 | 2994160.0146 | 2814818.6627 | 2489251.3728 | 3315068.5515 | 3111355.7126 | 2739931.4213 | 3654402.5953 | 3425738.0347 | 3007325.3769 | 4257502.8951 | 3985997.9751 | 3486917.8411
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 300377.1319 | 0 | 0 | 166976.9611 | 158957.804 | 144740.574 | 208836.497 | 197150.9419 | 176133.447 | 249664.0159 | 234709.8779 | 207562.8862 | 276422.5437 | 259436.2219 | 228465.5057 | 304717.4577 | 285650.5701 | 250761.792 | 355006.1671 | 332367.0936 | 290751.9662
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 192241.3644 | 0 | 0 | 1314505.3552 | 1251375.5387 | 1139452.164 | 1644039.3449 | 1552046.2657 | 1386588.6512 | 1965448.9083 | 1847724.3169 | 1634013.0018 | 2176102.09 | 2042379.3848 | 1798566.2739 | 2398850.2807 | 2248748.5798 | 1974091.0139 | 2794741.8897 | 2616518.5997 | 2288908.6858
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 396258128.5246 | 395808996.8562 | 394996948.4462 | 398516070.3921 | 397898876.4307 | 396763839.6882 | 400607151.8555 | 399852053.2631 | 398449246.4331 | 401931181.4531 | 401094526.7302 | 399533206.7638 | 403298030.0689 | 402380472.7693 | 400662133.2377 | 405656778.7424 | 404605124.0364 | 402627354.1615
| Survey, Design, Supervision etc. | [5 empty] | 6383231.3782 | 6378740.0615 | 6370619.5774 | 6405810.7969 | 6399638.8573 | 6388288.4899 | 6426721.6115 | 6419170.6256 | 6405142.5573 | 6439961.9075 | 6431595.3603 | 6415982.1606 | 6453630.3937 | 6444454.8207 | 6427271.4254 | 6477217.8804 | 6466701.3334 | 6446923.6346
| TOTAL COST | [5 empty] | 402641359.9029 | 402187736.9177 | 401367568.0236 | 404921881.189 | 404298515.288 | 403152128.178 | 407033873.467 | 406271223.8888 | 404854388.9904 | 408371143.3606 | 407526122.0905 | 405949188.9244 | 409751660.4626 | 408824927.59 | 407089404.6631 | 412133996.6228 | 411071825.3698 | 409074277.7961
| TOTAL COST IN RS. LAKHS | [5 empty] | 4026.4136 | 4021.8774 | 4013.6757 | 4049.2188 | 4042.9852 | 4031.5213 | 4070.3387 | 4062.7122 | 4048.5439 | 4083.7114 | 4075.2612 | 4059.4919 | 4097.5166 | 4088.2493 | 4070.894 | 4121.34 | 4110.7183 | 4090.7428
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 40.2641 | 40.2188 | 40.1368 | 40.4922 | 40.4299 | 40.3152 | 40.7034 | 40.6271 | 40.4854 | 40.8371 | 40.7526 | 40.5949 | 40.9752 | 40.8825 | 40.7089 | 41.2134 | 41.1072 | 40.9074
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 13309062.3407 | 13941842.3508 | 14341910.5814
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 7828860.2004 | 8201083.7358 | 8436417.9891
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 12243.3706 | 13283.528 | 13922.4666 | 734602.2359 | 797011.6778 | 835347.9947
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 282821.8608 | 306849.4959 | 321608.978
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) x No. of Ckts. | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 2436 |  |  |  | 876960000 | 876960000 | 876960000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 21000 | 1680 |  |  |  | 35280000 | 35280000 | 35280000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 40 |  |  |  | 1240000 | 1240000 | 1240000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 840 |  |  |  | 49560000 | 49560000 | 49560000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 40 |  |  |  | 1800000 | 1800000 | 1800000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 812 |  |  |  | 1055600 | 1055600 | 1055600
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 5040 | 10080 |  |  |  | 50803200 | 50803200 | 50803200
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 1680 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 0 |  |  |  | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 380000 | 100 |  |  |  | 38000000 | 38000000 | 38000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 484837.4757 | 526027.7073 | 551329.6765
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 110476.1386 | 135501.5486 | 151914.4961 | 33142841.5799 | 40650464.5715 | 45574348.8348
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 12275.1265 | 15055.7276 | 16879.3885 | 69968221.113 | 85817647.4288 | 96212514.2067
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 1841.269 | 2258.3591 | 2531.9083 | 8653964.1903 | 10614287.9715 | 11899968.8624
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 1178.4121 | 1445.3499 | 1620.4213 | 63634255.8333 | 78048891.9773 | 87502749.7628
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 1565772040.0812 | 1640216747.1546 | 1687283597.8152
| Survey, Design, Supervision etc. | [5 empty] | 34966782.7415 | 36344009.8224 | 37214746.5596
| TOTAL COST | [5 empty] | 1600738822.8227 | 1676560756.9769 | 1724498344.3747
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 288132988.1081 | 301780936.2558 | 310409701.9875
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
v) | Contengency at 3% | [5 empty] | 48022164.6847 | 50296822.7093 | 51734950.3312
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1984916140.3001 | 2078935338.6514 | 2138377947.0247
| TOTAL COST IN RS. LAKHS | [5 empty] | 19849.1614 | 20789.3534 | 21383.7795
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 198.4916 | 207.8935 | 213.8378
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 8411202.1434 | 8912246.9919 | 9223024.2025
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
III | Detailed survey (Rs. Per kM) | 50000 | 100 |  |  |  | 5000000 | 5000000 | 5000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 4947765.9667 | 5242498.2305 | 5425308.3544
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 15939.2541 | 17870.532 | 19033.8182 | 200834601.2279 | 225168702.6717 | 239826109.8086
| b) 'B' Type towers | 60000 | 25 | 22649.4998 | 24911.6351 | 26290.2337 | 33974249.7567 | 37367452.5951 | 39435350.6152
| c) 'C' Type towers | 60000 | 25 | 27275.3928 | 29766.9223 | 31292.2837 | 40913089.2638 | 44650383.4197 | 46938425.5896
| d) 'D' Type towers | 60000 | 20 | 30608.4265 | 33208.8199 | 34806.1664 | 36730111.7938 | 39850583.8878 | 41767399.7359
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 520753.4201 | 578395.2043 | 613278.8096 | 31245205.2042 | 34703712.2574 | 36796728.5749
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 12029404.0036 | 13360929.2191 | 14166740.5013
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 1218 |  |  |  | 438480000 | 438480000 | 438480000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of suspn.x1) | 24000 | 210 |  |  |  | 5040000 | 5040000 | 5040000
| b) Double 'I' Suspension Insulator Sring (No. Suspn. X 2) | 21000 | 420 |  |  |  | 8820000 | 8820000 | 8820000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'V' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
| f) Single 'I' Suspension Pilot strings (No. of Suspn x 1) | 15000 | 210 |  |  |  | 3150000 | 3150000 | 3150000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 406 |  |  |  | 527800 | 527800 | 527800
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 2700 | 5040 |  |  |  | 13608000 | 13608000 | 13608000
| f) Quad Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 1000 | 840 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190000 | 100 |  |  |  | 19000000 | 19000000 | 19000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 20621835.4348 | 22904450.0899 | 24285840.8595
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 48382.6073 | 59272.006 | 66421.8968 | 14514782.1992 | 17781601.804 | 19926569.0329
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 5375.8453 | 6585.7784 | 7380.2108 | 30642317.976 | 37538937.1417 | 42067201.2916
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 806.3768 | 987.8668 | 1107.0316 | 3789970.9076 | 4642973.8044 | 5203048.5808
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 516.0811 | 632.2347 | 708.5002 | 27868381.8224 | 34140675.4636 | 38259012.5431
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 989553193.3401 | 1048499646.1046 | 1085061670.8834
| Survey, Design, Supervision etc. | [5 empty] | 23306734.0768 | 24397243.4529 | 25073640.9113
| TOTAL COST | [5 empty] | 1012859927.4169 | 1072896889.5575 | 1110135311.7948
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 182314786.935 | 193121440.1204 | 199824356.1231
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
v) | Contengency at 3% | [5 empty] | 30385797.8225 | 32186906.6867 | 33304059.3538
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1255946309.997 | 1330392143.0513 | 1376567786.6255
| TOTAL COST IN RS. LAKHS | [5 empty] | 12559.4631 | 13303.9214 | 13765.6779
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 125.5946 | 133.0392 | 137.6568
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 5050227.0344 | 5357651.6793 | 5546861.9223
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2970721.785 | 3151559.8114 | 3262859.9543
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 10366.8386 | 11627.9013 | 12386.9423 | 130622166.4713 | 146511556.3957 | 156075473.2845
| b) 'B' Type towers | 60000 | 25 | 16898.4575 | 18612.4108 | 19653.708 | 25347686.3224 | 27918616.1635 | 29480562.0497
| c) 'C' Type towers | 60000 | 25 | 20290.3432 | 22180.6901 | 23333.1622 | 30435514.7251 | 33271035.0929 | 34999743.239
| d) 'D' Type towers | 60000 | 20 | 25560.0611 | 27781.5378 | 29139.1942 | 30672073.3304 | 33337845.351 | 34967032.9907
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 361795.7347 | 401731.755 | 425871.3526 | 21707744.0849 | 24103905.3003 | 25552281.1564
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 7163555.548 | 7954288.7491 | 8432252.7816
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 609 |  |  |  | 219240000 | 219240000 | 219240000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) | 21000 | 840 |  |  |  | 17640000 | 17640000 | 17640000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 203 |  |  |  | 263900 | 263900 | 263900
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 900 | 5040 |  |  |  | 4536000 | 4536000 | 4536000
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 840 |  |  |  | 420000 | 420000 | 420000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 3360 |  |  |  | 3024000 | 3024000 | 3024000
V | ERECTION
2 | Stringing of Conductor (Route kM) | 95000 | 100 |  |  |  | 9500000 | 9500000 | 9500000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 12280380.9395 | 13635923.5699 | 14455290.4828
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 21646.7931 | 26473.7232 | 29642.2493 | 6494037.9255 | 7942116.9663 | 8892674.7876
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 2405.1992 | 2941.5248 | 3293.5833 | 13709635.6204 | 16766691.3734 | 18773424.5515
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 360.7799 | 441.2287 | 494.0375 | 1695665.4583 | 2073774.9857 | 2321976.1945
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 230.8991 | 282.3864 | 316.184 | 12468552.8169 | 15248864.5753 | 17073935.5921
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 594144356.9927 | 630311962.2731 | 652571990.8604
| Survey, Design, Supervision etc. | [5 empty] | 16991670.6044 | 17660771.3021 | 18072581.8309
| TOTAL COST | [5 empty] | 611136027.5971 | 647972733.5751 | 670644572.6913
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 110004484.9675 | 116635092.0435 | 120716023.0844
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
v) | Contengency at 3% | [5 empty] | 18334080.8279 | 19439182.0073 | 20119337.1807
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 757808674.2204 | 803486189.6332 | 831599270.1372
| TOTAL COST IN RS. LAKHS | [5 empty] | 7578.0867 | 8034.8619 | 8315.9927
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 75.7809 | 80.3486 | 83.1599

## Bersi-Std-Hilly
CERC
Capital Cost Benchmarking
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1803195.8692 | 1801735.3131 | 1798138.0136 | 1813052.9914 | 1811062.3253 | 1806082.9461 | 1822146.2036 | 1819721.0162 | 1813600.8299 | 1827894.3486 | 1825211.6333 | 1818415.5716 | 1833824.077 | 1830885.2984 | 1823418.4677 | 1844051.9503 | 1840687.3188 | 1832108.6573
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1803195.8692 | 1801735.3131 | 1798138.0136 | 1813052.9914 | 1811062.3253 | 1806082.9461 | 1822146.2036 | 1819721.0162 | 1813600.8299 | 1827894.3486 | 1825211.6333 | 1818415.5716 | 1833824.077 | 1830885.2984 | 1823418.4677 | 1844051.9503 | 1840687.3188 | 1832108.6573
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 10736.956 | 12057.6633 | 12852.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 17132.487 | 18950.123 | 20054.3624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 20389.7437 | 22403.5518 | 23631.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 25511.93 | 27885.7649 | 29338.4186 | 6659322.9597 | 6536132.2035 | 6227995.4502 | 7464184.13 | 7305173.0713 | 6899728.1175 | 8169995.8962 | 7984905.0528 | 7507648.4307 | 8600186.1385 | 8400862.8735 | 7884349.8016 | 9032222.4043 | 8819536.6843 | 8266225.064 | 9751975.6427 | 9518565.7067 | 8908409.2488
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 10204.772 | 11154.306 | 11735.3675 | 998898.444 | 980419.8305 | 934199.3175 | 1119627.6195 | 1095775.9607 | 1034959.2176 | 1225499.3844 | 1197735.7579 | 1126147.2646 | 1290027.9208 | 1260129.431 | 1182652.4702 | 1354833.3606 | 1322930.5026 | 1239933.7596 | 1462796.3464 | 1427784.856 | 1336261.3873
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 312978.105 | 307188.3259 | 292706.3646 | 350805.3625 | 343332.0833 | 324276.7838 | 383977.4477 | 375278.4581 | 352848.1188 | 404195.7383 | 394827.8464 | 370552.5134 | 424500.7893 | 414504.8822 | 388500.0731 | 458328.1026 | 447358.1887 | 418681.7583
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 416364.7579 | 408662.4299 | 389396.6149 | 466687.5652 | 456745.6235 | 431395.7507 | 510817.4486 | 499244.9051 | 469405.1092 | 537714.4856 | 525252.0801 | 492957.8301 | 564726.9426 | 551429.0685 | 516834.0413 | 609728.4967 | 595134.8703 | 556985.7
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 12617189.112 | 2937.0007 | 3250.9652 | 625095.1311 | 602181.7881 | 546742.1224 | 785327.2181 | 752223.6441 | 671042.3299 | 940870.0363 | 898722.2087 | 794499.8427 | 1042561.452 | 994795.3641 | 876229.2156 | 1149940.0686 | 1096421.3989 | 963164.3785 | 1340513.4532 | 1277111.9995 | 1118629.534
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 326.3334 | 361.2184 | 1401909.9013 | 1350521.8151 | 1226186.4742 | 1761264.7227 | 1687022.858 | 1504956.3492 | 2110102.8533 | 2015577.31 | 1781836.3007 | 2338167.6636 | 2231041.9668 | 1965131.9486 | 2578987.2419 | 2458960.1463 | 2160102.6973 | 3006388.9309 | 2864197.5727 | 2508766.6526
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 210286.4852 | 48.95 | 54.1828 | 175344.5645 | 168917.1746 | 153365.8712 | 220291.044 | 211005.2066 | 188233.1492 | 263922.1433 | 252099.3149 | 222864.0442 | 292447.4607 | 279048.6619 | 245789.8367 | 322568.0869 | 307555.6393 | 270175.8982 | 376025.5615 | 358240.9081 | 313785.2124
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 134583.3505 | 31.328 | 34.677 | 1533753.6358 | 1477532.716 | 1341504.1589 | 1926904.2679 | 1845680.2678 | 1646491.169 | 2308549.1586 | 2205133.8853 | 1949410.5163 | 2558062.5058 | 2440862.0874 | 2149944.3496 | 2821530.1534 | 2690215.0139 | 2363251.2778 | 3289127.175 | 3133563.3171 | 2744705.6128
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 360639173.8446 | 360347062.6287 | 359627602.7192 | 362610598.2752 | 362212465.0604 | 361216589.212 | 364429240.7138 | 363944203.2381 | 362720165.9724 | 365578869.7106 | 365042326.6564 | 363683114.3111 | 366764815.3927 | 366177059.6812 | 364683693.5349 | 368810390.0543 | 368137463.7644 | 366421731.4515
| Survey, Design, Supervision etc. | [5 empty] | 6027041.8314 | 6024120.7193 | 6016926.1202 | 6046756.0757 | 6042774.7436 | 6032815.9851 | 6064942.5001 | 6060092.1254 | 6047851.7527 | 6076438.7901 | 6071073.3596 | 6057481.2361 | 6088298.2469 | 6082420.6898 | 6067487.0283 | 6108753.9935 | 6102024.7306 | 6084867.4075
| TOTAL COST | [5 empty] | 366666215.6761 | 366371183.3479 | 365644528.8393 | 368657354.3509 | 368255239.804 | 367249405.1971 | 370494183.2139 | 370004295.3634 | 368768017.7251 | 371655308.5006 | 371113400.016 | 369740595.5472 | 372853113.6396 | 372259480.371 | 370751180.5632 | 374919144.0479 | 374239488.495 | 372506598.859
| TOTAL COST IN RS. LAKHS | [5 empty] | 3666.6622 | 3663.7118 | 3656.4453 | 3686.5735 | 3682.5524 | 3672.4941 | 3704.9418 | 3700.043 | 3687.6802 | 3716.5531 | 3711.134 | 3697.406 | 3728.5311 | 3722.5948 | 3707.5118 | 3749.1914 | 3742.3949 | 3725.066
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 36.6666 | 36.6371 | 36.5645 | 36.8657 | 36.8255 | 36.7249 | 37.0494 | 37.0004 | 36.8768 | 37.1655 | 37.1113 | 36.9741 | 37.2853 | 37.2259 | 37.0751 | 37.4919 | 37.4239 | 37.2507
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 2553366.2883 | 2551430.192 | 2546699.3557 | 2566381.8656 | 2563724.8497 | 2557129.7866 | 2578461.4735 | 2575208.285 | 2567060.3899 | 2586126.6522 | 2582518.2847 | 2573445.4312 | 2594054.4689 | 2590091.784 | 2580097.8278 | 2607771.6088 | 2603217.4985 | 2591690.9153
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 2553366.2883 | 2551430.192 | 2546699.3557 | 2566381.8656 | 2563724.8497 | 2557129.7866 | 2578461.4735 | 2575208.285 | 2567060.3899 | 2586126.6522 | 2582518.2847 | 2573445.4312 | 2594054.4689 | 2590091.784 | 2580097.8278 | 2607771.6088 | 2603217.4985 | 2591690.9153
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 40.0568 | 48.36 | 53.8088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 6.0085 | 7.254 | 8.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4806.8175 | 5803.2042 | 6457.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8004058.2809 | 7854875.4913 | 7484090.7527 | 8971864.7131 | 8778977.332 | 8290009.9376 | 9821691.9756 | 9596985.7401 | 9020760.9936 | 10339942.8136 | 10097881.3234 | 9473976.3061 | 10860547.7226 | 10602199.8115 | 9933622.9023 | 11728018.4514 | 11444427.8991 | 10706897.2347
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1200608.7421 | 1178231.3237 | 1122613.6129 | 1345779.707 | 1316846.5998 | 1243501.4906 | 1473253.7963 | 1439547.861 | 1353114.149 | 1550991.422 | 1514682.1985 | 1421096.4459 | 1629082.1584 | 1590329.9717 | 1490043.4353 | 1759202.7677 | 1716664.1849 | 1606034.5852
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 376178.6308 | 369167.2654 | 351740.9436 | 421664.0691 | 412598.654 | 389617.9261 | 461604.6648 | 451043.8117 | 423962.1203 | 485961.6702 | 474585.1464 | 445262.5544 | 510429.3134 | 498287.3524 | 466865.2491 | 551199.1253 | 537870.7984 | 503207.9729
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1827 |  |  |  | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446 | 438917019.8446
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'v'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 609 |  |  |  | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021 | 929338.6021
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 288 |  |  |  | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521 | 191032.8521
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 500442.4336 | 491114.9905 | 467932.1987 | 560953.1632 | 548893.1523 | 518321.1569 | 614087.4119 | 600037.9721 | 564010.3341 | 646490.3133 | 631355.7606 | 592346.9811 | 679040.3995 | 662887.5615 | 621085.735 | 733277.781 | 715546.6825 | 669433.6199
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 18227325.1949 | 158.0273 | 176.0122 | 903038.8727 | 869690.1911 | 789521.6642 | 1134622.5053 | 1086360.125 | 968715.0866 | 1359748.476 | 1298242.015 | 1147023.4945 | 1507031.1695 | 1437296.8894 | 1265174.8484 | 1662606.2841 | 1584447.7812 | 1390917.2713 | 1938809.9606 | 1846180.3998 | 1615895.3446
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17.5586 | 19.5569 | 2025258.355 | 1950466.7837 | 1770671.6678 | 2544634.3207 | 2436395.5817 | 2172551.3507 | 3049527.595 | 2911586.1643 | 2572446.1988 | 3379840.624 | 3223446.5445 | 2837425.951 | 3728751.1862 | 3553463.98 | 3119430.3035 | 4348197.1705 | 4140455.5133 | 3623991.8858
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 303788.7532 | 2.6338 | 2.9335 | 253310.1763 | 243955.5841 | 221467.6223 | 318271.3785 | 304733.3654 | 271732.9196 | 381421.151 | 364168.0593 | 321749.9627 | 422735.2141 | 403174.1484 | 354892.4344 | 466375.3728 | 444451.2401 | 390164.2663 | 543852.8814 | 517869.4923 | 453272.5523
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 194424.8021 | 1.6856 | 1.8775 | 2215725.3918 | 2133899.9876 | 1937195.8966 | 2783946.4844 | 2665528.3468 | 2376870.6748 | 3336322.8492 | 3185408.6066 | 2814373.9527 | 3697700.4304 | 3526598.1449 | 3104273.937 | 4079424.5646 | 3887652.3333 | 3412799.6136 | 4757126.8404 | 4529847.9535 | 3964813.0922
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 510673257.6616 | 510286038.3956 | 509339871.137 | 513276373.1195 | 512744969.9351 | 511425957.3211 | 515692294.6981 | 515041657.0081 | 513412077.9839 | 517225330.4353 | 516503656.9342 | 514689086.2365 | 518810893.7799 | 518018356.8098 | 516019565.5547 | 521554321.7565 | 520643499.7019 | 518338183.0657
| Survey, Design, Supervision etc. | [5 empty] | 7527382.6696 | 7523510.4769 | 7514048.8044 | 7553413.8242 | 7548099.7923 | 7534909.6662 | 7577573.04 | 7571066.6631 | 7554770.8728 | 7592903.3973 | 7585686.6623 | 7567540.9554 | 7608759.0308 | 7600833.6611 | 7580845.7485 | 7636193.3106 | 7627085.09 | 7604031.9236
| TOTAL COST | [5 empty] | 518200640.3312 | 517809548.8725 | 516853919.9414 | 520829786.9437 | 520293069.7275 | 518960866.9873 | 523269867.738 | 522612723.6712 | 520966848.8568 | 524818233.8327 | 524089343.5966 | 522256627.1918 | 526419652.8107 | 525619190.4708 | 523600411.3032 | 529190515.067 | 528270584.7919 | 525942214.9893
| TOTAL COST IN RS. LAKHS | [5 empty] | 5182.0064 | 5178.0955 | 5168.5392 | 5208.2979 | 5202.9307 | 5189.6087 | 5232.6987 | 5226.1272 | 5209.6685 | 5248.1823 | 5240.8934 | 5222.5663 | 5264.1965 | 5256.1919 | 5236.0041 | 5291.9052 | 5282.7058 | 5259.4221
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 51.8201 | 51.781 | 51.6854 | 52.083 | 52.0293 | 51.8961 | 52.327 | 52.2613 | 52.0967 | 52.4818 | 52.4089 | 52.2257 | 52.642 | 52.5619 | 52.36 | 52.9191 | 52.8271 | 52.5942
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 3336284.3403 | 3333969.1498 | 3328340.5393 | 3351844.1582 | 3348646.0385 | 3340748.0303 | 3366368.9338 | 3362433.9574 | 3352627.9948 | 3375620.6117 | 3371244.2269 | 3360295.2845 | 3385214.2615 | 3380396.0108 | 3368304.6961 | 3401866.7592 | 3396308.0765 | 3382308.1131
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 3336284.3403 | 3333969.1498 | 3328340.5393 | 3351844.1582 | 3348646.0385 | 3340748.0303 | 3366368.9338 | 3362433.9574 | 3352627.9948 | 3375620.6117 | 3371244.2269 | 3360295.2845 | 3385214.2615 | 3380396.0108 | 3368304.6961 | 3401866.7592 | 3396308.0765 | 3382308.1131
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 5171.2716 | 6521.2975 | 7409.1895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8543101.1457 | 8383241.0339 | 7987245.1339 | 9576321.4822 | 9369445.649 | 8846615.7148 | 10484222.4281 | 10243118.0431 | 9626620.6551 | 11038048.1566 | 10778279.3545 | 10110610.1655 | 11594462.7805 | 11317183.5237 | 10601584.2045 | 12521695.6098 | 12217285.8025 | 11427733.5408
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1281465.1719 | 1257486.1551 | 1198086.7701 | 1436448.2223 | 1405416.8474 | 1326992.3572 | 1572633.3642 | 1536467.7065 | 1443993.0983 | 1655707.2235 | 1616741.9032 | 1516591.5248 | 1739169.4171 | 1697577.5286 | 1590237.6307 | 1878254.3415 | 1832592.8704 | 1714160.0311
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 401512.83 | 393999.6466 | 375388.4384 | 450072.6228 | 440349.7716 | 415777.5556 | 492742.5938 | 481411.0525 | 452436.6079 | 518771.5653 | 506562.8245 | 475183.3827 | 544922.2108 | 531890.5052 | 498258.4198 | 588500.7511 | 574193.9507 | 537086.1888
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 8 |  |  |  | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157 | 1687.9157
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 8 |  |  |  | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387 | 1431.387
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 2436 |  |  |  | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262 | 585222693.1262
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 48 |  |  |  | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732 | 628962.6732
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 2304 |  |  |  | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326 | 1591412.326
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 812 |  |  |  | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361 | 1239118.1361
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 384 |  |  |  | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695 | 254710.4695
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 534145.327 | 524150.2995 | 499391.2154 | 598745.9686 | 585811.3494 | 553122.1466 | 655511.1923 | 640436.4813 | 601890.8533 | 690138.3633 | 673896.6861 | 632151.6135 | 724927.4015 | 707590.9077 | 662849.0715 | 782901.3238 | 763868.5308 | 714502.8913
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 23837461.2777 | 85.8156 | 94.7378 | 1180982.6144 | 1137198.5941 | 1032301.206 | 1483917.7925 | 1420496.6059 | 1266387.8433 | 1778626.9158 | 1697761.8213 | 1499547.1463 | 1971500.8869 | 1879798.4147 | 1654120.4813 | 2175272.4996 | 2072474.1635 | 1818670.1642 | 2537106.4679 | 2415248.8 | 2113161.1551
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 9.5351 | 10.5264 | 2648606.8086 | 2550411.7524 | 2315156.8614 | 3328003.9188 | 3185768.3054 | 2840146.3523 | 3988952.3366 | 3807595.0185 | 3363056.097 | 4421513.5845 | 4215851.1222 | 3709719.9534 | 4878515.1306 | 4647967.8137 | 4078757.9097 | 5690005.4102 | 5416713.454 | 4739217.1189
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 397291.0213 | 1.4303 | 1.579 | 331275.7881 | 318993.9936 | 289569.3734 | 416251.713 | 398461.5243 | 355232.6899 | 498920.1586 | 476236.8036 | 420635.8812 | 553022.9676 | 527299.6349 | 463995.0321 | 610182.6588 | 581346.8408 | 510152.6345 | 711680.2013 | 677498.0766 | 592759.8921
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 254266.2536 | 0.91537 | 1.0105 | 2897697.1478 | 2790267.2592 | 2532887.6344 | 3640988.7009 | 3485376.4258 | 3107250.1805 | 4364096.5397 | 4165683.328 | 3679337.3892 | 4837338.355 | 4612334.2024 | 4058603.5244 | 5337318.9759 | 5085089.6528 | 4462347.9495 | 6225126.5058 | 5926132.5898 | 5184920.5716
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 667256868.0614 | 666793829.9622 | 665668107.8607 | 670368831.6489 | 669729207.7066 | 668149606.0682 | 673273786.757 | 672486791.4825 | 670525598.9561 | 675124122.3306 | 674248845.3703 | 672059056.9056 | 677042852.3028 | 676079202.1638 | 673660939.2121 | 680373351.8392 | 679261615.3025 | 676461622.6177
| Survey, Design, Supervision etc. | [5 empty] | 9093218.7736 | 9088588.3926 | 9077331.1716 | 9124338.4095 | 9117942.1701 | 9102146.1537 | 9153387.9606 | 9145518.0078 | 9125906.0825 | 9171891.3163 | 9163138.5467 | 9141240.662 | 9191078.616 | 9181442.1146 | 9157259.4851 | 9224383.6114 | 9213266.246 | 9185266.3192
| TOTAL COST | [5 empty] | 676350086.835 | 675882418.3548 | 674745439.0323 | 679493170.0583 | 678847149.8767 | 677251752.2219 | 682427174.7175 | 681632309.4903 | 679651505.0386 | 684296013.6469 | 683411983.917 | 681200297.5676 | 686233930.9188 | 685260644.2784 | 682818198.6973 | 689597735.4506 | 688474881.5485 | 685646888.9369
| TOTAL COST IN RS. LAKHS | [5 empty] | 6763.5009 | 6758.8242 | 6747.4544 | 6794.9317 | 6788.4715 | 6772.5175 | 6824.2717 | 6816.3231 | 6796.5151 | 6842.9601 | 6834.1198 | 6812.003 | 6862.3393 | 6852.6064 | 6828.182 | 6895.9774 | 6884.7488 | 6856.4689
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 67.635 | 67.5882 | 67.4745 | 67.9493 | 67.8847 | 67.7252 | 68.2427 | 68.1632 | 67.9652 | 68.4296 | 68.3412 | 68.12 | 68.6234 | 68.5261 | 68.2818 | 68.9598 | 68.8475 | 68.5647
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1031362.3704 | 1030521.7573 | 1028941.0144 | 1035517.0332 | 1034369.577 | 1032173.0931 | 1039341.3659 | 1037944.4651 | 1035241.8352 | 1041753.295 | 1040209.7671 | 1037209.262 | 1044236.3883 | 1042548.0012 | 1039253.6381 | 1048506.8428 | 1046579.5035 | 1042802.0494
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1031362.3704 | 1030521.7573 | 1028941.0144 | 1035517.0332 | 1034369.577 | 1032173.0931 | 1039341.3659 | 1037944.4651 | 1035241.8352 | 1041753.295 | 1040209.7671 | 1037209.262 | 1044236.3883 | 1042548.0012 | 1039253.6381 | 1048506.8428 | 1046579.5035 | 1042802.0494
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 12.8652 | 15.2805 | 16.8693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 1.9298 | 2.2921 | 2.5304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 1543.8232 | 1833.6656 | 2024.3112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 3284960.7387 | 3205197.7366 | 3053017.5594 | 3668181.2522 | 3564092.7577 | 3361150.7555 | 4006235.1596 | 3884277.7708 | 3643334.0973 | 4212934.4634 | 4081209.1455 | 3819398.7606 | 4420902.8243 | 4280011.3345 | 3998625.6635 | 4768023.3781 | 4612943.0683 | 4301350.1076
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 492744.1108 | 480779.6605 | 457952.6339 | 550227.1878 | 534613.9137 | 504172.6133 | 600935.2739 | 582641.6656 | 546500.1146 | 631940.1695 | 612181.3718 | 572909.8141 | 663135.4236 | 642001.7002 | 599793.8495 | 715203.5067 | 691941.4602 | 645202.5161
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 154388.1853 | 150639.4449 | 143487.2068 | 172398.9697 | 167506.9679 | 157969.0008 | 188286.992 | 182555.1792 | 171231.191 | 198001.5465 | 191810.6559 | 179505.9638 | 207775.7449 | 201154.058 | 187929.3572 | 224089.8858 | 216801.3459 | 202156.9481
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 609 |  |  |  | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 1152 |  |  |  | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 96 |  |  |  | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174 | 63677.6174
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 205387.5283 | 200400.4593 | 190885.6087 | 229347.8494 | 222839.8633 | 210151.2014 | 250484.1922 | 242858.9788 | 227794.3161 | 263407.7741 | 255171.8347 | 238802.5104 | 276410.702 | 267601.6607 | 250008.4192 | 298113.9241 | 288417.7469 | 268935.8373
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 4762940.9133 | 0 | 0 | 235971.0351 | 224650.8084 | 203824.758 | 294238.7757 | 277777.0284 | 247044.0026 | 350970.979 | 329927.7838 | 290266.1065 | 388121.5325 | 364230.268 | 318998.2765 | 427385.9772 | 400578.9919 | 349638.9674 | 497135.8507 | 465323.0011 | 404583.2676
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 529215.657 | 503827.6207 | 457120.7358 | 659893.5624 | 622974.5634 | 554049.1615 | 787127.6964 | 739933.8178 | 650983.9999 | 870445.7805 | 816864.4957 | 715422.0535 | 958504.7191 | 898384.305 | 784140.3747 | 1114933.7705 | 1043586.6319 | 907364.7521
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 79382.3486 | 0 | 0 | 66191.9064 | 63016.4853 | 57174.5989 | 82536.5091 | 77918.8473 | 69297.969 | 98450.3805 | 92547.5831 | 81422.1412 | 108871.4305 | 102169.7251 | 89481.7622 | 119885.4451 | 112365.855 | 98076.7397 | 139450.885 | 130527.1069 | 113489.0888
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 50804.7031 | 0 | 0 | 578986.1655 | 551210.4911 | 500111.0199 | 721953.7787 | 681562.703 | 606155.1566 | 861153.7482 | 809521.4837 | 712206.3092 | 952307.548 | 893687.1685 | 782704.4909 | 1048648.0597 | 982873.5733 | 857885.4814 | 1219788.6059 | 1141731.5688 | 992698.5937
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 206272474.0883 | 206104351.4681 | 205788202.8828 | 207103406.6464 | 206873915.406 | 206434618.6221 | 207868273.1832 | 207588893.0242 | 207048367.0371 | 208350659.0063 | 208041953.4265 | 207441852.3934 | 208847277.6573 | 208509600.2399 | 207850727.614 | 209701368.5682 | 209315900.6912 | 208560409.8728
| Survey, Design, Supervision etc. | [5 empty] | 4483374.8339 | 4481693.6077 | 4478532.1218 | 4491684.1595 | 4489389.247 | 4484996.2792 | 4499332.8248 | 4496539.0232 | 4491133.7634 | 4504156.6831 | 4501069.6273 | 4495068.6169 | 4509122.8696 | 4505746.0954 | 4499157.3691 | 4517663.7787 | 4513809.0999 | 4506254.1917
| TOTAL COST | [5 empty] | 210755848.9222 | 210586045.0758 | 210266735.0046 | 211595090.8058 | 211363304.653 | 210919614.9013 | 212367606.008 | 212085432.0474 | 211539500.8004 | 212854815.6894 | 212543023.0537 | 211936921.0103 | 213356400.5269 | 213015346.3353 | 212349884.9831 | 214219032.3469 | 213829709.7911 | 213066664.0645
| TOTAL COST IN RS. LAKHS | [5 empty] | 2107.5585 | 2105.8605 | 2102.6674 | 2115.9509 | 2113.633 | 2109.1961 | 2123.6761 | 2120.8543 | 2115.395 | 2128.5482 | 2125.4302 | 2119.3692 | 2133.564 | 2130.1535 | 2123.4988 | 2142.1903 | 2138.2971 | 2130.6666
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 21.0756 | 21.0586 | 21.0267 | 21.1595 | 21.1363 | 21.092 | 21.2368 | 21.2085 | 21.154 | 21.2855 | 21.2543 | 21.1937 | 21.3356 | 21.3015 | 21.235 | 21.4219 | 21.383 | 21.3067
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1404773.5489 | 1403687.8798 | 1401675.3129 | 1410090.3142 | 1408597.1779 | 1405777.8463 | 1415016.9415 | 1413189.576 | 1409700.7031 | 1418136.7908 | 1416111.9391 | 1412226.8795 | 1421357.4454 | 1419136.8527 | 1414859.629 | 1426914.3964 | 1424369.7313 | 1419445.3742
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1404773.5489 | 1403687.8798 | 1401675.3129 | 1410090.3142 | 1408597.1779 | 1405777.8463 | 1415016.9415 | 1413189.576 | 1409700.7031 | 1418136.7908 | 1416111.9391 | 1412226.8795 | 1421357.4454 | 1419136.8527 | 1414859.629 | 1426914.3964 | 1424369.7313 | 1419445.3742
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 26.8371 | 32.7017 | 36.5643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4.0256 | 4.9053 | 5.4846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 3220.4572 | 3924.209 | 4387.7149 | 3895809.9723 | 3799959.9029 | 3619397.6448 | 4350752.1776 | 4225299.6474 | 3983546.6946 | 4753028.6402 | 4605821.3787 | 4318183.3507 | 4999254.8728 | 4840163.5204 | 4527336.8503 | 5247120.5665 | 5076885.5687 | 4740445.1778 | 5661015.23 | 5473548.73 | 5100712.1952
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 1288.1829 | 1569.6836 | 1755.086 | 584371.4958 | 569993.9854 | 542909.6467 | 652612.8266 | 633794.9471 | 597532.0042 | 712954.296 | 690873.2068 | 647727.5026 | 749888.2309 | 726024.5281 | 679100.5275 | 787068.085 | 761532.8353 | 711066.7767 | 849152.2845 | 821032.3095 | 765106.8293
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 183097.1752 | 178592.3669 | 170106.214 | 204478.7706 | 198582.6915 | 187220.6684 | 223385.1558 | 216466.6372 | 202948.085 | 234957.4163 | 227480.3634 | 212777.9831 | 246606.7289 | 238605.9415 | 222793.7521 | 266059.152 | 257248.51 | 239725.7569
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 913.5 |  |  |  | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'v'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 1152 |  |  |  | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 144 |  |  |  | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261 | 95516.4261
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 243580.0134 | 237587.1233 | 226297.7232 | 272024.6319 | 264180.8898 | 249065.628 | 297176.3993 | 287972.4733 | 269988.3121 | 312571.3466 | 302624.3846 | 283065.3391 | 328068.7988 | 317425.0961 | 296389.6361 | 353946.9778 | 342225.8998 | 318914.8223
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 6699005.8521 | 22535.8691 | 25593.0982 | 331889.766 | 315759.4515 | 286464.5792 | 413930.1143 | 390403.1902 | 347006.9359 | 494013.928 | 463887.3328 | 407756.1201 | 546523.5594 | 512292.9735 | 448212.4838 | 602060.892 | 563628.6754 | 491401.6245 | 700788.518 | 655143.3072 | 568931.4866
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 2503.9855 | 2843.6776 | 744333.9836 | 708158.2937 | 642458.2594 | 928327.0607 | 875562.8872 | 778237.4796 | 1107932.1892 | 1040366.8379 | 914480.5544 | 1225696.2998 | 1148926.8691 | 1005212.6272 | 1350250.6798 | 1264058.191 | 1102073.5382 | 1571668.556 | 1469299.3809 | 1275950.8826
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 111650.0975 | 375.5978 | 426.5516 | 93097.9359 | 88573.2439 | 80355.7801 | 116110.9598 | 109511.4551 | 97338.4322 | 138575.1588 | 130124.3896 | 114379.1013 | 153304.5624 | 143702.5884 | 125727.4595 | 168883.2622 | 158102.6946 | 137842.3852 | 196577.211 | 183773.3365 | 159590.1788
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 71456.0624 | 240.3826 | 272.993 | 814335.4665 | 774757.605 | 702878.7587 | 1015632.3193 | 957905.8971 | 851427.4438 | 1212128.5554 | 1138208.9668 | 1000483.6073 | 1340967.8856 | 1256978.6126 | 1099748.6502 | 1477236.0816 | 1382937.5515 | 1205718.9228 | 1719477.3785 | 1607480.8127 | 1395948.7007
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 280954709.7866 | 280737575.9503 | 280335062.5838 | 282018062.8389 | 281719435.583 | 281155569.2646 | 283003388.3006 | 282637915.2009 | 281940140.6112 | 283627358.1516 | 283222387.8178 | 282445375.8985 | 284271489.0727 | 283827370.532 | 282971925.7911 | 285382879.2855 | 284873946.2645 | 283889074.8302
| Survey, Design, Supervision etc. | [5 empty] | 5230197.1909 | 5228025.8525 | 5224000.7188 | 5240830.7214 | 5237844.4488 | 5232205.7856 | 5250683.976 | 5247029.245 | 5240051.4991 | 5256923.6745 | 5252873.9712 | 5245103.852 | 5263364.9837 | 5258923.7983 | 5250369.3509 | 5274478.8858 | 5269389.5556 | 5259540.8413
| TOTAL COST | [5 empty] | 286184906.9775 | 285965601.8028 | 285559063.3026 | 287258893.5602 | 286957280.0319 | 286387775.0502 | 288254072.2766 | 287884944.4459 | 287180192.1103 | 288884281.8261 | 288475261.789 | 287690479.7505 | 289534854.0564 | 289086294.3303 | 288222295.142 | 290657358.1713 | 290143335.8201 | 289148615.6715
| TOTAL COST IN RS. LAKHS | [5 empty] | 2861.8491 | 2859.656 | 2855.5906 | 2872.5889 | 2869.5728 | 2863.8778 | 2882.5407 | 2878.8494 | 2871.8019 | 2888.8428 | 2884.7526 | 2876.9048 | 2895.3485 | 2890.8629 | 2882.223 | 2906.5736 | 2901.4334 | 2891.4862
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 28.6185 | 28.5966 | 28.5559 | 28.7259 | 28.6957 | 28.6388 | 28.8254 | 28.7885 | 28.718 | 28.8884 | 28.8475 | 28.769 | 28.9535 | 28.9086 | 28.8222 | 29.0657 | 29.0143 | 28.9149
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1815479.9959 | 1814163.9328 | 1811744.0491 | 1821896.7741 | 1820077.6483 | 1816669.5914 | 1827869.49 | 1825635.0621 | 1821401.3824 | 1831662.5026 | 1829181.7479 | 1824457.5775 | 1835585.5548 | 1832860.0599 | 1827649.1558 | 1842370.0342 | 1839238.2351 | 1833221.8588
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1815479.9959 | 1814163.9328 | 1811744.0491 | 1821896.7741 | 1820077.6483 | 1816669.5914 | 1827869.49 | 1825635.0621 | 1821401.3824 | 1831662.5026 | 1829181.7479 | 1824457.5775 | 1835585.5548 | 1832860.0599 | 1827649.1558 | 1842370.0342 | 1839238.2351 | 1833221.8588
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 6.2783 | 7.4713 | 8.2549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5022.6622 | 5977.0135 | 6603.9322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 4423087.5671 | 4313478.6421 | 4108425.7817 | 4939892.238 | 4796202.3555 | 4521056.7497 | 5397466.2904 | 5228725.2122 | 4900972.5112 | 5677700.3949 | 5495279.5851 | 5138652.6464 | 5959879.7553 | 5764636.7737 | 5380951.0098 | 6431184.9557 | 6216126.4182 | 5790761.353
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 663463.1351 | 647021.7963 | 616263.8673 | 740983.8357 | 719430.3533 | 678158.5125 | 809619.9436 | 784308.7818 | 735145.8767 | 851655.0592 | 824291.9378 | 770797.897 | 893981.9633 | 864695.5161 | 807142.6515 | 964677.7434 | 932418.9627 | 868614.2029
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 207878.4245 | 202726.9708 | 193089.7966 | 232167.4622 | 225414.2551 | 212482.8279 | 253672.7505 | 245742.1751 | 230338.2939 | 266843.3295 | 258269.8274 | 241508.9007 | 280105.3325 | 270929.2078 | 252896.5573 | 302255.964 | 292148.538 | 272157.0235
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'I'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 120 kN | 575.8943 | 2024 |  |  |  | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225 | 1165610.1225
| Insulators 160 kN | 690.7172 | 1152 |  |  |  | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163 | 795706.163
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681 | 619559.0681
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 72 |  |  |  | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805 | 52877.2805
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x condr) | 663.3085 | 192 |  |  |  | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348 | 127355.2348
V | ERECTION
2 | Stringing of Conductor (Route kM) | 266273.3924 | 100 |  |  |  | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389 | 26627339.2389
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 276547.3 | 269694.1568 | 256873.5165 | 308859.7817 | 299875.7749 | 282672.6847 | 337468.9528 | 326918.6553 | 306426.3808 | 354990.1941 | 343584.5908 | 321286.9954 | 372633.0599 | 360425.7684 | 336436.3582 | 402100.7516 | 388654.5204 | 362059.1708
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 8635070.7908 | 161773.7303 | 178816.3574 | 427808.4968 | 406868.0945 | 369104.4004 | 533621.453 | 503029.352 | 446969.8693 | 637056.877 | 597846.8818 | 525246.1337 | 704925.5863 | 660355.679 | 577426.6912 | 776735.8069 | 726678.3589 | 633164.2815 | 904441.1852 | 844963.6134 | 733279.7057
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 17974.8589 | 19868.4842 | 959452.3101 | 912488.9666 | 827795.7829 | 1196760.559 | 1128151.211 | 1002425.7976 | 1428736.682 | 1340799.8581 | 1177977.109 | 1580946.8191 | 1480989.2426 | 1295003.2008 | 1741996.6405 | 1629732.077 | 1420006.7017 | 2028403.3414 | 1895012.1299 | 1644537.013
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 143917.8465 | 2696.2288 | 2980.2726 | 120003.9655 | 114130.0024 | 103536.9612 | 149685.4105 | 141104.0628 | 125378.8954 | 178699.9372 | 167701.1961 | 147336.0613 | 197737.6943 | 185235.4517 | 161973.1568 | 217881.0792 | 203839.5342 | 177608.0306 | 253703.537 | 237019.5662 | 205691.2688
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 92107.4218 | 1725.5865 | 1907.3745 | 1049684.7676 | 998304.719 | 905646.4974 | 1309310.86 | 1234249.0912 | 1096699.7311 | 1563103.3625 | 1466896.4498 | 1288760.9054 | 1729628.2232 | 1620270.0568 | 1416792.8094 | 1905824.1035 | 1783001.5296 | 1553552.3642 | 2219166.151 | 2073230.0567 | 1799198.8077
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 363095999.1777 | 362832786.5596 | 362348809.8149 | 364379354.8112 | 364015529.6667 | 363333918.2793 | 365573898.0069 | 365127012.4211 | 364280276.483 | 366332500.5117 | 365836349.5822 | 364891515.5087 | 367117110.9522 | 366572011.9765 | 365529831.1657 | 368474006.8403 | 367847647.0166 | 366644371.7563
| Survey, Design, Supervision etc. | [5 empty] | 6051610.0848 | 6048977.9586 | 6044138.1911 | 6064443.6411 | 6060805.3897 | 6053989.2758 | 6076389.0731 | 6071920.2172 | 6063452.8578 | 6083975.0981 | 6079013.5888 | 6069565.2481 | 6091821.2025 | 6086370.2128 | 6075948.4046 | 6105390.1614 | 6099126.5632 | 6087093.8106
| TOTAL COST | [5 empty] | 369147609.2625 | 368881764.5182 | 368392948.0061 | 370443798.4523 | 370076335.0564 | 369387907.555 | 371650287.0799 | 371198932.6383 | 370343729.3408 | 372416475.6098 | 371915363.171 | 370961080.7568 | 373208932.1547 | 372658382.1893 | 371605779.5703 | 374579397.0017 | 373946773.5798 | 372731465.5669
| TOTAL COST IN RS. LAKHS | [5 empty] | 3691.4761 | 3688.8176 | 3683.9295 | 3704.438 | 3700.7634 | 3693.8791 | 3716.5029 | 3711.9893 | 3703.4373 | 3724.1648 | 3719.1536 | 3709.6108 | 3732.0893 | 3726.5838 | 3716.0578 | 3745.794 | 3739.4677 | 3727.3147
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 36.9148 | 36.8882 | 36.8393 | 37.0444 | 37.0076 | 36.9388 | 37.165 | 37.1199 | 37.0344 | 37.2416 | 37.1915 | 37.0961 | 37.3209 | 37.2658 | 37.1606 | 37.4579 | 37.3947 | 37.2731
ESTIMATE FOR A 765 KV, SC LINE WITH TWIN ACSR BERSIMIS MOOSE CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1070061.9075 | 1068631.1062 | 1065958.8657 | 1077432.605 | 1075490.136 | 1071805.6816 | 1084183.4474 | 1081827.4418 | 1077317.1779 | 1088428.8422 | 1085830.4602 | 1080835.8333 | 1092791.5933 | 1089954.1475 | 1084482.4825 | 1100279.3398 | 1097048.2128 | 1090793.4675
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1070061.9075 | 1068631.1062 | 1065958.8657 | 1077432.605 | 1075490.136 | 1071805.6816 | 1084183.4474 | 1081827.4418 | 1077317.1779 | 1088428.8422 | 1085830.4602 | 1080835.8333 | 1092791.5933 | 1089954.1475 | 1084482.4825 | 1100279.3398 | 1097048.2128 | 1090793.4675
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 33.3523 | 40.1376 | 44.6039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 5.0029 | 6.0206 | 6.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 4002.281 | 4816.5159 | 5352.4685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 5969732.8625 | 5828889.6017 | 5562345.1813 | 6676005.8618 | 6492879.3319 | 6139682.5939 | 7297034.6461 | 7082922.0989 | 6665181.5049 | 7676164.6287 | 7445119.1126 | 6991980.1598 | 8057306.2644 | 7810366.8671 | 7324017.3222 | 8692976.3697 | 8421417.8379 | 7883774.6479
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 895459.9294 | 874333.4403 | 834351.7772 | 1001400.8793 | 973931.8998 | 920952.3891 | 1094555.1969 | 1062438.3148 | 999777.2257 | 1151424.6943 | 1116767.8669 | 1048797.024 | 1208595.9397 | 1171555.0301 | 1098602.5983 | 1303946.4555 | 1263212.6757 | 1182566.1972
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 280568.4137 | 273948.9935 | 261421.8089 | 313762.1762 | 305155.5063 | 288555.7939 | 342949.5896 | 332886.6238 | 313253.4478 | 360768.1252 | 349909.3355 | 328612.4902 | 378681.2055 | 367075.4274 | 344217.7345 | 408556.7388 | 395793.8987 | 370525.4821
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 609 |  |  |  | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815 | 146305673.2815
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 1920 |  |  |  | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 203 |  |  |  | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534 | 309779.534
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 373249.1115 | 364443.0857 | 347777.7724 | 417407.8328 | 405958.1053 | 383874.9783 | 456236.78 | 442849.6955 | 416731.0552 | 479941.3464 | 465495.552 | 437163.6793 | 503771.6886 | 488332.1517 | 457923.8337 | 543516.0636 | 526537.2502 | 492921.8695
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 9942759.5821 | 0 | 0 | 410496.2517 | 391355.1568 | 356381.6002 | 513372.7584 | 485594.8413 | 434201.4211 | 613327.1889 | 577862.2596 | 511709.3612 | 678715.8036 | 638473.2428 | 563118.4743 | 747789.1243 | 702655.2068 | 617871.4476 | 870435.1072 | 816901.7618 | 715925.4555
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1104751.0647 | 1053237.4518 | 959114.6097 | 1381618.2222 | 1306860.6977 | 1168547.7766 | 1650621.3203 | 1555176.0677 | 1377141.592 | 1826598.9117 | 1718295.8233 | 1515496.7467 | 2012492.9956 | 1891026.0073 | 1662851.0899 | 2342564.9015 | 2198492.8909 | 1926739.6619
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 165712.6597 | 0 | 0 | 92118.1854 | 87822.7919 | 79974.485 | 115204.3819 | 108970.826 | 97437.7886 | 137634.8443 | 129676.27 | 114831.1041 | 152308.4997 | 143277.792 | 126367.6631 | 167809.0285 | 157680.6666 | 138654.6073 | 195331.6316 | 183318.3802 | 160658.6018
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 106056.1022 | 0 | 0 | 725188.9557 | 691374.0047 | 629589.1847 | 906932.1657 | 857859.2724 | 767066.8704 | 1083513.1911 | 1020860.3046 | 903993.5826 | 1199029.7177 | 1127936.5945 | 994813.708 | 1321055.7024 | 1241321.4336 | 1091541.1479 | 1537723.9713 | 1443151.1447 | 1264764.8578
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 214012381.4909 | 213726221.2428 | 213191773.1359 | 215486520.9947 | 215098027.1972 | 214361136.3283 | 216836689.4737 | 216365488.3513 | 215463435.5899 | 217685768.4437 | 217166092.036 | 216167166.6617 | 218558318.6654 | 217990829.5071 | 216896496.4978 | 220055867.9555 | 219409642.5564 | 218158693.4901
| Survey, Design, Supervision etc. | [5 empty] | 4560773.9079 | 4557912.3054 | 4552567.8243 | 4575515.3029 | 4571630.365 | 4564261.4563 | 4589016.9877 | 4584304.9765 | 4575284.4489 | 4597507.7774 | 4592311.0133 | 4582321.7596 | 4606233.2796 | 4600558.3881 | 4589615.058 | 4621208.7725 | 4614746.5186 | 4602237.0279
| TOTAL COST | [5 empty] | 218573155.3988 | 218284133.5482 | 217744340.9603 | 220062036.2976 | 219669657.5621 | 218925397.7846 | 221425706.4615 | 220949793.3278 | 220038720.0388 | 222283276.2212 | 221758403.0493 | 220749488.4213 | 223164551.945 | 222591387.8951 | 221486111.5558 | 224677076.7281 | 224024389.0749 | 222760930.518
| TOTAL COST IN RS. LAKHS | [5 empty] | 2185.7316 | 2182.8413 | 2177.4434 | 2200.6204 | 2196.6966 | 2189.254 | 2214.2571 | 2209.4979 | 2200.3872 | 2222.8328 | 2217.584 | 2207.4949 | 2231.6455 | 2225.9139 | 2214.8611 | 2246.7708 | 2240.2439 | 2227.6093
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 21.8573 | 21.8284 | 21.7744 | 22.0062 | 21.967 | 21.8925 | 22.1426 | 22.095 | 22.0039 | 22.2283 | 22.1758 | 22.0749 | 22.3165 | 22.2591 | 22.1486 | 22.4677 | 22.4024 | 22.2761
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH TRIPPLE ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1448327.6402 | 1446475.6883 | 1443088.0896 | 1457714.5001 | 1455181.9843 | 1450472.5714 | 1466368.7516 | 1463281.345 | 1457483.3849 | 1471833.08 | 1468418.7678 | 1461978.9467 | 1477463.467 | 1473725.6611 | 1466651.6077 | 1487157.6235 | 1482885.1127 | 1474766.1135
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1448327.6402 | 1446475.6883 | 1443088.0896 | 1457714.5001 | 1455181.9843 | 1450472.5714 | 1466368.7516 | 1463281.345 | 1457483.3849 | 1471833.08 | 1468418.7678 | 1461978.9467 | 1477463.467 | 1473725.6611 | 1466651.6077 | 1487157.6235 | 1482885.1127 | 1474766.1135
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 7079406.516 | 6909119.698 | 6593003.4193 | 7917117.9139 | 7695100.9009 | 7274487.9431 | 8655463.3523 | 8395530.4648 | 7896973.51 | 9106671.6487 | 8826033.7497 | 8284748.2741 | 9560493.065 | 9260434.806 | 8679092.7753 | 10317675.9463 | 9987565.9822 | 9344435.5613
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1061910.9774 | 1036367.9547 | 988950.5129 | 1187567.6871 | 1154265.1351 | 1091173.1915 | 1298319.5028 | 1259329.5697 | 1184546.0265 | 1366000.7473 | 1323905.0625 | 1242712.2411 | 1434073.9597 | 1389065.2209 | 1301863.9163 | 1547651.3919 | 1498134.8973 | 1401665.3342
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 332721.3967 | 324718.1738 | 309861.187 | 372092.5651 | 361658.1014 | 341889.9286 | 406793.6838 | 394577.2313 | 371145.8086 | 427999.7911 | 414810.2344 | 389370.6359 | 449328.7112 | 435226.4269 | 407904.2309 | 484915.1611 | 469400.4922 | 439174.3353
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 913.5 |  |  |  | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223 | 219458509.9223
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 1920 |  |  |  | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 304.5 |  |  |  | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301 | 464669.301
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190630.2522 | 100 |  |  |  | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221 | 19063025.2221
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 442629.8886 | 431982.946 | 412218.2224 | 495006.61 | 481125.31 | 454827.0792 | 541170.6152 | 524918.6788 | 493747.1097 | 569381.7764 | 551835.2883 | 517992.1788 | 597756.3191 | 578995.6005 | 542648.0115 | 645098.1088 | 624458.4498 | 584247.629
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 13982693.7486 | 0 | 0 | 577288.7622 | 549850.766 | 500686.6397 | 721994.0645 | 682068.5717 | 609542.873 | 862938.8959 | 811887.1817 | 718324.6391 | 955253.7619 | 897285.3323 | 790602.2307 | 1052834.1964 | 987784.3888 | 867656.9752 | 1226205.2412 | 1148996.5478 | 1005785.9114
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 1553632.6387 | 1479789.929 | 1347476.6116 | 1943071.8506 | 1835622.0736 | 1640436.7523 | 2322390.6675 | 2184997.3652 | 1933196.4824 | 2570833.7316 | 2414825.7679 | 2127714.084 | 2833447.7954 | 2658382.021 | 2335088.2334 | 3300033.8983 | 3092245.433 | 2706828.7515
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 233044.8958 | 0 | 0 | 129547.5733 | 123390.298 | 112357.5295 | 162020.4395 | 153060.884 | 136785.6178 | 193649.4301 | 182193.0739 | 161196.9951 | 214365.5217 | 201357.007 | 177416.5844 | 236263.2431 | 221665.6184 | 194708.1996 | 275168.8993 | 257842.7369 | 225705.284
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 149148.7333 | 0 | 0 | 1019847.1554 | 971374.7717 | 884520.6744 | 1275485.7553 | 1204952.7691 | 1076827.7608 | 1524481.0497 | 1434292.3108 | 1269003.2922 | 1687565.9038 | 1585157.9896 | 1396689.9909 | 1859952.9915 | 1745035.0067 | 1532816.0809 | 2166232.9305 | 2029834.8722 | 1776836.7718
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 289665528.0326 | 289295137.6613 | 288617617.921 | 291542900.0103 | 291036396.8699 | 290094514.2706 | 293273750.3215 | 292656269.0003 | 291496676.9878 | 294366616.0069 | 293683753.556 | 292395789.3443 | 295492693.4057 | 294745132.2134 | 293330321.5474 | 297431524.7017 | 296577022.5356 | 294953222.7028
| Survey, Design, Supervision etc. | [5 empty] | 5317305.3733 | 5313601.4696 | 5306826.2722 | 5336079.0931 | 5331014.0617 | 5321595.2357 | 5353387.5962 | 5347212.783 | 5335616.8629 | 5364316.2531 | 5357487.6285 | 5344607.9864 | 5375577.027 | 5368101.4151 | 5353953.3085 | 5394965.34 | 5386420.3183 | 5370182.32
| TOTAL COST | [5 empty] | 294982833.4059 | 294608739.1309 | 293924444.1932 | 296878979.1034 | 296367410.9316 | 295416109.5063 | 298627137.9177 | 298003481.7833 | 296832293.8507 | 299730932.2599 | 299041241.1846 | 297740397.3307 | 300868270.4328 | 300113233.6286 | 298684274.8558 | 302826490.0417 | 301963442.854 | 300323405.0228
| TOTAL COST IN RS. LAKHS | [5 empty] | 2949.8283 | 2946.0874 | 2939.2444 | 2968.7898 | 2963.6741 | 2954.1611 | 2986.2714 | 2980.0348 | 2968.3229 | 2997.3093 | 2990.4124 | 2977.404 | 3008.6827 | 3001.1323 | 2986.8427 | 3028.2649 | 3019.6344 | 3003.2341
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 29.4983 | 29.4609 | 29.3924 | 29.6879 | 29.6367 | 29.5416 | 29.8627 | 29.8003 | 29.6832 | 29.9731 | 29.9041 | 29.774 | 30.0868 | 30.0113 | 29.8684 | 30.2826 | 30.1963 | 30.0323
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD ACSR BERSIMIS CONDUCTOR FOR A 100 kM LENGTH
HILLY AREA
| Particulars |  | Total Quantity | Unit weight (kG) |  |  | WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3 | TERRAIN CATEGORY-1 | TERRAIN CATEGORY-2 | TERRAIN CATEGORY-3
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 1954374.39 | 1952128.7317 | 1948068.4897 | 1965664.0994 | 1962578.1296 | 1956902.9459 | 1976119.5067 | 1972344.0137 | 1965329.9796 | 1982739.6547 | 1978556.3811 | 1970749.7812 | 1989573.8978 | 1984986.1113 | 1976394.4136 | 2001367.6411 | 1996109.3676 | 1986220.5182
III | Detailed survey (Rs. Per kM) | 14097.2947 | 100 |  |  |  | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679 | 1409729.4679
| Check Survey | 10109.2063 | 100 |  |  |  | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251 | 1010920.6251
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 1954374.39 | 1952128.7317 | 1948068.4897 | 1965664.0994 | 1962578.1296 | 1956902.9459 | 1976119.5067 | 1972344.0137 | 1965329.9796 | 1982739.6547 | 1978556.3811 | 1970749.7812 | 1989573.8978 | 1984986.1113 | 1976394.4136 | 2001367.6411 | 1996109.3676 | 1986220.5182
2 | Supply of tower parts
| a) 'A' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'B' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) 'C' Type towers | 71585.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) 'D' Type towers | 71585.8528 | 4 | 0 | 0 | 0 | 8037305.6921 | 7841933.1808 | 7483027.7467 | 8988462.4858 | 8733365.5444 | 8254734.8422 | 9827887.7211 | 9529012.4415 | 8961012.0379 | 10341152.4323 | 10018380.3532 | 9401399.9689 | 10857526.0097 | 10512348.6907 | 9849470.6999 | 11719259.1788 | 11339429.8841 | 10605802.6202
| e) Extension pieces @ 15% of the above total tonnage | 71585.8528 |  | 0 | 0 | 0 | 1205595.8538 | 1176289.9771 | 1122454.162 | 1348269.3729 | 1310004.8317 | 1238210.2263 | 1474183.1582 | 1429351.8662 | 1344151.8057 | 1551172.8649 | 1502757.053 | 1410209.9953 | 1628628.9015 | 1576852.3036 | 1477420.605 | 1757888.8768 | 1700914.4826 | 1590870.393
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 97519.6171 |  |  |  |  | 377741.2089 | 368558.9964 | 351690.9839 | 422444.1393 | 410454.9689 | 387960.05 | 461895.8555 | 447849.1695 | 421154.0098 | 486018.5205 | 470848.721 | 441851.5763 | 510287.2974 | 494064.4856 | 462910.2228 | 550787.4528 | 532936.0505 | 498456.6789
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 184.967 | 4 |  |  |  | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682 | 739.8682
| b) Number plate (one per tower) | 186.2396 | 4 |  |  |  | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583 | 744.9583
| c) Phase plate (set of three per tower) x No. of Ckts. | 210.9895 | 4 |  |  |  | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579 | 843.9579
| d) Anti climbing device (one set per tower) | 6448.8813 | 4 |  |  |  | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251 | 25795.5251
| e) Circuit plate (one per circuit in case of two or more ckt) | 178.9234 | 4 |  |  |  | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935 | 715.6935
| d) Supply of pipe type earthing (60% of total No.) | 1882.5193 | 2.4 |  |  |  | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463 | 4518.0463
| e) Supply of Counter poise earthing (40% of total No.) | 5624.3163 | 1.6 |  |  |  | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061 | 8998.9061
4 | Supply of ACSR Bersimis Conductor (kM) | 240239.2008 | 1218 |  |  |  | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631 | 292611346.5631
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 35606.9429 | 203 |  |  |  | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056 | 7228209.4056
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of 'A' Towers) | 17611.7014 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 2) x Ckts | 8685.7559 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 14016.0961 | 8 |  |  |  | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687 | 112128.7687
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 13103.389 | 24 |  |  |  | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366 | 314481.3366
| e) Double 'V'' suspn. Insulator string (Special Locations) | 16318.8337 | 40 |  |  |  | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496 | 652753.3496
| Insulators 160 kN | 690.7172 | 5880 |  |  |  | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735 | 4061416.8735
| Insulators 210 kN | 756.5845 | 1920 |  |  |  | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649 | 1452642.2649
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1526.0076 | 406 |  |  |  | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523 | 29063856.2523
| b) Mid span compression joint for GW (one No. for 8 kM) | 210.2973 | 25.375 |  |  |  | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932 | 5336.2932
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 352.077 | 200 |  |  |  | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985 | 70415.3985
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 278.718 | 8 |  |  |  | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443 | 2229.7443
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 734.4067 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) Spacer damper for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 698.1584 | 48 |  |  |  | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018 | 33511.6018
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 278.718 | 16 |  |  |  | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887 | 4459.4887
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 214.5564 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 229.3749 | 16 |  |  |  | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986 | 3669.9986
| j) Vibration dampers for conductor (No. towersx4xCktsx3x Condr) | 663.3085 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 163660.9478 | 100 |  |  |  | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777 | 16366094.777
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3892.0037 |  |  |  |  | 502521.181 | 490305.7909 | 467865.7357 | 561990.9155 | 546041.3397 | 516115.6314 | 614474.7922 | 595788.0377 | 560274.615 | 646565.943 | 626385.0748 | 587809.2481 | 678851.4712 | 657269.7471 | 615824.2374 | 732730.1199 | 708981.83 | 663112.822
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 294 |  | 18022627.9152 | 0 | 0 | 744081.2728 | 708346.3752 | 644991.6793 | 930615.3706 | 878542.302 | 784884.325 | 1112550.6028 | 1045912.1038 | 924939.917 | 1231791.7203 | 1156097.4219 | 1018085.9872 | 1357879.2685 | 1272913.5707 | 1117442.5029 | 1581975.3752 | 1481091.3339 | 1295646.3673
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5934.2225 |  |  | 0 | 0 | 2002514.2128 | 1906342.4062 | 1735838.6135 | 2504525.4791 | 2364383.4494 | 2112325.728 | 2994160.0146 | 2814818.6627 | 2489251.3728 | 3315068.5515 | 3111355.7126 | 2739931.4213 | 3654402.5953 | 3425738.0347 | 3007325.3769 | 4257502.8951 | 3985997.9751 | 3486917.8411
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4948.1718 |  | 300377.1319 | 0 | 0 | 166976.9611 | 158957.804 | 144740.574 | 208836.497 | 197150.9419 | 176133.447 | 249664.0159 | 234709.8779 | 207562.8862 | 276422.5437 | 259436.2219 | 228465.5057 | 304717.4577 | 285650.5701 | 250761.792 | 355006.1671 | 332367.0936 | 290751.9662
4 | Reinforcements (4% of weight of M20) in MT | 54102.5933 |  | 192241.3644 | 0 | 0 | 1314505.3552 | 1251375.5387 | 1139452.164 | 1644039.3449 | 1552046.2657 | 1386588.6512 | 1965448.9083 | 1847724.3169 | 1634013.0018 | 2176102.09 | 2042379.3848 | 1798566.2739 | 2398850.2807 | 2248748.5798 | 1974091.0139 | 2794741.8897 | 2616518.5997 | 2288908.6858
5 | Benching
| a) All kinds of soil except fissured rock | 126.7554 | 3000 | 1500 | 1500 | 1500 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177 | 380266.177
| b) Fissured rock | 752.9865 | 10000 | 4000 | 4000 | 4000 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018 | 7529865.3018
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 3053.7228 | 3000 | 1500 | 1500 | 1500 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434 | 9161168.5434
| b) 1:2:4 Cement Concrete revetment | 4927.4272 | 1000 | 100 | 100 | 100 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177 | 4927427.177
| c) Back filling and levelling (Included above) | 135.269
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 390874878.0088 | 390425746.3403 | 389613697.9303 | 393132819.8762 | 392515625.9148 | 391380589.1723 | 395223901.3396 | 394468802.7473 | 393065995.9172 | 396547930.9372 | 395711276.2143 | 394149956.248 | 397914779.5531 | 396997222.2535 | 395278882.7219 | 400273528.2266 | 399221873.5206 | 397244103.6456
| Survey, Design, Supervision etc. | [5 empty] | 6329398.8731 | 6324907.5564 | 6316787.0723 | 6351978.2917 | 6345806.3521 | 6334455.9847 | 6372889.1064 | 6365338.1205 | 6351310.0522 | 6386129.4024 | 6377762.8551 | 6362149.6555 | 6399797.8885 | 6390622.3155 | 6373438.9202 | 6423385.3753 | 6412868.8282 | 6393091.1294
| TOTAL COST | [5 empty] | 397204276.8819 | 396750653.8967 | 395930485.0026 | 399484798.168 | 398861432.267 | 397715045.157 | 401596790.446 | 400834140.8677 | 399417305.9694 | 402934060.3396 | 402089039.0695 | 400512105.9034 | 404314577.4416 | 403387844.569 | 401652321.6421 | 406696913.6018 | 405634742.3488 | 403637194.7751
| TOTAL COST IN RS. LAKHS | [5 empty] | 3972.0428 | 3967.5065 | 3959.3049 | 3994.848 | 3988.6143 | 3977.1505 | 4015.9679 | 4008.3414 | 3994.1731 | 4029.3406 | 4020.8904 | 4005.1211 | 4043.1458 | 4033.8784 | 4016.5232 | 4066.9691 | 4056.3474 | 4036.3719
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 39.7204 | 39.6751 | 39.593 | 39.9485 | 39.8861 | 39.7715 | 40.1597 | 40.0834 | 39.9417 | 40.2934 | 40.2089 | 40.0512 | 40.4315 | 40.3388 | 40.1652 | 40.6697 | 40.5635 | 40.3637
SAMPLE ESTIMATE FOR A 400 KV, DC LINE WITH QUAD ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 13440252.5658 | 14117921.7674 | 14547211.5918
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 7906030.9211 | 8304659.8632 | 8557183.2893
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 7906030.9211 | 8304659.8632 | 8557183.2893
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 16508.0925 | 18532.0288 | 19750.7674 | 208001965.4743 | 233503562.6456 | 248859669.4525
| b) 'B' Type towers | 60000 | 25 | 22935.8387 | 25336.28 | 26798.9755 | 34403758.1069 | 38004420.0232 | 40198463.2127
| c) 'C' Type towers | 60000 | 25 | 27367.7998 | 30022.8969 | 31649.2306 | 41051699.6895 | 45034345.3439 | 47473845.9071
| d) 'D' Type towers | 60000 | 20 | 30499.6211 | 33278.2668 | 34987.2913 | 36599545.2934 | 39933920.1689 | 41984749.5951
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 12199.8484 | 13311.3067 | 13994.9165 | 731990.9059 | 798678.4034 | 839694.9919
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 281816.4988 | 307491.1853 | 323282.5719
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) x No. of Ckts. | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 560 |  |  |  | 170800 | 170800 | 170800
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 2436 |  |  |  | 876960000 | 876960000 | 876960000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) x Ckts | 21000 | 1680 |  |  |  | 35280000 | 35280000 | 35280000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 40 |  |  |  | 1240000 | 1240000 | 1240000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 840 |  |  |  | 49560000 | 49560000 | 49560000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 40 |  |  |  | 1800000 | 1800000 | 1800000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 812 |  |  |  | 1055600 | 1055600 | 1055600
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 5040 | 10080 |  |  |  | 50803200 | 50803200 | 50803200
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 1680 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 0 |  |  |  | 0 | 0 | 0
V | ERECTION
2 | Stringing of Conductor (Route kM) | 380000 | 100 |  |  |  | 38000000 | 38000000 | 38000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 483113.9979 | 527127.7462 | 554198.6947
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 115410.7813 | 142601.7111 | 160477.2053 | 34623234.3997 | 42780513.3387 | 48143161.6025
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 12823.4201 | 15844.6346 | 17830.8006 | 73093494.8437 | 90314417.0484 | 101635563.383
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 1923.513 | 2376.6952 | 2674.6201 | 9040511.2044 | 11170467.3718 | 12570714.4184
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 1231.0483 | 1521.0849 | 1711.7569 | 66476610.0474 | 82138585.6103 | 92434870.2767
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 1581206184.2118 | 1660931972.6358 | 1711436657.8564
| Survey, Design, Supervision etc. | [5 empty] | 35252314.4079 | 36727241.4938 | 37661578.1703
| TOTAL COST | [5 empty] | 1616458498.6197 | 1697659214.1296 | 1749098236.0267
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 290962529.7515 | 305578658.5433 | 314837682.4848
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 48493754.9586 | 50929776.4239 | 52472947.0808
v) | Contengency at 3% | [5 empty] | 48493754.9586 | 50929776.4239 | 52472947.0808
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 2004408538.2884 | 2105097425.5207 | 2168881812.6732
| TOTAL COST IN RS. LAKHS | [5 empty] | 20044.0854 | 21050.9743 | 21688.8181
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 200.4409 | 210.5097 | 216.8882
SAMPLE ESTIMATE FOR A 765 KV, SC LINE WITH QUAD MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 8515676.9446 | 9047312.8003 | 9377441.1242
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 5009221.7321 | 5321948.706 | 5516141.8378
III | Detailed survey (Rs. Per kM) | 50000 | 100 |  |  |  | 5000000 | 5000000 | 5000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 5009221.7321 | 5321948.706 | 5516141.8378
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 16508.0925 | 18532.0288 | 19750.7674 | 208001965.4743 | 233503562.6456 | 248859669.4525
| b) 'B' Type towers | 60000 | 25 | 22935.8387 | 25336.28 | 26798.9755 | 34403758.1069 | 38004420.0232 | 40198463.2127
| c) 'C' Type towers | 60000 | 25 | 27367.7998 | 30022.8969 | 31649.2306 | 41051699.6895 | 45034345.3439 | 47473845.9071
| d) 'D' Type towers | 60000 | 20 | 30499.6211 | 33278.2668 | 34987.2913 | 36599545.2934 | 39933920.1689 | 41984749.5951
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 533428.2809 | 594127.0803 | 630861.2136 | 32005696.8564 | 35647624.8182 | 37851672.8167
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 12322193.2897 | 13724335.555 | 14572894.0344
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 1218 |  |  |  | 438480000 | 438480000 | 438480000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings (No. of suspn.x1) | 24000 | 210 |  |  |  | 5040000 | 5040000 | 5040000
| b) Double 'I' Suspension Insulator Sring (No. Suspn. X 2) | 21000 | 420 |  |  |  | 8820000 | 8820000 | 8820000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Quad Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'V' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
| f) Single 'I' Suspension Pilot strings (No. of Suspn x 1) | 15000 | 210 |  |  |  | 3150000 | 3150000 | 3150000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 406 |  |  |  | 527800 | 527800 | 527800
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Quad spacer damper for Conductor (6x No. of towers x 3 x Ckts) | 2700 | 5040 |  |  |  | 13608000 | 13608000 | 13608000
| f) Quad Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 1000 | 840 |  |  |  | 840000 | 840000 | 840000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
V | ERECTION
2 | Stringing of Conductor (Route kM) | 190000 | 100 |  |  |  | 19000000 | 19000000 | 19000000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 21123759.9252 | 23527432.38 | 24982104.059
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 50354.7034 | 62119.3722 | 69860.8386 | 15106411.0092 | 18635811.6465 | 20958251.5755
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 5594.967 | 6902.1525 | 7762.3154 | 31891312.1305 | 39342269.0315 | 44245197.7704
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 839.2451 | 1035.3229 | 1164.3473 | 3944451.7635 | 4866017.4855 | 5472432.3558
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 537.1168 | 662.6066 | 745.1823 | 29004309.1376 | 35780758.3613 | 40239843.0249
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 1001844346.4263 | 1064389741.2095 | 1103228367.5542
| Survey, Design, Supervision etc. | [5 empty] | 23534120.4089 | 24691210.2124 | 25409724.7998
| TOTAL COST | [5 empty] | 1025378466.8352 | 1089080951.4219 | 1128638092.354
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 184568124.0303 | 196034571.2559 | 203154856.6237
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 30761354.0051 | 32672428.5427 | 33859142.7706
v) | Contengency at 3% | [5 empty] | 30761354.0051 | 32672428.5427 | 33859142.7706
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 1271469298.8756 | 1350460379.7632 | 1399511234.5189
| TOTAL COST IN RS. LAKHS | [5 empty] | 12714.693 | 13504.6038 | 13995.1123
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 127.1469 | 135.046 | 139.9511
SAMPLE ESTIMATE FOR A 400 KV, SC LINE WITH TWIN ACSR MOOSE CONDUCTOR FOR A 100 kM LENGTH
TERRAIN CATEGORY-2
Sl.No, | Particulars | Unit Rate | PLAIN AREA (Predominantly Normal Soil)
|  |  | Total Quantity | Unit weight (kG) |  |  | Total cost Rs.
|  |  |  | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4 | WIND ZONE-2 | WIND ZONE-3 | WIND ZONE-4
| Total Length of the Line kMs | [5 empty] | 100 | 100 | 100
I | Preliminary studies such as Load flow, stability analysis, EMTS, Protection coordination, Reactive compensation etc, Detailed Engg. Supervision etc. at 0.85% of total cost | 0.85 |  |  |  |  | 5112135.9979 | 5437165.8013 | 5637373.8804
II | Statutory clearances and charges. (% of total cost) | 0.5 |  |  |  |  | 3007138.8223 | 3198332.8243 | 3316102.2826
III | Detailed survey (Rs. Per kM) | 60000 | 100 |  |  |  | 6000000 | 6000000 | 6000000
IV | SUPPLY OF MATERIALS
1 | Design and testing of towers (% of total cost) | 0.5 |  |  |  |  | 3007138.8223 | 3198332.8243 | 3316102.2826
2 | Supply of tower parts
| a) 'A' Type towers | 60000 | 210 | 10736.956 | 12057.6633 | 12852.409 | 135285646.115 | 151926557.0846 | 161940353.7345
| b) 'B' Type towers | 60000 | 25 | 17132.487 | 18950.123 | 20054.3624 | 25698730.4451 | 28425184.472 | 30081543.5696
| c) 'C' Type towers | 60000 | 25 | 20389.7437 | 22403.5518 | 23631.9916 | 30584615.5102 | 33605327.7254 | 35447987.415
| d) 'D' Type towers | 60000 | 20 | 25511.93 | 27885.7649 | 29338.4186 | 30614316.0205 | 33462917.8931 | 35206102.353
| e) Extension pieces @ 10% of the above total tonnage | 60000 |  | 370305.5135 | 412366.6453 | 437793.3118 | 22218330.8091 | 24741998.7175 | 26267598.7072
| f) Supply of Bolts and Nuts (3% of total tower Wt. Of towers) | 70000 |  |  |  |  | 7332049.167 | 8164859.5768 | 8668307.5734
3 | Supply of tower accessories
| a) Danger plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| b) Number plate (one per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| c) Phase plate (set of three per tower) | 305 | 280 |  |  |  | 85400 | 85400 | 85400
| d) Anti climbing device (one set per tower) | 5400 | 280 |  |  |  | 1512000 | 1512000 | 1512000
| e) Circuit plate (one per circuit in case of two or more ckt) | 305 | 0 |  |  |  | 0 | 0 | 0
| d) Supply of pipe type earthing (60% of total No.) | 3100 | 168 |  |  |  | 520800 | 520800 | 520800
| e) Supply of Counter poise earthing (40% of total No.) | 6100 | 112 |  |  |  | 683200 | 683200 | 683200
4 | Supply of ACSR Moose Conductor (kM) | 360000 | 609 |  |  |  | 219240000 | 219240000 | 219240000
(=Route kM x 3 x No. of Ckts x No. of sub Condrs x 1.015)
5 | Supply of 7/3.66mm GSS Ground wire (kM) | 42000 | 203 |  |  |  | 8526000 | 8526000 | 8526000
(=Route kM x 2 x 1.015)
6 | Supply of Insulators with Hardware
| a) Single 'V' suspension Insulator strings | 24000 | 0 |  |  |  | 0 | 0 | 0
| b) 'I' Suspension Insulator Sring (No. Suspn. X 3) | 21000 | 840 |  |  |  | 17640000 | 17640000 | 17640000
| c) Single 'I' suspn. Pilot string (No. of 'D' type x 1) | 31000 | 20 |  |  |  | 620000 | 620000 | 620000
| d) Double Tension string (No. of anchor x 2 x 3 x No. of Ckts) | 59000 | 420 |  |  |  | 24780000 | 24780000 | 24780000
| e) Double 'I' suspn. Insulator string (Special Locations) | 45000 | 20 |  |  |  | 900000 | 900000 | 900000
7 | Supply of Conductor and GW Accessories
| a) Mid span compression Joint for condr. (one No. for 3 kM) | 1300 | 203 |  |  |  | 263900 | 263900 | 263900
| b) Mid span compression joint for GW (one No. for 8 kM) | 250 | 25.375 |  |  |  | 6343.75 | 6343.75 | 6343.75
| c) Repair sleeves for Conductor (2 Nos. for every Route kM) | 750 | 200 |  |  |  | 150000 | 150000 | 150000
| d) Flexible copper Earth bonds (2x 'A' type + 2x2xNo. of Anchor) | 290 | 350 |  |  |  | 101500 | 101500 | 101500
| e) Bundle Spacers for Conductor (6x No. of towers x 3 x Ckts) | 900 | 5040 |  |  |  | 4536000 | 4536000 | 4536000
| f) Rigid spacer for Conductor (2 x No. of anchor x 2 x 3x Ckts) | 500 | 840 |  |  |  | 420000 | 420000 | 420000
| g) Vibration Damper for GW (No. Of towers x 2 x2) | 320 | 1120 |  |  |  | 358400 | 358400 | 358400
| h) Earth wire suspension clamp ( No. 'A' towers x 2) | 620 | 420 |  |  |  | 260400 | 260400 | 260400
| I) Earth wire tension clamps (No. of Anchor x 2 x 2) | 620 | 280 |  |  |  | 173600 | 173600 | 173600
| j) Vibration dampers for conductor (No. towersx4xCktsx3) | 900 | 3360 |  |  |  | 3024000 | 3024000 | 3024000
V | ERECTION
2 | Stringing of Conductor (Route kM) | 95000 | 100 |  |  |  | 9500000 | 9500000 | 9500000
| Stringing of GW (Route kM) | 25000 | 100 |  |  |  | 2500000 | 2500000 | 2500000
2 | Erection of Tower parts (Rate x total tonnage) | 3600 |  |  |  |  | 12569227.1434 | 13996902.1316 | 14859955.8401
VI | CIVIL WORKS |  |  | Total Quantity
1 | Excavations (9 times M20 concrete) | 300 |  | 22408.6745 | 27584.8038 | 30989.6684 | 6722602.3397 | 8275441.1414 | 9296900.5279
2 | M20 Concrete (1:1½:3 Concrete) (Cu.M) | 5700 |  | 2489.8527 | 3064.9782 | 3443.2965 | 14192160.4949 | 17470375.7429 | 19626790.0033
3 | 1:3:6 Concrete (15% of M20 Concrete) in Cu.M | 4700 |  | 373.4779 | 459.7467 | 516.4945 | 1755346.1665 | 2160809.6314 | 2427524.0267
4 | Reinforcements (4% of weight of M20) in MT | 54000 |  | 239.0259 | 294.2379 | 330.5565 | 12907396.4922 | 15888846.9915 | 17850049.0136
5 | Benching
| a) All kinds of soil except fissured rock | 110 |  | 1500 | 1500 | 1500 | 165000 | 165000 | 165000
| b) Fissured rock | 320 |  | 4000 | 4000 | 4000 | 1280000 | 1280000 | 1280000
6 | Revetment works
| a) Random Rubble Masonry (1:5 cement mortar) in Cu.M | 2300 |  | 1500 | 1500 | 1500 | 3450000 | 3450000 | 3450000
| b) 1:2:4 Cement Concrete revetment | 4300 |  | 100 | 100 | 100 | 430000 | 430000 | 430000
| c) Back filling and levelling | 100 |  | 2500 | 2500 | 2500 | 250000 | 250000 | 250000
VII | Supervision of construction, testing and commissioning
| Total cost of construction of the line (IV to VII) excluding survey and design etc. | [5 empty] | 601427764.4534 | 639666564.8581 | 663220456.5143
| Survey, Design, Supervision etc. | [5 empty] | 17126413.6424 | 17833831.4499 | 18269578.4455
| TOTAL COST | [5 empty] | 618554178.0958 | 657500396.308 | 681490034.9598
VIII | OTHER EXPENSES
i) | Interest during construction (12% for 18 months) | [5 empty] | 111339752.0572 | 118350071.3354 | 122668206.2928
ii) | ED VAT etc. at | [5 empty] | As per actuals. In the present case it is included
iii) | Service tax | [5 empty] | As per actuals. In the present case it is included
iv | Insurance and Trasportation charges at 3% | [5 empty] | 18556625.3429 | 19725011.8892 | 20444701.0488
v) | Contengency at 3% | [5 empty] | 18556625.3429 | 19725011.8892 | 20444701.0488
vi) | Hilly area weightage at 6% of erection
| TOTAL COST | [5 empty] | 767007180.8388 | 815300491.4219 | 845047643.3502
| TOTAL COST IN RS. LAKHS | [5 empty] | 7670.0718 | 8153.0049 | 8450.4764
| COST PER KM OF THE LINE Rs. Lakhs | [5 empty] | 76.7007 | 81.53 | 84.5048

## Assumptions made
NUMBER OF TOWERS AND PERCENTAGE OF TOWERS ASSUMED (100 KM LINE)
|  | Normal, Plain terrain |  | Hilly Terrain |  | Very Hilly Terrain
Sl.No. | Particulars | Number | Percentage | Number | Percentage | Number | Percentage
1 | 'A' TYPE TOWERS | 210 | 75 | 70 | 25 | 29 | 5
2 | 'B' TYPE TOWERS | 25 | 8.9286 | 90 | 32.1429 | 100 | 35.0877
3 | 'C' TYPE TOWERS | 25 | 8.9286 | 45 | 16.0714 | 70 | 24.5614
4 | 'D' TYPE TOWERS | 20 | 7.1429 | 80 | 28.5714 | 86 | 35
| TOTAL | 280 | 100 | 285 | 101.7857 | 285 | 100
TYPES OF FOUNDATIONS ASSUMED (100 KM LINE)
Sl.No. | Particulars | Number | Percentage | Hilly Terrain |  | Very Hilly Terrain
1 | Normal Dry soil | 85 | 30.3571 | 14 | 5 | 14 | 5
2 | Wet Black Cotton soil | 50 | 17.8571 | 14 | 5 | 14 | 5
3 | Dry Fissured Rock | 83 | 29.6429 | 85 | 30 | 85 | 30
4 | Submerged Fissured Rock | 40 | 14.2857 | 142 | 50 | 142 | 50
5 | Wet soil | 22 | 7.8571 | 30 | 10 | 30 | 10
| TOTAL | 280 | 100 | 285 | 100 | 285 | 100
| SFR, WBC, Wet and other high vol fdns. |  | 40 |  | 65 |  | 65
| Normal Dry, DFR and other low vol fdns. |  | 60 |  | 35 |  | 35
VOLUMES AND WEIGHTS OF FOUNDATIONS ASSUMED
Sl.No. | Particulars | M20 Concrete | 1:03 | Reinforcements | Excavations-Times M20
400 kV
1 | Normal Dry soil | 2.5 | 15 | 5 | 9
2 | Wet and Partially submerged | 4.5 | 15 | 5 | 9
3 | Fully submerged, Submerged fissured rock, WBC | 6.5 | 15 | 5 | 9
765 kV
1 | Normal Dry soil | 4 | 10 | 3 | 7.5
2 | Wet and Partially submerged | 7.75 | 10 | 3 | 7.5
3 | Fully submerged, Submerged fissured rock, WBC | 11 | 10 | 3 | 7.5
i) | M20: Percentage of total overturning moments.
ii) | 1:3:6: Percentage of M20
iii) | Reinforcements: Percentage of weight of M20 concrete
TOWER GEOMETRY
| Particulars | 400 kV, DC | 400 kV,SC | 765 kV, SC
i) | Height of Ground wire in Mtrs. | 46.5 | 32 | 38
ii) | Height of top conductor in Mtrs. | 38.5 | 22 | 27
iii) | Height of Middle conductor in Mtrs. | 30.5 | -- | --
| Height of Bottom conductor in Mtrs. | 22.5 | -- | --
Value of 'K' assumed in Ryle's formula
| Particulars | 400 kV, DC | 400 kV,SC | 765 kV, SC | 400 kV, Quad
i) | 'A' TYPE TOWER | 0.25 | 0.38 | 0.52 | 0.26
ii) | 'B' TYPE TOWER | 0.3 | 0.35 | 0.54 | 0.32
iii) | 'C' TYPE TOWER | 0.3 | 0.35 | 0.54 | 0.3
iv) | 'D' TYPE TOWER | 0.3 | 0.35 | 0.48 | 0.28
i) | Interest during construction at percentage | 12
ii) | Completion period (months) | 18

## Wts of towers-Bersms
400 kV DC Line
|  |  | Sl.No. | Particulars | Details of the line | Dimensions in mm
[6 empty] | a | b | c | d | Total | BW
a
|  |  | 1 | KEC International - 'A' Type | DVG-Hoody | 4030 | 8000 | 8000 | 25900 | 45930 | 10300
|  |  | 2 | KEC International - 'B' Type | DVG-Hoody | 8030 | 8000 | 8000 | 22000 | 46030 | 14900
|  |  | 3 | KEC International - 'C' Type | DVG-Hoody | 8030 | 8000 | 8000 | 22000 | 46030 | 14800
|  |  | 4 | KEC International - 'D' Type | DVG-Hoody | 8030 | 8000 | 8000 | 22000 | 46030 | 15800
b
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV DC with twin ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 48696.9568 | 46343.1146 | 39768.6378 | 66583.4724 | 63305.5392 | 54137.5818 | 83699.3987 | 79543.7536 | 67914.1274 | 94920.703 | 90191.2615 | 76953.1881 | 106850.706 | 101511.9659 | 86566.5106 | 128300.8501 | 121867.5018 | 103855.8728
|  | c | Top Condr | 38.5 | 213823.4522 | 202387.5252 | 174210.557 | 293924.4528 | 277881.1099 | 238292.8873 | 370999.4685 | 350571.0089 | 300110.4658 | 421679.657 | 398385.1238 | 340817.1861 | 475652.7579 | 449316.5256 | 384205.9036 | 572866.461 | 541070.7441 | 462423.8189
|  |  | Middle Condr | 30.5 | 169392.605 | 160332.9745 | 138010.9607 | 232849.2418 | 220139.5806 | 188777.4821 | 293908.6699 | 277725.0849 | 237749.8495 | 334057.9101 | 315603.7994 | 269998.0305 | 376815.8212 | 355952.0527 | 304370.9106 | 453829.2743 | 428640.4596 | 366335.7526
|  |  | Bottm Condr. | 22.5 | 124961.7578 | 118278.4238 | 101811.3645 | 171774.0309 | 162398.0512 | 139262.077 | 216817.8712 | 204879.161 | 175389.2332 | 246436.1632 | 232822.475 | 199178.875 | 277978.8845 | 262587.5799 | 224535.9177 | 334792.0876 | 316210.1751 | 270247.6864
|  |  | TOTAL M |  | 656388.2934 | 621578.0604 | 534895.8516 | 901860.143 | 853053.8099 | 731348.0221 | 1137946.9288 | 1075821.8952 | 920757.6249 | 1293145.2084 | 1222315.0351 | 1045444.7585 | 1458403.3526 | 1378334.2078 | 1178321.923 | 1756013.9087 | 1659360.7537 | 1417814.7721
|  |  | Weight kG |  | 9418.3185 | 9165.1758 | 8502.1268 | 11039.8344 | 10736.956 | 9941.5707 | 12400.9217 | 12057.6633 | 11154.8985 | 13219.5481 | 12852.409 | 11886.2129 | 14038.8582 | 13648.0382 | 12619 | 15404.831 | 14974.8806 | 13842.1232
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 98520.9238 | 94765.7912 | 84278.5815 | 126899.0502 | 121726.5583 | 107188.1489 | 153661.4333 | 147202.2565 | 128994.5963 | 170981.7065 | 163702.9577 | 143163.1863 | 189210.875 | 181075.9451 | 158103.5242 | 221552.1558 | 211907.2882 | 184651.9265
|  | d | Top Condr | 38.5 | 392581.1528 | 375313.0863 | 333450.3668 | 513003.6291 | 488355.5358 | 428138.9229 | 629630.64 | 598199.4925 | 521023.456 | 706185.7225 | 670431.5314 | 582433.8008 | 787424.6277 | 747162.1721 | 647878.5032 | 932789.6738 | 884604.0401 | 765494.8778
|  |  | Middle Condr | 30.5 | 311005.8483 | 297325.9515 | 264161.9789 | 406405.4724 | 386879.0609 | 339174.9909 | 498798.2992 | 473898.2992 | 412758.8417 | 559445.8321 | 531121.0833 | 461408.5955 | 623803.9258 | 591907.6948 | 513254.3986 | 738963.2481 | 700790.2136 | 606431.007
|  |  | Bottm Condr. | 22.5 | 229430.5438 | 219338.8167 | 194873.591 | 299807.3157 | 285402.5859 | 250211.0588 | 367965.9584 | 349597.106 | 304494.2275 | 412705.9417 | 391810.6352 | 340383.3901 | 460183.224 | 436653.2175 | 378630.2941 | 545136.8223 | 516976.387 | 447367.1363
|  |  | TOTAL M |  | 1213295.5468 | 1160607.876 | 1031250.4263 | 1583301.0126 | 1508316.2321 | 1322887.5735 | 1940796.2564 | 1845336.8328 | 1608184.2932 | 2175169.2465 | 2066661.2734 | 1796514.9097 | 2423704.3639 | 2301587.0184 | 1997030.8361 | 2868095.3627 | 2722053.6999 | 2357040.0475
|  |  | Weight kG |  | 15365.8826 | 15028.546 | 14166.2949 | 17553.1859 | 17132.487 | 16044.8505 | 19434.0887 | 18950.123 | 17690.5818 | 20574.0947 | 20054.3624 | 18697.7617 | 21717.71 | 21163.5202 | 19713.6296 | 23624.9556 | 23015.6133 | 21416.9532
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 155050.9039 | 149705.8755 | 134779.3019 | 195332.7502 | 188010.7033 | 167379.0106 | 233039.9466 | 223967.1964 | 198296.1373 | 257280.0742 | 247108.8963 | 218284.6612 | 282656.2388 | 271348.7684 | 239268.9996 | 327354.5392 | 314065.9006 | 276322.6543
| Ground Level | e | Top Condr | 38.5 | 595398.5894 | 571513.4117 | 514122.9194 | 761569.5751 | 727158.5827 | 643537.1194 | 923072.0473 | 879157.3148 | 771670.0365 | 1028984.6326 | 979093.7867 | 856570.5922 | 1141159.159 | 1085096.0924 | 947039.8852 | 1341156.436 | 1274374.8989 | 1109357.5202
|  |  | Middle Condr | 30.5 | 471679.402 | 452757.3781 | 407292.1829 | 603321.3517 | 576060.6954 | 509815.1205 | 731264.8686 | 696475.2754 | 611323.0159 | 815169.644 | 775645.7271 | 678581.8977 | 904035.1779 | 859621.5797 | 750252.3766 | 1062474.5792 | 1009569.7251 | 878841.6718
|  |  | Bottm Condr. | 22.5 | 347960.2146 | 334001.3445 | 300461.4464 | 445073.1283 | 424962.8081 | 376093.1217 | 539457.69 | 513793.2359 | 450975.9953 | 601354.6554 | 572197.6676 | 500593.2032 | 666911.1968 | 634147.067 | 553464.868 | 783792.7223 | 744764.5513 | 648325.8235
|  |  | TOTAL M |  | 1750492.3486 | 1681244.6832 | 1512535.6078 | 2235705.4082 | 2136363.341 | 1891789.4925 | 2705677.8427 | 2579201.8808 | 2265772.4548 | 3013339.4631 | 2869803.972 | 2513018.4419 | 3338859.9003 | 3177703.0394 | 2776130.1317 | 3918626.3007 | 3726859.9321 | 3247533.867
|  |  | Weight kG |  | 18456.7112 | 18087.9634 | 17156.4335 | 20858.4242 | 20389.7437 | 19187.1562 | 22946.278 | 22403.5518 | 20998.2138 | 24215.7674 | 23631.9916 | 22114.2414 | 25490.2037 | 24867.4276 | 23243.1036 | 27614.751 | 26930.5822 | 25139.1768
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 261323.0329 | 252989.1192 | 229716.8741 | 323982.981 | 312619.9316 | 280533.3225 | 382265.6067 | 368279.534 | 328577.8441 | 419514.5421 | 403905.814 | 359507.4077 | 458326.524 | 441054.9152 | 391854.0143 | 526255.096 | 506116.4409 | 448656.7569
|  |  | Top Condr | 38.5 | 976680.1801 | 940355.329 | 853773.7866 | 1228854.9371 | 1176090.4256 | 1048469.5964 | 1474719.9157 | 1407336.9784 | 1242866.8356 | 1635822.4075 | 1559355.7094 | 1371927.2283 | 1806153.5849 | 1720386.5529 | 1509440.8777 | 2108855.3643 | 2007114.9214 | 1755793.5342
|  |  | Middle Condr | 30.5 | 773733.6492 | 744956.8191 | 676366.2465 | 973508.4567 | 931707.9995 | 830605.7842 | 1168284.6086 | 1114903.3206 | 984608.7918 | 1295911.2579 | 1235333.7438 | 1086851.4406 | 1430848.9439 | 1362903.6328 | 1195790.8252 | 1670651.6522 | 1590052.0806 | 1390953.3193
|  |  | Bottm Condr. | 22.5 | 570787.1183 | 549558.3092 | 498958.7065 | 718161.9762 | 687325.5734 | 612741.9719 | 861849.3014 | 822469.6627 | 726350.7481 | 956000.1083 | 911311.7782 | 801775.6529 | 1055544.3029 | 1005420.7127 | 882140.7727 | 1232447.9402 | 1172989.2398 | 1026113.1044
|  |  | TOTAL M |  | 2779312.3078 | 2677434.4763 | 2430937.3635 | 3491739.8874 | 3344554.0175 | 2983603.7965 | 4183317.9331 | 3995919.2953 | 3532523.4212 | 4635460.6375 | 4423081.9623 | 3895910.4333 | 5112889.9054 | 4874933.9686 | 4282443.5485 | 5960221.6587 | 5678324.6612 | 4973676.2885
|  |  | Weight kG |  | 23256.4211 | 22826.2008 | 21750.0917 | 26067.246 | 25511.93 | 24095.9905 | 28532.1595 | 27885.7649 | 26219.0368 | 30034.5173 | 29338.4186 | 27534.5948 | 31543.3219 | 30800.5574 | 28868.2216 | 34056.9235 | 33241.7836 | 31110.928
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV DC with Tripple ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 48696.9568 | 46343.1146 | 39768.6378 | 66583.4724 | 63305.5392 | 54137.5818 | 83699.3987 | 79543.7536 | 67914.1274 | 94920.703 | 90191.2615 | 76953.1881 | 106850.706 | 101511.9659 | 86566.5106 | 128300.8501 | 121867.5018 | 103855.8728
|  |  | Top Condr | 38.5 | 315559.326 | 298427.5626 | 256465.4002 | 433657.5963 | 409623.4867 | 350664.756 | 547297.6876 | 516694.3352 | 441542.7027 | 622020.4425 | 587123.527 | 501386.8338 | 701597.015 | 662143.4633 | 565173.7882 | 844922.3239 | 797290.2129 | 680162.2971
|  |  | Middle Condr | 30.5 | 249988.557 | 236416.6405 | 203173.8885 | 343546.9269 | 324506.918 | 277799.3522 | 433573.4928 | 409329.2785 | 349793.5697 | 492769.4415 | 465123.833 | 397202.5566 | 555810.6223 | 524555.2112 | 447735.079 | 669354.0488 | 631619.5193 | 538829.8718
|  |  | Bottm Condr. | 22.5 | 184417.7879 | 174405.7184 | 149882.3767 | 253436.2576 | 239390.3494 | 204933.9483 | 319849.2979 | 301964.2219 | 258044.4366 | 363518.4404 | 343124.1391 | 293018.2795 | 410024.2295 | 386966.9591 | 330296.3697 | 493785.7737 | 465948.8257 | 397497.4464
|  |  | TOTAL M |  | 941383.6392 | 890617.5118 | 765318.4804 | 1293298.2272 | 1222107.1519 | 1046138.2569 | 1631815.709 | 1541187.4841 | 1316955.4237 | 1854365.0546 | 1751032.826 | 1495252.6833 | 2091346.8686 | 1974531.8365 | 1685271.9588 | 2518131.0641 | 2377115.0067 | 2027771.2267
|  |  | Weight kG |  | 11279.1477 | 10970.807 | 10169.8386 | 13220.3302 | 12851.3161 | 11890.1547 | 14850.0705 | 14431.8065 | 13340.6963 | 15830.3523 | 15382.9669 | 14215.111 | 16811.4819 | 16335.2217 | 15091.3454 | 18447.271 | 17923.3035 | 16553.9805
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 98520.9238 | 94765.7912 | 84278.5815 | 126899.0502 | 121726.5583 | 107188.1489 | 153661.4333 | 147202.2565 | 128994.5963 | 170981.7065 | 163702.9577 | 143163.1863 | 189210.875 | 181075.9451 | 158103.5242 | 221552.1558 | 211907.2882 | 184651.9265
|  |  | Top Condr | 38.5 | 583695.8768 | 557815.9043 | 495325.115 | 762276.3606 | 725335.1256 | 635433.8095 | 935244.4448 | 888137.0606 | 772912.188 | 1048779.5409 | 995193.1383 | 863811.756 | 1169254.8197 | 1108911.9331 | 960682.6876 | 1384807.1432 | 1312590.1568 | 1134768.8854
|  |  | Middle Condr | 30.5 | 462408.4219 | 441906.106 | 392400.4158 | 603881.2727 | 574616.1385 | 503395.6153 | 740907.9368 | 703589.1 | 612307.058 | 830851.3246 | 788399.7589 | 684318.4041 | 926292.7792 | 878488.6743 | 761060.311 | 1097055.0095 | 1039844.1502 | 898972.7534
|  |  | Bottm Condr. | 22.5 | 341120.967 | 325996.3077 | 289475.7166 | 445486.1848 | 423897.1513 | 371357.4212 | 546571.4288 | 519041.1393 | 451701.928 | 612923.1083 | 581606.3795 | 504825.0522 | 683330.7388 | 648065.4155 | 561437.9343 | 809302.8759 | 767098.1436 | 663176.6213
|  |  | TOTAL M |  | 1747534.6681 | 1670773.4092 | 1483752.5747 | 2280114.1217 | 2170765.2841 | 1902356.469 | 2795104.3236 | 2655823.7923 | 2312310.1291 | 3132850.6672 | 2974494.8081 | 2583074.4603 | 3491066.5319 | 3312816.6627 | 2871438.7785 | 4131657.9522 | 3918439.4207 | 3389302.8535
|  |  | Weight kG |  | 18441.1121 | 18031.5469 | 16992.4089 | 21064.5652 | 20553.2565 | 19240.6685 | 23322.3989 | 22733.8943 | 21212.7634 | 24691.3056 | 24059.1797 | 22420.3646 | 26064.7324 | 25390.5968 | 23638.7217 | 28355.4398 | 27614.0926 | 25682.0328
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 155050.9039 | 149705.8755 | 134779.3019 | 195332.7502 | 188010.7033 | 167379.0106 | 233039.9466 | 223967.1964 | 198296.1373 | 257280.0742 | 247108.8963 | 218284.6612 | 282656.2388 | 271348.7684 | 239268.9996 | 327354.5392 | 314065.9006 | 276322.6543
|  |  | Top Condr | 38.5 | 887922.0318 | 852116.3924 | 766333.9438 | 1135125.2796 | 1083539.6959 | 958531.1042 | 1375406.5558 | 1309573.7941 | 1148882.0587 | 1532977.906 | 1458186.5213 | 1275016.9429 | 1699856.6167 | 1615812.8135 | 1409424.7607 | 1997357.2865 | 1897246.445 | 1650562.849
|  |  | Middle Condr | 30.5 | 703418.7524 | 675053.2459 | 607095.7217 | 899255.0917 | 858388.5903 | 759355.8098 | 1089607.7909 | 1037454.5642 | 910153.3193 | 1214437.0424 | 1155186.7246 | 1010078.3574 | 1346639.6574 | 1280059.5016 | 1116557.278 | 1582322.0062 | 1503013.4175 | 1307588.7505
|  |  | Bottm Condr. | 22.5 | 518915.4731 | 497990.0994 | 447857.4996 | 663384.9037 | 633237.4846 | 560180.5154 | 803809.0261 | 765335.3342 | 671424.5798 | 895896.1788 | 852186.928 | 745139.7718 | 993422.6981 | 944306.1897 | 823689.7952 | 1167286.7259 | 1108780.3899 | 964614.652
|  |  | TOTAL M |  | 2525590.9541 | 2424757.6722 | 2180818.5041 | 3225514.9883 | 3080665.451 | 2726428.236 | 3904227.4149 | 3719675.3081 | 3265270.1704 | 4348769.1306 | 4139254.7463 | 3621774.6507 | 4819239.1026 | 4583941.757 | 4001310.1352 | 5657359.9899 | 5377281.05 | 4681564.2212
|  |  | Weight kG |  | 22169.4906 | 21722.4286 | 20600.7945 | 25053.8077 | 24484.7952 | 23034.0997 | 27563.9695 | 26904.6114 | 25207.7317 | 29090.9152 | 28381.4961 | 26548.1902 | 30624.1078 | 29867.1479 | 27904.5687 | 33180.3616 | 32348.6064 | 30183.5071
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 261323.0329 | 252989.1192 | 229716.8741 | 323982.981 | 312619.9316 | 280533.3225 | 382265.6067 | 368279.534 | 328577.8441 | 419514.5421 | 403905.814 | 359507.4077 | 458326.524 | 441054.9152 | 391854.0143 | 526255.096 | 506116.4409 | 448656.7569
|  |  | Top Condr | 38.5 | 1459844.4179 | 1405379.2684 | 1275810.2447 | 1836053.3227 | 1756937.4602 | 1565929.8198 | 2202878.3584 | 2101843.2896 | 1855677.2574 | 2443234.5684 | 2328579.4053 | 2048051.8971 | 2697348.2555 | 2568748.5043 | 2253026.2495 | 3148905.6789 | 2996356.4789 | 2620216.8701
|  |  | Middle Condr | 30.5 | 1156500.1233 | 1113352.4074 | 1010706.8172 | 1454535.7492 | 1391859.5464 | 1240541.8053 | 1745137.4008 | 1665096.632 | 1470081.9832 | 1935549.4633 | 1844718.7496 | 1622482.6717 | 2136860.3063 | 2034982.5813 | 1784864.9509 | 2494587.6157 | 2373736.9508 | 2075756.2218
|  |  | Bottm Condr. | 22.5 | 853155.8286 | 821325.5464 | 745603.3898 | 1073018.1756 | 1026781.6326 | 915153.7908 | 1287396.4432 | 1228349.9744 | 1084486.7089 | 1427864.3582 | 1360858.094 | 1196913.4464 | 1576372.3571 | 1501216.6583 | 1316703.6523 | 1840269.5526 | 1751117.4227 | 1531295.5734
|  |  | TOTAL M |  | 4015112.146 | 3866836.4727 | 3510389.33 | 5044784.6039 | 4830199.3019 | 4307123.2342 | 6045744.8581 | 5772273.4205 | 5099922.1667 | 6700596.5474 | 6390542.3921 | 5625249.4262 | 7392318.1901 | 7044808.0617 | 6184328.2706 | 8620381.3105 | 8208529.633 | 7184630.9393
|  |  | Weight kG |  | 27952.6539 | 27431.6614 | 26136.7661 | 31332.5341 | 30658.9116 | 28951.2858 | 34300.3945 | 33515.6506 | 31503.2951 | 36110.2872 | 35264.9334 | 33086.0636 | 37928.401 | 37026.1699 | 34691.292 | 40957.8778 | 39967.4916 | 37391.8058
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV DC with Quad ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 48696.9568 | 46343.1146 | 39768.6378 | 66583.4724 | 63305.5392 | 54137.5818 | 83699.3987 | 79543.7536 | 67914.1274 | 94920.703 | 90191.2615 | 76953.1881 | 106850.706 | 101511.9659 | 86566.5106 | 128300.8501 | 121867.5018 | 103855.8728
|  |  | Top Condr | 38.5 | 417295.1998 | 394467.6001 | 338720.2434 | 573390.7397 | 541365.8635 | 463036.6248 | 723595.9066 | 682817.6615 | 582974.9396 | 822361.2281 | 775861.9301 | 661956.4815 | 927541.2721 | 874970.4011 | 746141.6729 | 1116978.1869 | 1053509.6817 | 897900.7754
|  |  | Middle Condr | 30.5 | 330584.5089 | 312500.3065 | 268336.8162 | 454244.612 | 428874.2555 | 366821.2223 | 573238.3156 | 540933.4721 | 461837.2898 | 651480.9729 | 614643.8667 | 524407.0827 | 734805.4233 | 693158.3697 | 591099.2474 | 884878.8234 | 834598.579 | 711323.9909
|  |  | Bottm Condr. | 22.5 | 243873.8181 | 230533.013 | 197953.389 | 335098.4842 | 316382.6475 | 270605.8197 | 422880.7247 | 399049.2827 | 340699.64 | 480600.7177 | 453425.8033 | 386857.684 | 542069.5746 | 511346.3383 | 436056.8218 | 652779.4599 | 615687.4763 | 524747.2064
|  |  | TOTAL M |  | 1226378.985 | 1159656.9632 | 995741.1093 | 1684736.3113 | 1591160.4938 | 1360928.4917 | 2125684.4892 | 2006553.073 | 1713153.2225 | 2415584.9009 | 2279750.617 | 1945060.608 | 2724290.3847 | 2570729.4652 | 2192221.9946 | 3280248.2194 | 3094869.2596 | 2637727.6813
|  |  | Weight kG |  | 13388.7074 | 13019.403 | 12064.2275 | 15692.5048 | 15250.4723 | 14104.0537 | 17626.8903 | 17125.8299 | 15824.2962 | 18790.4618 | 18254.5013 | 16861.3705 | 19955.0582 | 19384.4949 | 17900.6403 | 21896.7498 | 21269.0188 | 19635.469
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 98520.9238 | 94765.7912 | 84278.5815 | 126899.0502 | 121726.5583 | 107188.1489 | 153661.4333 | 147202.2565 | 128994.5963 | 170981.7065 | 163702.9577 | 143163.1863 | 189210.875 | 181075.9451 | 158103.5242 | 221552.1558 | 211907.2882 | 184651.9265
|  |  | Top Condr | 38.5 | 774810.6009 | 740318.7222 | 657199.8632 | 1011549.0922 | 962314.7154 | 842728.6962 | 1240858.2496 | 1178074.6287 | 1024800.92 | 1391373.3592 | 1319954.7451 | 1145189.7111 | 1551085.0116 | 1470661.6941 | 1273486.8721 | 1836824.6126 | 1740576.2735 | 1504042.8931
|  |  | Middle Condr | 30.5 | 613810.9955 | 586486.2605 | 520638.8527 | 801357.0731 | 762353.2161 | 667616.2398 | 983017.5743 | 933279.9007 | 811855.2743 | 1102256.817 | 1045678.4345 | 907228.2127 | 1228781.6326 | 1165069.6538 | 1008866.2233 | 1455146.771 | 1378898.0868 | 1191514.4997
|  |  | Bottm Condr. | 22.5 | 452811.3902 | 432653.7987 | 384077.8421 | 591165.0539 | 562391.7168 | 492503.7835 | 725176.8991 | 688485.1726 | 598909.6286 | 813140.2749 | 771402.1238 | 669266.7143 | 906478.2535 | 859477.6134 | 744245.5746 | 1073468.9294 | 1017219.9001 | 878986.1063
|  |  | TOTAL M |  | 2281773.7894 | 2180938.9423 | 1936254.723 | 2976927.2308 | 2833214.3362 | 2481825.3645 | 3649412.3907 | 3466310.7517 | 3016435.965 | 4090532.0878 | 3882328.3427 | 3369634.0109 | 4558428.6999 | 4324046.3069 | 3745846.7209 | 5395220.5418 | 5114825.1415 | 4421565.6596
|  |  | Weight kG |  | 22477.0455 | 21974.7875 | 20705.4263 | 25673.616 | 25046.2463 | 23441.6696 | 28425.9117 | 27703.63 | 25843.42 | 30094.895 | 29318.9939 | 27314.5656 | 31769.5098 | 30941.9799 | 28799.0348 | 34562.6897 | 33652.577 | 31288.9486
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 38253.5492 | 36246.9428 | 31138.1286 | 53428.5109 | 50625.8954 | 43490.4441 | 68006.3098 | 64439.0095 | 55356.6731 | 77596.0425 | 73525.7086 | 63162.6502 | 87818.0653 | 83211.5308 | 71483.3072 | 106259.859 | 100685.9523 | 86494.8017
|  |  | Top Condr | 38.5 | 1180445.4741 | 1132719.3731 | 1018544.9683 | 1508680.9842 | 1439920.8091 | 1273525.0891 | 1827741.0642 | 1739990.2734 | 1526094.081 | 2036971.1794 | 1937279.2558 | 1693463.2937 | 2258554.0743 | 2146529.5347 | 1871809.6362 | 2653558.137 | 2520117.9911 | 2191768.1779
|  |  | Middle Condr | 30.5 | 935158.1029 | 897349.1137 | 806899.2606 | 1195188.8316 | 1140716.4851 | 1008896.4991 | 1447950.7132 | 1378433.853 | 1208983.6226 | 1613704.4409 | 1534727.7221 | 1341574.8171 | 1789244.1368 | 1700497.4236 | 1482862.1793 | 2102169.4332 | 1996457.1099 | 1736335.8292
|  |  | Bottm Condr. | 22.5 | 689870.7316 | 661978.8544 | 595253.5529 | 881696.6791 | 841512.1612 | 744267.9092 | 1068160.3622 | 1016877.4325 | 891873.1642 | 1190437.7023 | 1132176.1885 | 989686.3405 | 1319934.1993 | 1254465.3125 | 1093914.7225 | 1550780.7294 | 1472796.2286 | 1280903.4806
|  |  | TOTAL M |  | 3170472.1888 | 3041775.2972 | 2733551.8564 | 4057115.532 | 3871797.2385 | 3422943.6167 | 4918780.9853 | 4682290.7597 | 4105404.6774 | 5483869.0711 | 5215177.6248 | 4557585.3294 | 6082393.2253 | 5780426.2684 | 5039425.8704 | 7149595.2201 | 6789804.8636 | 5903955.5024
|  |  | Weight kG |  | 24839.1186 | 24329.757 | 23064.1719 | 28098.4844 | 27449.2518 | 25809.1725 | 30938.7633 | 30185.8491 | 28265.2085 | 32667.6389 | 31857.2849 | 29781.1601 | 34404.1993 | 33539.3113 | 31315.8885 | 37300.5242 | 36349.8693 | 33895.7888
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 261323.0329 | 252989.1192 | 229716.8741 | 323982.981 | 312619.9316 | 280533.3225 | 382265.6067 | 368279.534 | 328577.8441 | 419514.5421 | 403905.814 | 359507.4077 | 458326.524 | 441054.9152 | 391854.0143 | 526255.096 | 506116.4409 | 448656.7569
|  |  | Top Condr | 38.5 | 1943008.6557 | 1870403.2077 | 1697846.7028 | 2443251.7083 | 2337784.4949 | 2083390.0431 | 2931036.8011 | 2796349.6007 | 2468487.6792 | 3250646.7293 | 3097803.1012 | 2724176.5659 | 3588542.9261 | 3417110.4557 | 2996611.6212 | 4188955.9935 | 3985598.0363 | 3484640.206
|  |  | Middle Condr | 30.5 | 1539266.5974 | 1481747.9957 | 1345047.3879 | 1935563.0417 | 1852011.0933 | 1650477.8264 | 2321990.193 | 2215289.9434 | 1955555.1745 | 2575187.6686 | 2454103.7555 | 2158113.9029 | 2842871.6687 | 2707061.5298 | 2373939.0766 | 3318523.5793 | 3157421.8209 | 2760559.1242
|  |  | Bottm Condr. | 22.5 | 1135524.539 | 1093092.7837 | 992248.073 | 1427874.375 | 1366237.6918 | 1217565.6096 | 1712943.585 | 1634230.2861 | 1442622.6697 | 1899728.608 | 1810404.4098 | 1592051.2398 | 2097200.4113 | 1997012.604 | 1751266.5319 | 2448091.165 | 2329245.6056 | 2036478.0424
|  |  | TOTAL M |  | 5250911.9842 | 5056238.469 | 4589841.2965 | 6597829.3205 | 6315844.5863 | 5630642.6719 | 7908171.7832 | 7548627.5457 | 6667320.9121 | 8765732.4572 | 8358002.822 | 7354588.4191 | 9671746.4747 | 9214682.1549 | 8086212.9927 | 11280540.9624 | 10738734.6048 | 9395585.5902
|  |  | Weight kG |  | 29835.1588 | 29276.8777 | 27893.9372 | 33443.4847 | 32721.0101 | 30895.1258 | 36614.1563 | 35772.145 | 33619.145 | 38548.2875 | 37641.0943 | 35309.3864 | 40491.46 | 39523.1148 | 37024.0201 | 43729.6446 | 42666.5511 | 39909.1898
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV SC with twin ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 31924.5524 | 29915.9949 | 25525.3011 | 43610.3983 | 40811.2669 | 34682.321 | 54797.2194 | 51247.4927 | 43469.2307 | 62132.4694 | 58092.1924 | 49236.6509 | 69931.4845 | 65370.4034 | 55371.5966 | 83954.7257 | 78458.2077 | 66406.8453
|  |  | All Condr | 22 | 171297.7585 | 158720.8215 | 135199.3116 | 235132.6979 | 217466.4967 | 184373.3521 | 296604.0019 | 274091.5292 | 231867.7394 | 337041.0756 | 311361.2612 | 263167.0827 | 380115.8128 | 351075.0548 | 296544.895 | 457718.2121 | 422646.4321 | 356747.1982
|  |  | TOTAL M |  | 239538.1379 | 222346.2155 | 189446.1009 | 328554.4875 | 304431.9999 | 258200.9219 | 414196.6195 | 383477.1052 | 324539.6867 | 470505.8575 | 435474.7858 | 368230.2808 | 530470.7493 | 490864.2616 | 414803.9687 | 638469.8917 | 590652.0389 | 498771.671
|  |  | Weight kG |  | 5951.4242 | 5733.878 | 5292.6894 | 6970.0722 | 6709.3234 | 6178.9185 | 7825.9461 | 7530.1442 | 6927.3556 | 8340.961 | 8024.4464 | 7378.9289 | 8856.5442 | 8519.5034 | 7831.6817 | 9716.3642 | 9345.433 | 8587.8503
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 65267.0537 | 62061.9035 | 55066.1062 | 83840.3878 | 79410.2117 | 69665.4798 | 101389.9121 | 95849.2417 | 83617.3123 | 112756.6041 | 106509.4586 | 92698.903 | 124724.0827 | 117739.5141 | 102283.9692 | 145962.2843 | 137678.4115 | 119330.1636
|  |  | Top Condr | 22 | 318778.3002 | 299856.6201 | 265319.0979 | 414438.1892 | 387261.9962 | 337222.7917 | 507443.4727 | 472657.1049 | 408207.3457 | 568620.2081 | 528982.3503 | 455322.3874 | 633617.295 | 588922.0019 | 505654.4245 | 750059.2222 | 696483.0265 | 596344.4745
|  |  | TOTAL M |  | 451714.1452 | 425688.5675 | 376837.0771 | 586075.2623 | 548899.8509 | 478581.9849 | 716109.8272 | 668677.1648 | 578484.1627 | 801435.4064 | 747465.4657 | 644582.6417 | 891961.1285 | 831175.275 | 715057.1386 | 1053900.4959 | 981140.6833 | 841776.5093
|  |  | Weight kG |  | 7527.4845 | 7307.4191 | 6875.3504 | 8574.2219 | 8297.8309 | 7748.1175 | 9477.8065 | 9158.5405 | 8518.5124 | 10026.5676 | 9683.0815 | 8992.0213 | 10577.6937 | 10210.9072 | 9470.8377 | 11497.8815 | 11093.8851 | 10275.8185
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 103097.2597 | 98534.4625 | 88582.9301 | 129485.0975 | 123204.3476 | 109357.1662 | 154253.7075 | 146454.1239 | 129169.0896 | 170194.4498 | 161443.4044 | 142010.9188 | 186891.4427 | 177157.1993 | 155510.4714 | 216315.696 | 204869.3067 | 179376.6495
|  |  | Top Condr | 22 | 486108.856 | 459988.4679 | 412952.2428 | 617877.1459 | 579910.9721 | 510644.8677 | 746660.6972 | 697948.4401 | 608281.2268 | 831368.5309 | 775893.9591 | 673340.6668 | 921238.5871 | 858781.7503 | 742908.8678 | 1081747.6143 | 1007176.4173 | 868190.1363
|  |  | TOTAL M |  | 656905.8985 | 622697.2151 | 559161.5643 | 833234.1652 | 783903.2699 | 691240.2675 | 1004429.4698 | 941424.4186 | 822183.3578 | 1116642.5672 | 1045037.4266 | 909035.4827 | 1235454.1702 | 1154968.3349 | 1001647.7213 | 1447210.7846 | 1351309.7777 | 1167932.2095
|  |  | Weight kG |  | 9077.5699 | 8838.0506 | 8375.0359 | 10223.546 | 9916.2909 | 9311.7764 | 11224.7776 | 10867.0271 | 10155.5246 | 11835.1867 | 11449.4321 | 10678.4555 | 12448.9104 | 12036.5787 | 11209.2234 | 13473.6083 | 13019.5353 | 12103.9422
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 174215.2138 | 167100.1417 | 151592.0488 | 215293.7333 | 205534.0432 | 183974.5638 | 253633.6836 | 241587.5125 | 214803.0194 | 278173.298 | 264715.1081 | 234713.8153 | 303761.4235 | 288857.9974 | 255572.3092 | 348574.8407 | 331183.1574 | 292259.5458
|  |  | Top Condr | 22 | 800677.7689 | 761024.3486 | 690491.4982 | 1000327.1479 | 942076.6183 | 836665.3821 | 1196371.1631 | 1121479.2771 | 984405.1386 | 1325315.6992 | 1240069.2912 | 1083198.7036 | 1461945.0747 | 1366097.8662 | 1188929.4521 | 1705296.9496 | 1591256.7226 | 1379239.6206
|  |  | TOTAL M |  | 1049179.8279 | 998847.5764 | 906250.3133 | 1308251.1923 | 1235058.594 | 1098412.7098 | 1560495.2161 | 1466932.4789 | 1290587.8197 | 1725674.8588 | 1619448.9706 | 1418337.4528 | 1900253.3333 | 1781063.5004 | 1554572.7955 | 2210376.8207 | 2068929.7989 | 1798867.4029
|  |  | Weight kG |  | 11472.1017 | 11193.5446 | 10662.0842 | 12810.4266 | 12446.9173 | 11738.1809 | 13991.0157 | 13565.1027 | 12723.6526 | 14712.8738 | 14252.8481 | 13338.525 | 15439.1638 | 14947.127 | 13964.441 | 16651.4164 | 16109.8279 | 15021.6486
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV SC with Tripple ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 31924.5524 | 29915.9949 | 25525.3011 | 43610.3983 | 40811.2669 | 34682.321 | 54797.2194 | 51247.4927 | 43469.2307 | 62132.4694 | 58092.1924 | 49236.6509 | 69931.4845 | 65370.4034 | 55371.5966 | 83954.7257 | 78458.2077 | 66406.8453
|  |  | All Condr | 22 | 252887.3119 | 233976.1739 | 198972.1629 | 347029.41 | 320466.2338 | 271215.1525 | 437689.4236 | 403839.4123 | 340998.4013 | 497327.407 | 458714.9186 | 386988.0796 | 560854.7894 | 517188.665 | 436032.2084 | 675301.413 | 622566.7082 | 524490.7849
|  |  | TOTAL M |  | 335707.7445 | 311049.6994 | 264615.1608 | 460447.142 | 425837.79 | 360561.3521 | 580494.0061 | 536410.935 | 453171.9979 | 659435.3563 | 609160.5417 | 514178.0898 | 743507.781 | 686662.3739 | 579217.665 | 894935.2107 | 826298.0684 | 696491.0368
|  |  | Weight kG |  | 7045.5395 | 6781.8545 | 6255.1962 | 8251.3207 | 7935.1598 | 7301.6862 | 9264.7231 | 8905.9938 | 8185.875 | 9874.604 | 9490.7265 | 8719.4754 | 10485.1907 | 10076.3954 | 9254.5323 | 11503.4835 | 11053.5542 | 10148.2543
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 65267.0537 | 62061.9035 | 55066.1062 | 83840.3878 | 79410.2117 | 69665.4798 | 101389.9121 | 95849.2417 | 83617.3123 | 112756.6041 | 106509.4586 | 92698.903 | 124724.0827 | 117739.5141 | 102283.9692 | 145962.2843 | 137678.4115 | 119330.1636
|  |  | Top Condr | 22 | 474108.1244 | 445679.8718 | 394151.8424 | 615987.6469 | 575159.483 | 500489.3119 | 753948.6298 | 701687.7757 | 605507.8107 | 844696.1057 | 785146.5522 | 675221.0365 | 941107.0127 | 873959.0856 | 749696.5026 | 1113812.9282 | 1033321.5998 | 883886.6995
|  |  | TOTAL M |  | 634413.0845 | 597205.8762 | 528370.1511 | 823137.7344 | 769904.8749 | 670616.066 | 1006049.193 | 938063.0399 | 810548.9696 | 1126155.8772 | 1048765.7999 | 903227.4328 | 1253630.5344 | 1166435.8929 | 1002099.4309 | 1481747.6049 | 1377330.2133 | 1179983.6744
|  |  | Weight kG |  | 8920.8059 | 8655.2588 | 8141.1763 | 10161.4171 | 9827.353 | 9171.8089 | 11233.8244 | 10847.6093 | 10083.4152 | 11885.4951 | 11469.8379 | 10644.2872 | 12540.1521 | 12096.1861 | 11211.7506 | 13633.4302 | 13144.2878 | 12166.23
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 103097.2597 | 98534.4625 | 88582.9301 | 129485.0975 | 123204.3476 | 109357.1662 | 154253.7075 | 146454.1239 | 129169.0896 | 170194.4498 | 161443.4044 | 142010.9188 | 186891.4427 | 177157.1993 | 155510.4714 | 216315.696 | 204869.3067 | 179376.6495
|  |  | Top Condr | 22 | 725103.9582 | 685877.6435 | 615601.5597 | 921146.0819 | 864132.9469 | 760622.4259 | 1112774.4666 | 1039624.7786 | 905618.6323 | 1238818.5899 | 1155513.9654 | 1002248.4556 | 1372538.9508 | 1278748.7082 | 1105578.1676 | 1611345.5163 | 1499361.6861 | 1291655.1922
|  |  | TOTAL M |  | 923361.5379 | 874541.0569 | 785095.2878 | 1171348.702 | 1100782.3496 | 969940.2472 | 1412609.7113 | 1322359.3684 | 1153684.8312 | 1570908.638 | 1468275.7716 | 1275734.7765 | 1738608.9457 | 1623189.4963 | 1405987.7236 | 2037659.4856 | 1900047.1338 | 1640053.4003
|  |  | Weight kG |  | 10762.2707 | 10473.8928 | 9923.8275 | 12121.6328 | 11750.8356 | 11030.381 | 13311.565 | 12879.3152 | 12029.8888 | 14037.6202 | 13571.3121 | 12650.2241 | 14767.908 | 14269.2989 | 13280.3276 | 15987.6204 | 15438.3261 | 14343.2318
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 174215.2138 | 167100.1417 | 151592.0488 | 215293.7333 | 205534.0432 | 183974.5638 | 253633.6836 | 241587.5125 | 214803.0194 | 278173.298 | 264715.1081 | 234713.8153 | 303761.4235 | 288857.9974 | 255572.3092 | 348574.8407 | 331183.1574 | 292259.5458
|  |  | Top Condr | 22 | 1196957.3275 | 1137431.4645 | 1031910.4429 | 1494821.0849 | 1407381.4162 | 1249653.1975 | 1787340.1654 | 1674921.0341 | 1469804.5001 | 1979739.3424 | 1851776.9635 | 1617035.5108 | 2183598.6822 | 2039722.8821 | 1774609.044 | 2546669.5193 | 2375482.144 | 2058229.4186
|  |  | TOTAL M |  | 1475655.8889 | 1403936.9146 | 1273685.3815 | 1840425.5673 | 1735819.6175 | 1542870.1967 | 2196496.0564 | 2062546.4978 | 1812974.6125 | 2429965.5836 | 2277768.7675 | 1992852.6248 | 2676896.9457 | 2506018.7424 | 2184881.1723 | 3115861.9802 | 2912913.1974 | 2529596.2235
|  |  | Weight kG |  | 13605.3767 | 13270.6385 | 12640.0591 | 15194.176 | 14756.0568 | 13911.7805 | 16599.0501 | 16084.9567 | 15080.4355 | 17458.9485 | 16903.3522 | 15810.8644 | 18324.5724 | 17730.059 | 16555.1048 | 19770.0209 | 19115.3298 | 17813.2689
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV SC with Quad ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 31924.5524 | 29915.9949 | 25525.3011 | 43610.3983 | 40811.2669 | 34682.321 | 54797.2194 | 51247.4927 | 43469.2307 | 62132.4694 | 58092.1924 | 49236.6509 | 69931.4845 | 65370.4034 | 55371.5966 | 83954.7257 | 78458.2077 | 66406.8453
|  |  | All Condr | 22 | 334476.8654 | 309231.5263 | 262745.0143 | 458926.1221 | 423465.9709 | 358056.9529 | 578774.8453 | 533587.2954 | 450129.0631 | 657613.7384 | 606068.5759 | 510809.0765 | 741593.7659 | 683302.2751 | 575519.5217 | 892884.614 | 822486.9844 | 692234.3717
|  |  | TOTAL M |  | 431877.3512 | 399753.1833 | 339784.2207 | 592339.7965 | 547243.5801 | 462921.7822 | 746791.3927 | 689344.7648 | 581804.309 | 848364.8551 | 782846.2976 | 660125.8988 | 956544.8127 | 882460.4861 | 743631.3612 | 1151400.5297 | 1061944.0979 | 894210.4025
|  |  | Weight kG |  | 7991.2329 | 7688.2862 | 7088.1872 | 9358.7755 | 8995.4711 | 8273.464 | 10508.3185 | 10096.0575 | 9275.1735 | 11200.1776 | 10758.998 | 9879.7729 | 11892.8581 | 11423.0271 | 10486.0621 | 13048.0853 | 12530.9617 | 11498.8242
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 65267.0537 | 62061.9035 | 55066.1062 | 83840.3878 | 79410.2117 | 69665.4798 | 101389.9121 | 95849.2417 | 83617.3123 | 112756.6041 | 106509.4586 | 92698.903 | 124724.0827 | 117739.5141 | 102283.9692 | 145962.2843 | 137678.4115 | 119330.1636
|  |  | Top Condr | 22 | 629437.9487 | 591503.1235 | 522984.5869 | 817537.1046 | 763056.9698 | 663755.8322 | 1000453.7869 | 930718.4466 | 802808.2757 | 1120772.0033 | 1041310.754 | 895119.6857 | 1248596.7304 | 1158996.1692 | 993738.5807 | 1477566.6341 | 1370160.1732 | 1171428.9245
|  |  | TOTAL M |  | 817112.0238 | 768723.1848 | 679903.2252 | 1060200.2065 | 990909.8989 | 862650.1472 | 1295988.5587 | 1207448.915 | 1042613.7766 | 1450876.348 | 1350066.1341 | 1161872.2239 | 1615299.9404 | 1501696.5107 | 1289141.7232 | 1909594.7139 | 1773519.7433 | 1518190.8394
|  |  | Weight kG |  | 10124.1559 | 9819.8084 | 9235.0994 | 11532.1947 | 11148.9792 | 10402.4437 | 12750.2472 | 12307.0058 | 11436.1476 | 13490.6608 | 13013.5428 | 12072.4998 | 14234.5785 | 13724.8975 | 12716.5222 | 15477.0656 | 14915.4389 | 13800.0674
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 103097.2597 | 98534.4625 | 88582.9301 | 129485.0975 | 123204.3476 | 109357.1662 | 154253.7075 | 146454.1239 | 129169.0896 | 170194.4498 | 161443.4044 | 142010.9188 | 186891.4427 | 177157.1993 | 155510.4714 | 216315.696 | 204869.3067 | 179376.6495
|  |  | Top Condr | 22 | 964099.0604 | 911766.8191 | 818250.8767 | 1224415.018 | 1148354.9217 | 1010599.9842 | 1478888.2359 | 1381301.1171 | 1202956.0379 | 1646268.649 | 1535133.9717 | 1331156.2445 | 1823839.3145 | 1698715.6661 | 1468247.4674 | 2140943.4184 | 1991546.9548 | 1715120.2481
|  |  | TOTAL M |  | 1189817.1774 | 1126384.8988 | 1011029.0112 | 1509463.2388 | 1417661.4293 | 1248640.2269 | 1820789.9527 | 1703294.3182 | 1485186.3046 | 2025174.7089 | 1891514.1166 | 1642434.0704 | 2241763.7212 | 2091410.6576 | 1810327.726 | 2628108.1866 | 2448784.49 | 2112174.5911
|  |  | Weight kG |  | 12216.819 | 11886.7036 | 11261.5931 | 13760.3441 | 13335.3459 | 12515.168 | 15112.9048 | 14617.1556 | 13649.2406 | 15938.5669 | 15403.6207 | 14353.6382 | 16769.223 | 16197.1156 | 15069.423 | 18156.8139 | 17526.4237 | 16277.3211
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 174215.2138 | 167100.1417 | 151592.0488 | 215293.7333 | 205534.0432 | 183974.5638 | 253633.6836 | 241587.5125 | 214803.0194 | 278173.298 | 264715.1081 | 234713.8153 | 303761.4235 | 288857.9974 | 255572.3092 | 348574.8407 | 331183.1574 | 292259.5458
|  |  | Top Condr | 22 | 1593236.8861 | 1513838.5804 | 1373329.3875 | 1989315.0219 | 1872686.2141 | 1662641.013 | 2378309.1678 | 2228362.7911 | 1955203.8615 | 2634162.9856 | 2463484.6358 | 2150872.3181 | 2905252.2897 | 2713347.8979 | 2360288.6359 | 3388042.089 | 3159707.5655 | 2737219.2166
|  |  | TOTAL M |  | 1902131.9499 | 1809026.2527 | 1641120.4498 | 2372599.9423 | 2236580.641 | 1987327.6837 | 2832496.8966 | 2658160.5167 | 2335361.4053 | 3134256.3085 | 2936088.5644 | 2567367.7968 | 3453540.5581 | 3230973.9845 | 2815189.5491 | 4021347.1397 | 3756896.5959 | 3260325.0441
|  |  | Weight kG |  | 15446.7936 | 15064.0052 | 14347.897 | 17251.6358 | 16749.8261 | 15788.9323 | 18849.6263 | 18260.3301 | 17115.716 | 19828.2907 | 19191.2206 | 17945.7688 | 20813.7485 | 20131.8995 | 18791.9498 | 22459.6925 | 21708.6413 | 20223.1346
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 765 kV SC with twin ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 38834.792 | 36690.7454 | 31489.1674 | 53074.8253 | 50087.9918 | 42831.1043 | 66704.0132 | 62916.8547 | 53709.4734 | 75640.0433 | 71329.7561 | 60848.1414 | 85140.7327 | 80275.0007 | 68440.929 | 102223.3233 | 96359.8316 | 82097.2794
|  |  | All Condr | 27 | 221908.0288 | 206399.5006 | 177955.4887 | 304913.5072 | 283137.3638 | 243138.8436 | 384819.2987 | 357075.8436 | 306058.2614 | 437375.8796 | 405732.4017 | 347509.6448 | 493357.5775 | 457575.5332 | 391705.9257 | 594209.8828 | 551000.9094 | 471408.4067
|  |  | TOTAL M |  | 307337.5629 | 286530.4729 | 246872.4162 | 421960.8476 | 392772.7266 | 337072.7776 | 532210.5277 | 495045.3935 | 424058.229 | 604691.8684 | 562313.1654 | 481331.3226 | 681875.9583 | 633964.4243 | 542375.0977 | 820885.8201 | 763044.1054 | 652417.1522
|  |  | Weight kG |  | 10954.5555 | 10577.2398 | 9818.0044 | 12835.8023 | 12383.9047 | 11472.2547 | 14415.4655 | 13903.0298 | 12867.6633 | 15365.7585 | 14817.5386 | 13709.1018 | 16316.9743 | 15733.2841 | 14552.4733 | 17903.1033 | 17260.8334 | 15960.6151
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 78979.5018 | 75558.3407 | 67264.499 | 101593.4327 | 96873.0335 | 85349.8497 | 122939.9709 | 117040.9917 | 102594.5596 | 136760.4423 | 130111.2112 | 113808.0569 | 151308.6971 | 143876.0211 | 125637.0403 | 177123.0514 | 168309.338 | 146664.0392
|  |  | Top Condr | 27 | 405119.9406 | 381761.0699 | 340058.2641 | 528253.1404 | 494764.3294 | 434491.9573 | 647787.8086 | 604969.0218 | 527461.7941 | 726361.9864 | 677596.0766 | 589076.6283 | 809816.5832 | 754850.5468 | 654842.5246 | 959290.0354 | 893434.0475 | 773244.9522
|  |  | TOTAL M |  | 569397.7642 | 537899.0908 | 479093.034 | 740825.5394 | 695883.8663 | 611437.9334 | 906530.0143 | 849228.178 | 741072.2832 | 1015204.6006 | 950025.3119 | 826732.9668 | 1130475.5546 | 1057082.1891 | 918000.0643 | 1336649.0727 | 1248822.5701 | 1081996.9557
|  |  | Weight kG |  | 15484.0739 | 15049.6972 | 14203.2354 | 17661.8149 | 17117.713 | 16045.5107 | 19537.4757 | 18909.914 | 17664.7559 | 20675.4107 | 20000.6884 | 18657.7807 | 21817.6487 | 21097.5359 | 19660.688 | 23723.8985 | 22931.2498 | 21344.7158
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 124527.4536 | 119657.286 | 107854.98 | 156642.3596 | 149955.067 | 133591.3684 | 186744.9581 | 178449.9196 | 158059.2911 | 206107.2877 | 196804.3047 | 173896.0659 | 226382.4806 | 216037.3651 | 190531.4122 | 262103.8428 | 249942.8252 | 219921.1055
|  |  | Top Condr | 27 | 612991.0992 | 580725.2759 | 523979.1206 | 781652.9758 | 734875.0411 | 651600.0756 | 946150.3347 | 886227.1651 | 778664.9412 | 1054243.925 | 986051.0046 | 863157.1082 | 1168869.1113 | 1092137.0302 | 953395.7634 | 1373507.8311 | 1281956.6738 | 1115706.9229
|  |  | TOTAL M |  | 822259.4344 | 780856.5182 | 704431.8387 | 1046105.4694 | 986497.0875 | 875409.9409 | 1263064.9619 | 1187008.4817 | 1044353.8466 | 1405165.5671 | 1318765.3843 | 1156210.5838 | 1555565.9998 | 1458483.6333 | 1275364.4081 | 1823543.4553 | 1707914.7514 | 1489091.6889
|  |  | Weight kG |  | 18607.2327 | 18132.7209 | 17222.5258 | 20987.7118 | 20380.9893 | 19199.1983 | 23061.6406 | 22356.5233 | 20970.1333 | 24324.3423 | 23564.6572 | 22064.5882 | 25593.0224 | 24781.5312 | 23173.6532 | 27709.9291 | 26817.016 | 25040.2163
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 210154.1916 | 202560.0004 | 184162.0442 | 260130.2191 | 249745.3143 | 224281.8106 | 306693.5553 | 293894.1047 | 262328.8323 | 336474.1635 | 322182.3255 | 286857.0224 | 367515.571 | 351695.2872 | 312527.971 | 421861.366 | 403407.6671 | 357638.9035
|  |  | Top Condr | 27 | 1003773.3086 | 954763.0817 | 869736.5559 | 1258025.6879 | 1186265.1958 | 1059747.0776 | 1507049.5378 | 1414971.4095 | 1250908.0439 | 1670637.4128 | 1565923.1673 | 1378407.8831 | 1843860.9729 | 1726210.358 | 1514653.4922 | 2152206.2641 | 2012350.1127 | 1759509.7792
|  |  | TOTAL M |  | 1306428.7757 | 1245511.1009 | 1134205.6734 | 1633839.3872 | 1545434.511 | 1381871.8895 | 1951950.3168 | 1839081.0664 | 1628545.5262 | 2160053.4784 | 2031979.1314 | 1792158.0913 | 2379883.4366 | 2236242.0554 | 1966412.6906 | 2770211.5835 | 2599838.5226 | 2278475.4123
|  |  | Weight kG |  | 20848.1586 | 20356.2903 | 19425.4345 | 23314.683 | 22675.1484 | 21441.6758 | 25483.5081 | 24735.7607 | 23276.881 | 26807.5476 | 26000.665 | 24418.1632 | 28138.6124 | 27276.2234 | 25577.74 | 30358.5696 | 29410.2029 | 27532.5862
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 765 kV SC with Tripple ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 38834.792 | 36690.7454 | 31489.1674 | 53074.8253 | 50087.9918 | 42831.1043 | 66704.0132 | 62916.8547 | 53709.4734 | 75640.0433 | 71329.7561 | 60848.1414 | 85140.7327 | 80275.0007 | 68440.929 | 102223.3233 | 96359.8316 | 82097.2794
|  |  | All Condr | 27 | 324217.4455 | 300924.0086 | 258806.625 | 445296.4012 | 412589.3849 | 353357.879 | 561860.7742 | 520191.1124 | 444640.0889 | 638528.5425 | 591001.1643 | 504779.9152 | 720191.1005 | 666447.6838 | 568902.7637 | 867302.0527 | 802403.4687 | 684538.6989
|  |  | TOTAL M |  | 427929.6723 | 397946.5105 | 342171.6506 | 587430.1647 | 545357.8238 | 466987.9545 | 740889.3149 | 687309.3609 | 587404.6291 | 841790.5122 | 780689.4559 | 666705.7903 | 949244.6318 | 880162.0283 | 751237.0105 | 1142779.5607 | 1059372.3021 | 903633.8276
|  |  | Weight kG |  | 12926.2676 | 12465.2011 | 11558.699 | 15144.853 | 14592.4332 | 13503.2957 | 17008.4057 | 16381.8547 | 15144.5238 | 18129.6305 | 17459.2706 | 16134.4458 | 19252.0072 | 18538.2295 | 17126.7685 | 21123.6115 | 20338.1407 | 18783.7881
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 78979.5018 | 75558.3407 | 67264.499 | 101593.4327 | 96873.0335 | 85349.8497 | 122939.9709 | 117040.9917 | 102594.5596 | 136760.4423 | 130111.2112 | 113808.0569 | 151308.6971 | 143876.0211 | 125637.0403 | 177123.0514 | 168309.338 | 146664.0392
|  |  | Top Condr | 27 | 599035.3132 | 563966.3625 | 501960.7882 | 780305.8509 | 730029.8334 | 640387.5495 | 956313.5391 | 892030.8797 | 776745.3879 | 1072007.7028 | 998796.6766 | 867130.3904 | 1194879.609 | 1112360.2042 | 963607.662 | 1414922.2815 | 1316053.176 | 1137293.5171
|  |  | TOTAL M |  | 797481.0253 | 752208.9559 | 669522.7828 | 1037289.9375 | 972603.1521 | 853612.3289 | 1269417.9785 | 1186870.3352 | 1034279.6463 | 1421753.0922 | 1327821.4577 | 1153779.8018 | 1583386.6856 | 1477585.0482 | 1281169.6189 | 1872563.7206 | 1745907.1889 | 1510190.8777
|  |  | Weight kG |  | 18324.7279 | 17796.992 | 16790.3611 | 20899.093 | 20236.9563 | 18958.6625 | 23119.5661 | 22355.2224 | 20868.7456 | 24467.4916 | 23645.429 | 22041.382 | 25820.8688 | 24943.2822 | 23226.3343 | 28079.9066 | 27113.6467 | 25216.9918
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 124527.4536 | 119657.286 | 107854.98 | 156642.3596 | 149955.067 | 133591.3684 | 186744.9581 | 178449.9196 | 158059.2911 | 206107.2877 | 196804.3047 | 173896.0659 | 226382.4806 | 216037.3651 | 190531.4122 | 262103.8428 | 249942.8252 | 219921.1055
|  |  | Top Condr | 27 | 910842.051 | 862412.6715 | 777842.0728 | 1160405.604 | 1090195.9008 | 966049.7269 | 1403857.3282 | 1313918.0946 | 1153550.1086 | 1563830.6107 | 1461479.0686 | 1278251.1103 | 1733458.4012 | 1618289.9294 | 1411437.5202 | 2036248.975 | 1898837.1154 | 1650986.4732
|  |  | TOTAL M |  | 1154333.4606 | 1094909.7956 | 987463.6442 | 1468376.7746 | 1382644.314 | 1225989.8572 | 1773362.489 | 1663841.099 | 1462313.3198 | 1973303.7629 | 1848820.1329 | 1618998.8867 | 2185026.5991 | 2045091.5006 | 1786035.1627 | 2562433.5566 | 2395674.7557 | 2085874.8595
|  |  | Weight kG |  | 22046.6699 | 21471.7048 | 20390.9713 | 24865.4378 | 24128.626 | 22720.6523 | 27326.0032 | 26468.7408 | 24814.0455 | 28825.3327 | 27901.316 | 26109.6248 | 30332.3264 | 29344.974 | 27423.467 | 32847.6015 | 31760.7892 | 29636.1293
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 210154.1916 | 202560.0004 | 184162.0442 | 260130.2191 | 249745.3143 | 224281.8106 | 306693.5553 | 293894.1047 | 262328.8323 | 336474.1635 | 322182.3255 | 286857.0224 | 367515.571 | 351695.2872 | 312527.971 | 421861.366 | 403407.6671 | 357638.9035
|  |  | Top Condr | 27 | 1497015.3651 | 1423469.3802 | 1296478.2258 | 1874964.6722 | 1767281.133 | 1578270.23 | 2245206.1328 | 2107034.4613 | 1861914.7627 | 2488420.8423 | 2331287.3127 | 2051127.2727 | 2745946.1936 | 2569399.921 | 2253324.1133 | 3204296.6246 | 2994427.2737 | 2616690.7575
|  |  | TOTAL M |  | 1837255.877 | 1749932.8193 | 1593465.0586 | 2297789.122 | 2170723.8625 | 1939906.5061 | 2746354.4444 | 2583879.3227 | 2286110.957 | 3040152.0052 | 2855664.0247 | 2516138.6983 | 3350707.551 | 3143682.6631 | 2761370.0131 | 3902471.2294 | 3656749.9633 | 3200973.5812
|  |  | Weight kG |  | 24723.4832 | 24128.7888 | 23024.8127 | 27649.0312 | 26873.6789 | 25404.768 | 30227.5625 | 29319.7962 | 27578.6807 | 31803.3218 | 30823.2472 | 28932.9104 | 33388.2069 | 32340.3104 | 30310.0837 | 36032.5244 | 34879.678 | 32633.6671
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 765 kV SC with Quad ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 38834.792 | 36690.7454 | 31489.1674 | 53074.8253 | 50087.9918 | 42831.1043 | 66704.0132 | 62916.8547 | 53709.4734 | 75640.0433 | 71329.7561 | 60848.1414 | 85140.7327 | 80275.0007 | 68440.929 | 102223.3233 | 96359.8316 | 82097.2794
|  |  | All Condr | 27 | 426526.8621 | 395448.5166 | 339657.7613 | 585679.2951 | 542041.406 | 463576.9143 | 738902.2497 | 683306.3812 | 583221.9164 | 839681.2055 | 776269.9269 | 662050.1856 | 947024.6235 | 875319.8345 | 746099.6016 | 1140394.2225 | 1053806.0281 | 897668.9911
|  |  | TOTAL M |  | 548521.7817 | 509362.5481 | 437470.8849 | 752899.4817 | 697942.9211 | 596903.1315 | 949568.1021 | 879573.3282 | 750751.0292 | 1078889.156 | 999065.7463 | 852080.258 | 1216613.3054 | 1126359.6322 | 960098.9234 | 1464673.3012 | 1355700.4988 | 1154850.5029
|  |  | Weight kG |  | 14634.7019 | 14102.6408 | 13069.5766 | 17145.7086 | 16508.0925 | 15266.4784 | 19255.2871 | 18532.0288 | 17121.2279 | 20524.6308 | 19750.7674 | 18240.099 | 21795.3186 | 20971.3061 | 19361.7644 | 23914.2807 | 23007.4676 | 21234.8806
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 78979.5018 | 75558.3407 | 67264.499 | 101593.4327 | 96873.0335 | 85349.8497 | 122939.9709 | 117040.9917 | 102594.5596 | 136760.4423 | 130111.2112 | 113808.0569 | 151308.6971 | 143876.0211 | 125637.0403 | 177123.0514 | 168309.338 | 146664.0392
|  |  | Top Condr | 27 | 792950.6857 | 746171.6551 | 663863.3122 | 1032358.5615 | 965295.3373 | 846283.1417 | 1264839.2696 | 1179092.7376 | 1026028.9818 | 1417653.4191 | 1319997.2767 | 1145184.1525 | 1579942.6348 | 1469869.8616 | 1272372.7994 | 1870554.5276 | 1738672.3044 | 1501342.0819
|  |  | TOTAL M |  | 1025564.2865 | 966518.8211 | 859952.5316 | 1333754.3356 | 1249322.4378 | 1095786.7245 | 1632305.9427 | 1524512.4925 | 1327487.0094 | 1828301.5838 | 1705617.6034 | 1480826.6368 | 2036297.8165 | 1898087.9072 | 1644339.1735 | 2408478.3684 | 2242991.8078 | 1938384.7997
|  |  | Weight kG |  | 20780.6344 | 20173.5586 | 19028.94 | 23698.1955 | 22935.8387 | 21480.3015 | 26216.7068 | 25336.28 | 23642.4509 | 27746.057 | 26798.9755 | 24970.628 | 29281.8158 | 28270.632 | 26313.1631 | 31845.5484 | 30732.0266 | 28569.1523
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 124527.4536 | 119657.286 | 107854.98 | 156642.3596 | 149955.067 | 133591.3684 | 186744.9581 | 178449.9196 | 158059.2911 | 206107.2877 | 196804.3047 | 173896.0659 | 226382.4806 | 216037.3651 | 190531.4122 | 262103.8428 | 249942.8252 | 219921.1055
|  |  | Top Condr | 27 | 1208693.0028 | 1144100.0671 | 1031705.0251 | 1539158.2322 | 1445516.7606 | 1280499.3783 | 1861564.3217 | 1741609.0242 | 1528435.2761 | 2073417.2963 | 1936907.1326 | 1693345.1124 | 2298047.6911 | 2144442.8285 | 1869479.277 | 2698990.119 | 2515717.5569 | 2186266.0234
|  |  | TOTAL M |  | 1486407.4867 | 1408963.073 | 1270495.4497 | 1890648.0798 | 1778791.5406 | 1576569.7735 | 2283660.0161 | 2140673.7164 | 1880272.793 | 2541441.9588 | 2378874.8814 | 2081787.1896 | 2814487.1984 | 2631699.3678 | 2296705.9173 | 3301323.658 | 3083434.76 | 2682658.0301
|  |  | Weight kG |  | 25017.6377 | 24357.1888 | 23129.3758 | 28215.1722 | 27367.7998 | 25765.2259 | 31009.3798 | 30022.8969 | 28137.6477 | 32712.7801 | 31649.2306 | 29607.0763 | 34425.2415 | 33288.5972 | 31097.8276 | 37283.9064 | 36032.5285 | 33609.3423
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 210154.1916 | 202560.0004 | 184162.0442 | 260130.2191 | 249745.3143 | 224281.8106 | 306693.5553 | 293894.1047 | 262328.8323 | 336474.1635 | 322182.3255 | 286857.0224 | 367515.571 | 351695.2872 | 312527.971 | 421861.366 | 403407.6671 | 357638.9035
|  |  | Top Condr | 27 | 1990257.4216 | 1892175.6787 | 1723219.8957 | 2491903.6564 | 2348297.0701 | 2096793.3824 | 2983362.7279 | 2799097.513 | 2472921.4815 | 3306204.2719 | 3096651.4581 | 2723846.6622 | 3648031.4142 | 3412589.4841 | 2991994.7345 | 4256386.985 | 3976504.4348 | 3473871.7359
|  |  | TOTAL M |  | 2368082.9782 | 2254354.5378 | 2052724.4438 | 2961738.8569 | 2796013.2141 | 2497941.1227 | 3540758.572 | 3328677.579 | 2943676.3878 | 3920250.5321 | 3679348.9179 | 3240119.3054 | 4321531.6655 | 4051123.2709 | 3556327.3356 | 5034730.8753 | 4713661.404 | 4123471.7502
|  |  | Weight kG |  | 28068.7642 | 27386.4628 | 26133.0537 | 31390.4987 | 30499.6211 | 28828.0942 | 34322.032 | 33278.2668 | 31294.6332 | 36114.5115 | 34987.2913 | 32832.6045 | 37917.8482 | 36712.382 | 34397.4064 | 40927.2877 | 39600.806 | 37038.7521

## Weights of Towers-Moose
400 kV DC Line
|  |  | Sl.No. | Particulars | Details of the line | Dimensions in mm
[6 empty] | a | b | c | d | Total | BW
a
|  |  | 1 | KEC International - 'A' Type | DVG-Hoody | 4030 | 8000 | 8000 | 25900 | 45930 | 10300
|  |  | 2 | KEC International - 'B' Type | DVG-Hoody | 8030 | 8000 | 8000 | 22000 | 46030 | 14900
|  |  | 3 | KEC International - 'C' Type | DVG-Hoody | 8030 | 8000 | 8000 | 22000 | 46030 | 14800
|  |  | 4 | KEC International - 'D' Type | DVG-Hoody | 8030 | 8000 | 8000 | 22000 | 46030 | 15800
b
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV DC with twin ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 48696.9568 | 46343.1146 | 39768.6378 | 66583.4724 | 63305.5392 | 54137.5818 | 83699.3987 | 79543.7536 | 67914.1274 | 94920.703 | 90191.2615 | 76953.1881 | 106850.706 | 101511.9659 | 86566.5106 | 128300.8501 | 121867.5018 | 103855.8728
|  | c | Top Condr | 38.5 | 198601.8493 | 188187.9833 | 162479.2357 | 271843.2673 | 257248.6732 | 221158.6393 | 342249.2968 | 323682.7834 | 277720.8098 | 388513.0579 | 367352.5901 | 314943.3171 | 437760.3166 | 413847.9363 | 354599.7374 | 526415.5505 | 497565.1061 | 426048.2954
|  |  | Middle Condr | 30.5 | 157333.9326 | 149083.9867 | 128717.3166 | 215356.3547 | 203794.4034 | 175203.5973 | 271132.5598 | 256424.0232 | 220012.5896 | 307783.0718 | 291019.5843 | 249500.5499 | 346797.1339 | 327853.5599 | 280916.6751 | 417030.501 | 394174.9542 | 337518.7795
|  |  | Bottm Condr. | 22.5 | 116066.0158 | 109979.9902 | 94955.3975 | 158869.442 | 150340.1337 | 129248.5554 | 200015.8228 | 189165.263 | 162304.3693 | 227053.0858 | 214686.5786 | 184057.7827 | 255833.9512 | 241859.1836 | 207233.6128 | 307645.4516 | 290784.8023 | 248989.2636
|  |  | TOTAL M |  | 613747.622 | 581800.5148 | 502032.5968 | 840003.5446 | 795255.629 | 683349.4082 | 1057408.326 | 1000499.2109 | 858036.8999 | 1200234.7529 | 1135382.7921 | 972963.6174 | 1352254.2724 | 1278975.1274 | 1095385.4007 | 1625889.7667 | 1537487.2798 | 1315915.0734
|  |  | Weight kG |  | 9107.2629 | 8867.0675 | 8236.8076 | 10654.511 | 10366.8386 | 9609.8005 | 11954.0295 | 11627.9013 | 10768.2702 | 12735.795 | 12386.9423 | 11466.7742 | 13518.3019 | 13146.9197 | 12166.8019 | 14823.082 | 14414.4716 | 13335.426
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 98520.9238 | 94765.7912 | 84278.5815 | 126899.0502 | 121726.5583 | 107188.1489 | 153661.4333 | 147202.2565 | 128994.5963 | 170981.7065 | 163702.9577 | 143163.1863 | 189210.875 | 181075.9451 | 158103.5242 | 221552.1558 | 211907.2882 | 184651.9265
|  | d | Top Condr | 38.5 | 385082.3701 | 369114.7865 | 330319.1141 | 496387.9298 | 473715.0835 | 418162.4219 | 603663.4025 | 574880.398 | 503984.2252 | 673847.1725 | 641186.0559 | 560546.2468 | 748158.3976 | 711461.2337 | 620685.6721 | 880782.2467 | 837003.4402 | 728462.6887
|  |  | Middle Condr | 30.5 | 305065.2542 | 292415.6101 | 261681.3761 | 393242.3859 | 375280.7804 | 331271.5291 | 478226.8513 | 455424.7309 | 399260.2304 | 533826.9808 | 507952.5897 | 444069.1046 | 592696.9124 | 563625.1332 | 491712.026 | 697762.5591 | 663080.6474 | 577093.8183
|  |  | Bottm Condr. | 22.5 | 225048.1383 | 215716.4337 | 193043.6381 | 290096.8421 | 276846.4774 | 244380.6362 | 352790.3001 | 335969.0638 | 294536.2355 | 393806.7891 | 374719.1236 | 327591.9624 | 437235.4272 | 415789.0327 | 362738.3798 | 514742.8715 | 489157.8547 | 425724.948
|  |  | TOTAL M |  | 1192333.5665 | 1143281.2454 | 1022497.3713 | 1536853.7458 | 1467390.5397 | 1294999.4181 | 1868207.8454 | 1780150.9995 | 1560553.093 | 2084770.5679 | 1984908.9269 | 1735330.7822 | 2313940.1562 | 2201789.1715 | 1921016.42 | 2722714.6117 | 2588991.7249 | 2253520.8434
|  |  | Weight kG |  | 15232.5669 | 14915.9441 | 14106.0464 | 17293.8018 | 16898.4575 | 15874.8267 | 19067.1948 | 18612.4108 | 17426.6329 | 20142.0348 | 19653.708 | 18376.6076 | 21220.2389 | 20699.6057 | 19334.8028 | 23018.4072 | 22446.03 | 20941.3655
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 155050.9039 | 149705.8755 | 134779.3019 | 195332.7502 | 188010.7033 | 167379.0106 | 233039.9466 | 223967.1964 | 198296.1373 | 257280.0742 | 247108.8963 | 218284.6612 | 282656.2388 | 271348.7684 | 239268.9996 | 327354.5392 | 314065.9006 | 276322.6543
| Ground Level | e | Top Condr | 38.5 | 596662.073 | 574393.2743 | 520749.2538 | 751154.9842 | 719316.6006 | 641681.756 | 900262.3106 | 859887.7353 | 760701.3667 | 997585.5823 | 951875.897 | 839205.8875 | 1100334.2363 | 1049131.532 | 922585.21 | 1282844.6179 | 1222128.1795 | 1071580.2822
|  |  | Middle Condr | 30.5 | 472680.3436 | 455038.8277 | 412541.6167 | 595070.8317 | 569848.2161 | 508345.2873 | 713194.8175 | 681209.7644 | 602633.5503 | 790295.0717 | 754083.5028 | 664825.4434 | 871693.356 | 831130.1747 | 730879.1924 | 1016279.5025 | 968179.4668 | 848914.2496
|  |  | Bottm Condr. | 22.5 | 348698.6141 | 335684.3811 | 304333.9795 | 438986.6791 | 420379.8315 | 375008.8185 | 526127.3244 | 502531.7934 | 444565.7338 | 583004.5611 | 556291.1086 | 490444.9992 | 643052.4758 | 613128.8174 | 539173.1747 | 749714.3871 | 714230.7542 | 626248.2169
|  |  | TOTAL M |  | 1753840.1979 | 1688875.4475 | 1530093.389 | 2208109.8939 | 2115584.4614 | 1886873.3412 | 2645238.9425 | 2528143.3261 | 2236708.7991 | 2930141.4811 | 2797684.8003 | 2467007.2292 | 3230686.2085 | 3082407.8371 | 2711332.6423 | 3764117.6277 | 3588421.9354 | 3147435.6179
|  |  | Weight kG |  | 18474.3521 | 18128.9653 | 17255.7237 | 20729.2958 | 20290.3432 | 19162.2094 | 22688.5458 | 22180.6901 | 20863.1044 | 23879.1302 | 23333.1622 | 21910.8597 | 25073.8831 | 24491.7184 | 22970.244 | 27064.861 | 26425.6671 | 24748.7139
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 261323.0329 | 252989.1192 | 229716.8741 | 323982.981 | 312619.9316 | 280533.3225 | 382265.6067 | 368279.534 | 328577.8441 | 419514.5421 | 403905.814 | 359507.4077 | 458326.524 | 441054.9152 | 391854.0143 | 526255.096 | 506116.4409 | 448656.7569
|  |  | Top Condr | 38.5 | 994416.0683 | 960301.4569 | 878743.6542 | 1230097.9658 | 1181029.0584 | 1061881.3637 | 1457846.044 | 1395680.1839 | 1243310.3659 | 1606189.5462 | 1535949.5292 | 1363065.1419 | 1762398.4368 | 1683926.4029 | 1490133.7305 | 2038691.7631 | 1946133.8452 | 1716615.6602
|  |  | Middle Condr | 30.5 | 787784.158 | 760758.297 | 696147.5702 | 974493.1937 | 935620.4228 | 841230.6907 | 1154916.9959 | 1105668.7171 | 984960.16 | 1272435.8743 | 1216791.1854 | 1079830.8267 | 1396185.7746 | 1334019.6179 | 1180495.5527 | 1615067.5006 | 1541742.3969 | 1359916.3022
|  |  | Bottm Condr. | 22.5 | 581152.2477 | 561215.1371 | 513551.4862 | 718888.4216 | 690211.7873 | 620580.0177 | 851987.9478 | 815657.2503 | 726609.9541 | 938682.2024 | 897632.8417 | 796596.5115 | 1029973.1124 | 984112.8328 | 870857.375 | 1191443.2382 | 1137350.9485 | 1003216.9443
|  |  | TOTAL M |  | 2824675.7805 | 2728451.1279 | 2494803.3451 | 3494919.2093 | 3357185.6676 | 3017907.3697 | 4140159.2588 | 3966104.4545 | 3533657.8485 | 4559668.014 | 4363215.4583 | 3873243.6793 | 5000976.397 | 4781679.0379 | 4233061.2317 | 5780762.6669 | 5522352.0162 | 4873470.1752
|  |  | Weight kG |  | 23445.4466 | 23042.6433 | 22033.9503 | 26079.1107 | 25560.0611 | 24234.1148 | 28384.5969 | 27781.5378 | 26223.2464 | 29787.9639 | 29139.1942 | 27454.3786 | 31196.1938 | 30504.5356 | 28701.2944 | 33540.2872 | 32782.0608 | 30795.9328
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV DC with Tripple ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 48696.9568 | 46343.1146 | 39768.6378 | 66583.4724 | 63305.5392 | 54137.5818 | 83699.3987 | 79543.7536 | 67914.1274 | 94920.703 | 90191.2615 | 76953.1881 | 106850.706 | 101511.9659 | 86566.5106 | 128300.8501 | 121867.5018 | 103855.8728
|  |  | Top Condr | 38.5 | 292726.9217 | 277128.2497 | 238868.4184 | 400535.8181 | 378674.8316 | 324963.3841 | 504172.43 | 476361.997 | 407958.2187 | 572270.5439 | 540574.7263 | 462576.0304 | 644758.3529 | 608940.5794 | 520764.539 | 775245.9582 | 732031.7558 | 625599.0119
|  |  | Middle Condr | 30.5 | 231900.5484 | 219543.1589 | 189233.4223 | 317307.5961 | 299989.1523 | 257438.525 | 399409.3277 | 377377.6859 | 323187.6797 | 453357.1841 | 428247.5104 | 366456.3357 | 510782.5913 | 482407.472 | 412553.7257 | 614155.889 | 579921.2611 | 495604.412
|  |  | Bottm Condr. | 22.5 | 171074.175 | 161958.068 | 139598.4263 | 234079.3742 | 221303.473 | 189913.666 | 294646.2253 | 278393.3749 | 238417.1408 | 334443.8243 | 315920.2946 | 270336.6411 | 376806.8296 | 355874.3646 | 304342.9124 | 453065.8197 | 427810.7664 | 365609.8122
|  |  | TOTAL M |  | 877422.632 | 830951.1933 | 716023.5982 | 1200513.3296 | 1135409.8806 | 974140.336 | 1511007.8048 | 1428203.4576 | 1222874.3363 | 1714999.3714 | 1620634.4616 | 1386530.9716 | 1932123.2483 | 1825493.2159 | 1560867.1753 | 2322944.8511 | 2194304.7958 | 1874921.6786
|  |  | Weight kG |  | 10889.2352 | 10596.946 | 9836.8631 | 12737.2729 | 12387.0901 | 11473.7062 | 14289.8054 | 13892.743 | 12855.3492 | 15223.8657 | 14799.1065 | 13688.5595 | 16158.8472 | 15706.6322 | 14523.6554 | 17717.9067 | 17220.3287 | 15917.8544
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 98520.9238 | 94765.7912 | 84278.5815 | 126899.0502 | 121726.5583 | 107188.1489 | 153661.4333 | 147202.2565 | 128994.5963 | 170981.7065 | 163702.9577 | 143163.1863 | 189210.875 | 181075.9451 | 158103.5242 | 221552.1558 | 211907.2882 | 184651.9265
|  |  | Top Condr | 38.5 | 572447.7028 | 548518.4546 | 490628.2359 | 737352.8117 | 703374.4471 | 620469.058 | 896293.5885 | 853158.4189 | 747353.3418 | 1000271.7159 | 951324.925 | 830980.4249 | 1110355.4745 | 1055360.5255 | 919893.4411 | 1306796.0026 | 1241189.257 | 1079220.6019
|  |  | Middle Condr | 30.5 | 453497.5308 | 434540.5939 | 388679.5116 | 584136.643 | 557218.7178 | 491540.4226 | 710050.7649 | 675878.7474 | 592059.1409 | 792423.0477 | 753647.0185 | 658309.1678 | 879632.259 | 836064.8319 | 728746.752 | 1035253.9761 | 983279.801 | 854966.9703
|  |  | Bottm Condr. | 22.5 | 334547.3588 | 320562.7332 | 286730.7872 | 430920.4744 | 411062.9886 | 362611.7872 | 523807.9413 | 498599.076 | 436764.94 | 584574.3794 | 555969.112 | 485637.9106 | 648909.0435 | 616769.1383 | 537600.063 | 763711.9496 | 725370.345 | 630713.3388
|  |  | TOTAL M |  | 1716091.6976 | 1644783.4632 | 1470622.9921 | 2210443.2214 | 2109376.7456 | 1860524.2359 | 2686221.7069 | 2558045.0423 | 2240863.3288 | 2997252.6492 | 2851866.2883 | 2491298.2691 | 3326420.2203 | 3163119.8923 | 2757417.1543 | 3913586.8256 | 3718846.4582 | 3234024.0474
|  |  | Weight kG |  | 18274.4558 | 17890.7511 | 16917.0598 | 20740.2453 | 20260.5525 | 19027.9444 | 22863.6274 | 22311.476 | 20882.4713 | 24151.0426 | 23558.0201 | 22018.4666 | 25442.6746 | 24810.3011 | 23164.6341 | 27596.9886 | 26901.6137 | 25086.8325
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 155050.9039 | 149705.8755 | 134779.3019 | 195332.7502 | 188010.7033 | 167379.0106 | 233039.9466 | 223967.1964 | 198296.1373 | 257280.0742 | 247108.8963 | 218284.6612 | 282656.2388 | 271348.7684 | 239268.9996 | 327354.5392 | 314065.9006 | 276322.6543
|  |  | Top Condr | 38.5 | 889817.2572 | 856436.1862 | 776273.4455 | 1119503.3934 | 1071776.7227 | 955748.0592 | 1341191.9507 | 1280669.4249 | 1132429.0541 | 1485879.3306 | 1417359.6867 | 1248969.886 | 1638619.2326 | 1561865.9729 | 1372742.7479 | 1909889.5593 | 1818876.3659 | 1593896.9922
|  |  | Middle Condr | 30.5 | 704920.1648 | 678475.4203 | 614969.8724 | 886879.3117 | 849069.8713 | 757151.0599 | 1062502.7142 | 1014556.2977 | 897119.1208 | 1177125.184 | 1122843.3882 | 989443.6759 | 1298126.9245 | 1237322.3941 | 1087497.5016 | 1513029.3912 | 1440928.0301 | 1262697.6172
|  |  | Bottm Condr. | 22.5 | 520023.0724 | 500514.6543 | 453666.2993 | 654255.2299 | 626363.0198 | 558554.0606 | 783813.4777 | 748443.1704 | 661809.1875 | 868371.0373 | 828327.0896 | 729917.4659 | 957634.6164 | 912778.8153 | 802252.2553 | 1116169.223 | 1062979.6943 | 931498.2422
|  |  | TOTAL M |  | 2530612.7281 | 2436203.8188 | 2207155.176 | 3184121.7169 | 3049497.1316 | 2719054.0089 | 3813569.0646 | 3643087.476 | 3221674.6868 | 4223972.1575 | 4031075.9888 | 3552757.8316 | 4656978.5649 | 4440998.9535 | 3904113.9012 | 5425596.9804 | 5169624.0549 | 4531416.8474
|  |  | Weight kG |  | 22191.5201 | 21773.639 | 20724.814 | 24892.5299 | 24360.6192 | 23002.9282 | 27242.0644 | 26626.1888 | 25038.8887 | 28670.4646 | 28008.1678 | 26294.0213 | 30104.1471 | 29397.7805 | 27563.5688 | 32493.6107 | 31717.8462 | 29695.5392
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 261323.0329 | 252989.1192 | 229716.8741 | 323982.981 | 312619.9316 | 280533.3225 | 382265.6067 | 368279.534 | 328577.8441 | 419514.5421 | 403905.814 | 359507.4077 | 458326.524 | 441054.9152 | 391854.0143 | 526255.096 | 506116.4409 | 448656.7569
|  |  | Top Condr | 38.5 | 1486448.2502 | 1435298.4601 | 1313265.046 | 1837917.8658 | 1764345.4094 | 1586047.4707 | 2177567.5508 | 2084358.0977 | 1856342.5529 | 2398785.2765 | 2293470.135 | 2034758.7675 | 2631715.5333 | 2514058.2793 | 2224065.5286 | 3043660.2772 | 2904884.8645 | 2561450.0591
|  |  | Middle Condr | 30.5 | 1177575.8865 | 1137054.6243 | 1040378.8027 | 1456012.8547 | 1397728.1815 | 1256479.1651 | 1725085.9818 | 1651244.7268 | 1470609.0354 | 1900336.3878 | 1816904.9121 | 1611951.7509 | 2084865.5523 | 1991656.5589 | 1761922.0422 | 2411211.3884 | 2301272.4251 | 2029200.6962
|  |  | Bottm Condr. | 22.5 | 868703.5228 | 838810.7884 | 767492.5594 | 1074107.8436 | 1031110.9535 | 926910.8595 | 1272604.4128 | 1218131.3558 | 1084875.5179 | 1401887.4992 | 1340339.6893 | 1189144.7343 | 1538015.5714 | 1469254.8385 | 1299778.5557 | 1778762.4996 | 1697659.9858 | 1496951.3332
|  |  | TOTAL M |  | 4083157.3551 | 3943361.4501 | 3606188.3023 | 5049553.5868 | 4849146.777 | 4358578.5941 | 5981006.8467 | 5727551.1593 | 5101623.8076 | 6586907.612 | 6300742.6362 | 5591249.2952 | 7224447.9274 | 6904925.6657 | 6110254.7954 | 8351192.823 | 7974570.6655 | 7034321.7694
|  |  | Weight kG |  | 28188.5195 | 27701.7688 | 26491.0034 | 31347.3404 | 30718.9858 | 29123.7067 | 34116.2554 | 33385.5624 | 31508.5504 | 35802.6352 | 35016.2858 | 32985.9226 | 37495.2747 | 36656.7292 | 34482.9068 | 40313.3105 | 39393.7989 | 36998.6027
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV DC with Quad ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 48696.9568 | 46343.1146 | 39768.6378 | 66583.4724 | 63305.5392 | 54137.5818 | 83699.3987 | 79543.7536 | 67914.1274 | 94920.703 | 90191.2615 | 76953.1881 | 106850.706 | 101511.9659 | 86566.5106 | 128300.8501 | 121867.5018 | 103855.8728
|  |  | Top Condr | 38.5 | 386851.9941 | 366068.5162 | 315257.601 | 529228.3688 | 500100.9901 | 428768.1288 | 666095.5632 | 629041.2106 | 538195.6276 | 756028.0299 | 713796.8625 | 610208.7436 | 851756.3893 | 804033.2225 | 686929.3405 | 1024076.366 | 966498.4056 | 825149.7284
|  |  | Middle Condr | 30.5 | 306467.1641 | 290002.331 | 249749.5281 | 419258.8376 | 396183.9012 | 339673.4527 | 527686.0955 | 498331.3487 | 426362.7699 | 598931.2964 | 565475.4365 | 483412.1216 | 674768.0487 | 636961.3841 | 544190.7763 | 811281.277 | 765667.568 | 653690.0446
|  |  | Bottm Condr. | 22.5 | 226082.3342 | 213936.1458 | 184241.4551 | 309289.3064 | 292266.8124 | 250578.7766 | 389276.6278 | 367621.4867 | 314529.9122 | 441834.5629 | 417154.0106 | 356615.4995 | 497779.7081 | 469889.5456 | 401452.212 | 598486.1879 | 564836.7305 | 482230.3608
|  |  | TOTAL M |  | 1141097.6421 | 1080101.8719 | 930014.5996 | 1561023.1146 | 1475564.1322 | 1264931.2638 | 1964607.2836 | 1855907.7044 | 1587711.7726 | 2229763.9899 | 2105886.1311 | 1800098.3258 | 2511992.2242 | 2372011.3044 | 2026348.9499 | 3019999.9354 | 2851122.3117 | 2433928.2839
|  |  | Weight kG |  | 12914.8006 | 12564.8891 | 11659.2653 | 15105.3561 | 14686.0616 | 13597.5218 | 16945.8819 | 16470.413 | 15233.9362 | 18053.2647 | 17544.611 | 16220.8801 | 19161.7622 | 18620.2144 | 17210.101 | 21010.1797 | 20414.2874 | 18861.6721
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 98520.9238 | 94765.7912 | 84278.5815 | 126899.0502 | 121726.5583 | 107188.1489 | 153661.4333 | 147202.2565 | 128994.5963 | 170981.7065 | 163702.9577 | 143163.1863 | 189210.875 | 181075.9451 | 158103.5242 | 221552.1558 | 211907.2882 | 184651.9265
|  |  | Top Condr | 38.5 | 759813.0355 | 727922.1227 | 650937.3578 | 978317.6936 | 933033.8107 | 822775.6942 | 1188923.7745 | 1131436.4398 | 990722.4584 | 1326696.2593 | 1261463.7941 | 1101414.603 | 1472552.5514 | 1399259.8173 | 1219101.21 | 1732809.7585 | 1645375.0738 | 1429978.515
|  |  | Middle Condr | 30.5 | 601929.8074 | 576665.5777 | 515677.6471 | 775030.9001 | 739156.6552 | 651809.3161 | 941874.6785 | 896332.764 | 784858.0515 | 1051019.1145 | 999341.4473 | 872549.2309 | 1166567.6056 | 1108504.5306 | 965781.478 | 1372745.3931 | 1303478.9546 | 1132840.1223
|  |  | Bottm Condr. | 22.5 | 444046.5792 | 425409.0327 | 380417.9364 | 571744.1067 | 545279.4998 | 480842.9381 | 694825.5825 | 661229.0882 | 578993.6445 | 775341.9697 | 737219.1005 | 643683.8589 | 860582.6599 | 817749.2439 | 712461.7461 | 1012681.0277 | 961582.8354 | 835701.7295
|  |  | TOTAL M |  | 2239849.8288 | 2146285.6811 | 1918748.6129 | 2884032.697 | 2751362.9515 | 2426049.0537 | 3504235.5685 | 3335939.0851 | 2921173.5646 | 3909734.7306 | 3718823.6498 | 3247265.7559 | 4338900.2845 | 4124450.6131 | 3593817.8886 | 5104459.0396 | 4848701.1915 | 4214527.2514
|  |  | Weight kG |  | 22269.5982 | 21799.5082 | 20611.6126 | 25269.8708 | 24681.8025 | 23176.7598 | 27854.7701 | 27177.6554 | 25432.0643 | 29422.2971 | 28694.9666 | 26814.015 | 30995.0803 | 30219.4103 | 28208.5631 | 33618.4583 | 32765.4126 | 30547.6189
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 38253.5492 | 36246.9428 | 31138.1286 | 53428.5109 | 50625.8954 | 43490.4441 | 68006.3098 | 64439.0095 | 55356.6731 | 77596.0425 | 73525.7086 | 63162.6502 | 87818.0653 | 83211.5308 | 71483.3072 | 106259.859 | 100685.9523 | 86494.8017
|  |  | Top Condr | 38.5 | 1182972.4415 | 1138479.0982 | 1031797.6372 | 1487851.8026 | 1424236.8449 | 1269814.3624 | 1782121.5908 | 1701451.1145 | 1504156.7415 | 1974173.0788 | 1882843.4764 | 1658733.8845 | 2176904.2288 | 2074600.4138 | 1822900.2858 | 2536934.5008 | 2415624.5523 | 2116213.7021
|  |  | Middle Condr | 30.5 | 937159.9861 | 901912.0128 | 817398.1282 | 1178687.7916 | 1128291.5265 | 1005956.8326 | 1411810.6109 | 1347902.8309 | 1191604.6913 | 1563955.2962 | 1491603.2735 | 1314061.9085 | 1724560.493 | 1643514.6136 | 1444115.8109 | 2009779.2798 | 1913676.5934 | 1676480.9847
|  |  | Bottm Condr. | 22.5 | 691347.5307 | 665344.9275 | 602998.6191 | 869523.7807 | 832346.208 | 742099.3027 | 1041499.631 | 994354.5474 | 879052.6411 | 1153737.5136 | 1100363.0706 | 969389.9325 | 1272216.7571 | 1212428.8133 | 1065331.3359 | 1482624.0589 | 1411728.6345 | 1236748.2674
|  |  | TOTAL M |  | 3177167.8875 | 3057036.8259 | 2768667.4188 | 4001924.5035 | 3830239.4793 | 3413111.314 | 4797903.1849 | 4580173.6503 | 4047277.3659 | 5317473.107 | 5070939.2815 | 4465562.904 | 5866045.8418 | 5589835.8637 | 4909830.8917 | 6840577.8741 | 6512928.8701 | 5703759.0041
|  |  | Weight kG |  | 24865.3336 | 24390.7156 | 23211.8418 | 27906.7109 | 27301.5417 | 25772.0778 | 30556.2425 | 29854.8697 | 28064.3955 | 32168.2073 | 31413.6509 | 29478.9706 | 33786.7901 | 32981.753 | 30910.6028 | 36485.5253 | 35601.0146 | 33316.1487
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 46.5 | 261323.0329 | 252989.1192 | 229716.8741 | 323982.981 | 312619.9316 | 280533.3225 | 382265.6067 | 368279.534 | 328577.8441 | 419514.5421 | 403905.814 | 359507.4077 | 458326.524 | 441054.9152 | 391854.0143 | 526255.096 | 506116.4409 | 448656.7569
|  |  | Top Condr | 38.5 | 1978480.432 | 1910295.4634 | 1747786.4379 | 2445737.7657 | 2347661.7604 | 2110213.5777 | 2897289.0576 | 2773036.0116 | 2469374.7399 | 3191381.0067 | 3050990.7407 | 2706452.3932 | 3501032.6298 | 3344190.1557 | 2957997.3267 | 4048628.7912 | 3863635.8838 | 3406284.458
|  |  | Middle Condr | 30.5 | 1567367.615 | 1513350.9515 | 1384610.0352 | 1937532.5157 | 1859835.9401 | 1671727.6394 | 2295254.9677 | 2196820.7364 | 1956257.9108 | 2528236.9014 | 2417018.6388 | 2144072.6751 | 2773545.3301 | 2649293.4999 | 2343348.5316 | 3207355.2762 | 3060802.4534 | 2698485.0901
|  |  | Bottm Condr. | 22.5 | 1156254.7979 | 1116406.4397 | 1021433.6325 | 1429327.2657 | 1372010.1197 | 1233241.7012 | 1693220.8778 | 1620605.4613 | 1443141.0818 | 1865092.7961 | 1783046.5368 | 1581692.957 | 2046058.0304 | 1954396.8442 | 1728699.7364 | 2366081.7611 | 2257969.023 | 1990685.7222
|  |  | TOTAL M |  | 5341638.9297 | 5158271.7722 | 4717573.2596 | 6604187.9643 | 6341107.8864 | 5699249.8184 | 7821854.4346 | 7488997.8641 | 6669589.7667 | 8614147.21 | 8238269.8141 | 7309254.911 | 9447919.4579 | 9028172.2936 | 7987448.3592 | 10921622.979 | 10426789.3149 | 9195173.3636
|  |  | Weight kG |  | 30091.8057 | 29570.8014 | 28279.4078 | 33459.5963 | 32786.3866 | 31082.7783 | 36413.7871 | 35630.5755 | 33624.8647 | 38213.5275 | 37370.507 | 35200.3951 | 40020.1835 | 39121.0861 | 36797.2206 | 43028.3383 | 42042.2822 | 39481.2546
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV SC with twin ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 31924.5524 | 29915.9949 | 25525.3011 | 43610.3983 | 40811.2669 | 34682.321 | 54797.2194 | 51247.4927 | 43469.2307 | 62132.4694 | 58092.1924 | 49236.6509 | 69931.4845 | 65370.4034 | 55371.5966 | 83954.7257 | 78458.2077 | 66406.8453
|  |  | All Condr | 22 | 159257.6941 | 147815.4018 | 126347.0004 | 217633.4039 | 201575.464 | 171390.9733 | 273795.6065 | 253351.0697 | 214868.9659 | 310715.3429 | 287406.6218 | 243504.815 | 350024.9541 | 323678.3964 | 274028.4112 | 420805.4237 | 389009.6759 | 329050.7177
|  |  | TOTAL M |  | 225346.514 | 209491.9973 | 179011.8818 | 307928.0696 | 285701.2397 | 242898.592 | 387312.3638 | 359030.3255 | 304503.2323 | 439475.7163 | 407239.4523 | 345054.3658 | 495002.6542 | 458571.8204 | 388263.7892 | 594960.7881 | 551004.3944 | 466125.8295
|  |  | Weight kG |  | 5772.4343 | 5565.668 | 5144.8712 | 6747.738 | 6499.645 | 5993.0248 | 7567.7061 | 7286.1673 | 6710.1083 | 8061.2245 | 7759.9424 | 7142.9455 | 8555.3413 | 8234.5004 | 7576.9953 | 9379.4581 | 9026.3279 | 8302.0465
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 65267.0537 | 62061.9035 | 55066.1062 | 83840.3878 | 79410.2117 | 69665.4798 | 101389.9121 | 95849.2417 | 83617.3123 | 112756.6041 | 106509.4586 | 92698.903 | 124724.0827 | 117739.5141 | 102283.9692 | 145962.2843 | 137678.4115 | 119330.1636
|  |  | Top Condr | 22 | 313630.8516 | 296127.5535 | 264087.8759 | 402140.5915 | 377121.2725 | 330878.0975 | 487793.1879 | 455908.2442 | 396585.034 | 543947.2875 | 507706.3934 | 440068.3637 | 603471.8371 | 562701.4302 | 486416.2514 | 709822.4176 | 661115.3711 | 569689.2634
|  |  | TOTAL M |  | 445659.7163 | 421302.4393 | 375388.9138 | 571610.8278 | 536972.3316 | 471119.3556 | 692997.1622 | 648977.1549 | 564813.9997 | 772415.1173 | 722440.6852 | 626640.8591 | 856504.0409 | 800334.6387 | 692429.1994 | 1006573.9664 | 939541.2471 | 810424.6501
|  |  | Weight kG |  | 7476.868 | 7269.6752 | 6862.1269 | 8467.7543 | 8207.1803 | 7687.4711 | 9323.6025 | 9022.6213 | 8417.2601 | 9843.3608 | 9519.6092 | 8865.9929 | 10365.3204 | 10019.6795 | 9319.781 | 11236.7539 | 10856.1528 | 10082.6419
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 103097.2597 | 98534.4625 | 88582.9301 | 129485.0975 | 123204.3476 | 109357.1662 | 154253.7075 | 146454.1239 | 129169.0896 | 170194.4498 | 161443.4044 | 142010.9188 | 186891.4427 | 177157.1993 | 155510.4714 | 216315.696 | 204869.3067 | 179376.6495
|  |  | Top Condr | 22 | 488781.7289 | 464401.6492 | 420367.8638 | 611481.3622 | 576294.5152 | 511831.2514 | 730593.5863 | 685728.424 | 602759.0171 | 808570.8813 | 757657.2196 | 663088.2111 | 891031.1811 | 833895.5598 | 727390.2467 | 1037739.4006 | 969844.8938 | 842716.3434
|  |  | TOTAL M |  | 659885.8845 | 627617.4709 | 567429.2401 | 826103.506 | 779871.2821 | 692562.9667 | 986516.2479 | 927800.3227 | 816026.6461 | 1091225.4677 | 1024705.2857 | 897605.0199 | 1201775.9333 | 1127222.7211 | 984346.0106 | 1398146.0271 | 1309688.8622 | 1139531.4777
|  |  | Weight kG |  | 9098.1364 | 8872.8989 | 8436.7247 | 10179.7065 | 9890.756 | 9320.6812 | 11124.2347 | 10788.1079 | 10117.4296 | 11699.7146 | 11337.5055 | 10611.1061 | 12278.0606 | 11891.1235 | 11111.9919 | 13243.2412 | 12817.4635 | 11955.87
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 174215.2138 | 167100.1417 | 151592.0488 | 215293.7333 | 205534.0432 | 183974.5638 | 253633.6836 | 241587.5125 | 214803.0194 | 278173.298 | 264715.1081 | 234713.8153 | 303761.4235 | 288857.9974 | 255572.3092 | 348574.8407 | 331183.1574 | 292259.5458
|  |  | Top Condr | 22 | 818052.2603 | 780744.3462 | 714162.5364 | 1005026.3327 | 950725.2943 | 852009.6282 | 1187040.1507 | 1117773.1497 | 990350.6638 | 1306043.4186 | 1227546.0529 | 1082348.8209 | 1431621.2111 | 1343720.2122 | 1180403.3102 | 1654198.7691 | 1550233.2742 | 1355986.8053
|  |  | TOTAL M |  | 1067878.2557 | 1020070.2379 | 931725.0846 | 1313308.455 | 1244366.299 | 1114926.1874 | 1550453.1804 | 1462943.9446 | 1296986.3939 | 1704934.0304 | 1605971.4615 | 1417422.8091 | 1867618.7914 | 1756980.6691 | 1545396.9616 | 2155384.9589 | 2024780.3637 | 1773842.723
|  |  | Weight kG |  | 11573.8778 | 11311.835 | 10810.9017 | 12835.1631 | 12493.7308 | 11826.0873 | 13945.9258 | 13546.6486 | 12755.1548 | 14624.1897 | 14193.4161 | 13334.2235 | 15306.0152 | 14845.7285 | 13923.1676 | 16442.9769 | 15937.0151 | 14916.7969
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV SC with Tripple ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 31924.5524 | 29915.9949 | 25525.3011 | 43610.3983 | 40811.2669 | 34682.321 | 54797.2194 | 51247.4927 | 43469.2307 | 62132.4694 | 58092.1924 | 49236.6509 | 69931.4845 | 65370.4034 | 55371.5966 | 83954.7257 | 78458.2077 | 66406.8453
|  |  | All Condr | 22 | 234827.2154 | 217618.0443 | 185693.6962 | 320780.469 | 296629.6848 | 251741.5843 | 403476.8304 | 372728.7231 | 315500.2409 | 457838.8079 | 422782.9594 | 357494.678 | 515718.5014 | 476093.6774 | 402257.4826 | 619932.2305 | 572111.574 | 482946.0642
|  |  | TOTAL M |  | 314420.3087 | 291768.3721 | 248963.8321 | 429507.5152 | 397741.6497 | 337607.8572 | 540167.6225 | 499740.7655 | 423117.3163 | 612890.1446 | 566807.5415 | 479414.2173 | 690305.6383 | 638223.712 | 539407.3958 | 829671.5552 | 766826.6017 | 647522.2744
|  |  | Weight kG |  | 6818.5004 | 6568.2955 | 6067.3871 | 7969.2777 | 7668.9183 | 7065.4503 | 8937.1254 | 8596.1892 | 7909.7722 | 9519.7358 | 9154.8532 | 8419.5529 | 10103.0915 | 9714.4908 | 8930.8341 | 11076.0951 | 10648.3461 | 9785.0023
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 65267.0537 | 62061.9035 | 55066.1062 | 83840.3878 | 79410.2117 | 69665.4798 | 101389.9121 | 95849.2417 | 83617.3123 | 112756.6041 | 106509.4586 | 92698.903 | 124724.0827 | 117739.5141 | 102283.9692 | 145962.2843 | 137678.4115 | 119330.1636
|  |  | Top Condr | 22 | 466386.9516 | 440086.2718 | 392305.0094 | 597541.2503 | 559948.3974 | 490972.2706 | 724473.2026 | 676564.4848 | 588074.3431 | 807686.7248 | 753232.6168 | 652340.0011 | 895888.8258 | 834628.2281 | 720839.2429 | 1053457.7214 | 980270.1168 | 843903.8829
|  |  | TOTAL M |  | 625331.4411 | 590626.6838 | 526197.9062 | 801441.0828 | 752013.596 | 659422.122 | 971380.1955 | 908513.025 | 790043.7251 | 1082625.4435 | 1011228.6291 | 876314.7589 | 1200444.903 | 1120174.9383 | 968157.5221 | 1410757.8107 | 1314931.0589 | 1132955.8854
|  |  | Weight kG |  | 8856.7249 | 8607.4509 | 8124.424 | 10026.6031 | 9712.4964 | 9094.9388 | 11038.5657 | 10675.3864 | 9955.0532 | 11653.5203 | 11262.7048 | 10484.5087 | 12271.2595 | 11853.8915 | 11020.2395 | 13302.8365 | 12843.0897 | 11921.3249
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 103097.2597 | 98534.4625 | 88582.9301 | 129485.0975 | 123204.3476 | 109357.1662 | 154253.7075 | 146454.1239 | 129169.0896 | 170194.4498 | 161443.4044 | 142010.9188 | 186891.4427 | 177157.1993 | 155510.4714 | 216315.696 | 204869.3067 | 179376.6495
|  |  | Top Condr | 22 | 729113.2676 | 692497.4154 | 626724.9913 | 911552.4065 | 858708.2615 | 762402.0014 | 1088673.8002 | 1021294.7545 | 897335.3177 | 1204622.1155 | 1128158.8562 | 986869.7721 | 1327227.8419 | 1241419.4224 | 1082300.236 | 1545333.1958 | 1443364.4009 | 1253444.5028
|  |  | TOTAL M |  | 927831.5169 | 881921.4406 | 797496.8016 | 1160652.7132 | 1094734.3678 | 971924.2959 | 1385739.8783 | 1301923.2246 | 1144449.7637 | 1532782.9887 | 1437777.5603 | 1258589.0822 | 1688091.5904 | 1581571.0755 | 1380035.1576 | 1964062.3494 | 1837615.7605 | 1597452.3027
|  |  | Weight kG |  | 10788.2893 | 10517.9953 | 10001.8998 | 12066.1625 | 11718.5101 | 11041.6567 | 13184.3548 | 12779.4072 | 11981.6434 | 13866.2287 | 13429.6246 | 12564.928 | 14551.7768 | 14085.1793 | 13157.1885 | 15696.241 | 15182.5729 | 14155.7203
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 174215.2138 | 167100.1417 | 151592.0488 | 215293.7333 | 205534.0432 | 183974.5638 | 253633.6836 | 241587.5125 | 214803.0194 | 278173.298 | 264715.1081 | 234713.8153 | 303761.4235 | 288857.9974 | 255572.3092 | 348574.8407 | 331183.1574 | 292259.5458
|  |  | Top Condr | 22 | 1223019.0647 | 1167011.461 | 1067417.0002 | 1501869.8621 | 1420354.4302 | 1272669.5667 | 1773343.6467 | 1669361.843 | 1478722.7878 | 1950830.9215 | 1832992.106 | 1615760.6868 | 2138112.8869 | 2006156.4011 | 1761819.8312 | 2470022.2486 | 2313946.9714 | 2023350.1956
|  |  | TOTAL M |  | 1503703.5305 | 1435770.9068 | 1311897.5386 | 1848011.4613 | 1749781.175 | 1567640.4132 | 2181433.0029 | 2056563.6964 | 1822572.4737 | 2398854.3411 | 2257552.5039 | 1991480.6592 | 2627945.1328 | 2469894.4956 | 2171117.4215 | 3033374.1875 | 2846689.0446 | 2492059.2037
|  |  | Weight kG |  | 13734.0661 | 13420.2497 | 12828.2667 | 15225.4576 | 14815.281 | 14023.0101 | 16542.036 | 16061.6111 | 15120.3006 | 17346.8236 | 16828.1724 | 15805.421 | 18156.2506 | 17601.8057 | 16502.8776 | 19506.5747 | 18896.79 | 17680.6082
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 400 kV SC with Quad ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 31924.5524 | 29915.9949 | 25525.3011 | 43610.3983 | 40811.2669 | 34682.321 | 54797.2194 | 51247.4927 | 43469.2307 | 62132.4694 | 58092.1924 | 49236.6509 | 69931.4845 | 65370.4034 | 55371.5966 | 83954.7257 | 78458.2077 | 66406.8453
|  |  | All Condr | 22 | 310396.7366 | 287420.6869 | 245040.392 | 423927.534 | 391683.9055 | 332092.1953 | 533158.0544 | 492106.3764 | 416131.516 | 604962.273 | 558159.2971 | 471484.541 | 681412.0486 | 628508.9584 | 530486.5541 | 819059.0372 | 755213.4721 | 636841.4108
|  |  | TOTAL M |  | 403494.1034 | 374044.7469 | 318915.7824 | 551086.9608 | 509782.0596 | 432317.1224 | 693022.8812 | 640451.2055 | 541731.4002 | 786304.5728 | 726375.6306 | 613774.0688 | 885608.6224 | 817875.6037 | 690551.0023 | 1064382.3223 | 982648.809 | 828918.7194
|  |  | Weight kG |  | 7724.1762 | 7436.9584 | 6867.0717 | 9027.0042 | 8682.1213 | 7995.3005 | 10122.9563 | 9731.4286 | 8950.0524 | 10782.7361 | 10363.6851 | 9526.5981 | 11443.3846 | 10997.0754 | 10104.8869 | 12545.339 | 12054.0431 | 11071.0688
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 65267.0537 | 62061.9035 | 55066.1062 | 83840.3878 | 79410.2117 | 69665.4798 | 101389.9121 | 95849.2417 | 83617.3123 | 112756.6041 | 106509.4586 | 92698.903 | 124724.0827 | 117739.5141 | 102283.9692 | 145962.2843 | 137678.4115 | 119330.1636
|  |  | Top Condr | 22 | 619143.0516 | 584044.9902 | 520522.1429 | 792941.9092 | 742775.5224 | 651066.4437 | 961153.2173 | 897220.7253 | 779563.6523 | 1071426.1622 | 998758.8402 | 864611.6385 | 1188305.8145 | 1106555.026 | 955262.2344 | 1397093.0251 | 1299424.8624 | 1118118.5023
|  |  | TOTAL M |  | 805003.1659 | 759950.9284 | 677006.8987 | 1031271.3377 | 967054.8604 | 847724.8884 | 1249763.2288 | 1168048.8952 | 1015273.4505 | 1392835.7697 | 1300016.5731 | 1125988.6588 | 1544385.7651 | 1440015.238 | 1243885.8447 | 1814941.6549 | 1690320.8708 | 1455487.1208
|  |  | Weight kG |  | 10048.8605 | 9763.6184 | 9215.408 | 11373.7714 | 11013.9621 | 10312.0614 | 12520.7947 | 12104.5468 | 11285.2072 | 13218.0679 | 12770.0462 | 11884.6126 | 13918.6117 | 13440.0711 | 12491.3186 | 15088.6143 | 14561.3821 | 13512.0799
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 103097.2597 | 98534.4625 | 88582.9301 | 129485.0975 | 123204.3476 | 109357.1662 | 154253.7075 | 146454.1239 | 129169.0896 | 170194.4498 | 161443.4044 | 142010.9188 | 186891.4427 | 177157.1993 | 155510.4714 | 216315.696 | 204869.3067 | 179376.6495
|  |  | Top Condr | 22 | 969444.8062 | 920593.1816 | 833082.1187 | 1211623.4507 | 1141122.0078 | 1012972.7515 | 1446754.0141 | 1356861.085 | 1191911.6184 | 1600673.3498 | 1498660.4927 | 1310651.3331 | 1763424.5026 | 1648943.2851 | 1437210.2252 | 2052926.991 | 1916883.9079 | 1664172.6622
|  |  | TOTAL M |  | 1195777.1494 | 1136225.4104 | 1027564.363 | 1495201.9204 | 1409597.4536 | 1251285.6252 | 1784963.5088 | 1676046.1264 | 1472872.8813 | 1974340.5098 | 1850849.8349 | 1619573.1446 | 2174407.2475 | 2035919.43 | 1775724.3046 | 2529978.6717 | 2365542.6589 | 2055373.1276
|  |  | Weight kG |  | 12247.3787 | 11938.514 | 11353.3111 | 13695.1863 | 13297.3646 | 12528.4184 | 14963.483 | 14499.7664 | 13592.5411 | 15737.2575 | 15237.1455 | 14253.3945 | 16515.376 | 15980.7926 | 14924.7063 | 17814.6155 | 17225.9592 | 16056.9613
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 32 | 174215.2138 | 167100.1417 | 151592.0488 | 215293.7333 | 205534.0432 | 183974.5638 | 253633.6836 | 241587.5125 | 214803.0194 | 278173.298 | 264715.1081 | 234713.8153 | 303761.4235 | 288857.9974 | 255572.3092 | 348574.8407 | 331183.1574 | 292259.5458
|  |  | Top Condr | 22 | 1627985.869 | 1553278.5757 | 1420671.464 | 1998713.3915 | 1889983.566 | 1693329.5052 | 2359647.1428 | 2220950.5363 | 1967094.9118 | 2595618.4244 | 2438438.1592 | 2149172.5528 | 2844604.5626 | 2668592.5899 | 2343236.3522 | 3285845.728 | 3077660.6686 | 2690713.5859
|  |  | TOTAL M |  | 1939528.8053 | 1851471.5757 | 1692069.9925 | 2382714.4677 | 2255196.0511 | 2020354.639 | 2812412.8254 | 2650183.4481 | 2348158.5536 | 3092774.6517 | 2909133.5463 | 2565538.5093 | 3388271.4742 | 3182808.322 | 2796837.8814 | 3911363.4161 | 3668597.7256 | 3210275.6843
|  |  | Weight kG |  | 15597.9003 | 15239.7045 | 14568.9142 | 17288.369 | 16819.3874 | 15919.5881 | 18782.6799 | 18232.9101 | 17162.5467 | 19696.6406 | 19102.9242 | 17939.3743 | 20616.129 | 19981.2781 | 18730.5991 | 22150.4272 | 21452.0139 | 20067.3113
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 765 kV SC with twin ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 38834.792 | 36690.7454 | 31489.1674 | 53074.8253 | 50087.9918 | 42831.1043 | 66704.0132 | 62916.8547 | 53709.4734 | 75640.0433 | 71329.7561 | 60848.1414 | 85140.7327 | 80275.0007 | 68440.929 | 102223.3233 | 96359.8316 | 82097.2794
|  |  | All Condr | 27 | 206741.2417 | 192627.8612 | 166629.4924 | 282883.7886 | 263085.2131 | 226551.9809 | 356115.9238 | 330914.9522 | 284354.7901 | 404251.7077 | 375523.1222 | 322413.291 | 455501.7174 | 423031.3832 | 362974.1396 | 547782.1453 | 508599.2765 | 436080.0989
|  |  | TOTAL M |  | 289460.4709 | 270297.8416 | 233522.4643 | 395994.4182 | 369137.2566 | 317521.8425 | 498377.8597 | 464209.5508 | 398476.3475 | 565648.4069 | 526705.4877 | 451750.2504 | 637255.256 | 593247.2347 | 508508.9413 | 766161.4459 | 713065.3007 | 610775.6758
|  |  | Weight kG |  | 10631.1825 | 10273.2588 | 9548.8544 | 12434.5901 | 12005.5174 | 11134.5775 | 13949.7463 | 13463.066 | 12473.4966 | 14861.4171 | 14340.7169 | 13281.1641 | 15774.066 | 15219.6548 | 14090.819 | 17296.0562 | 16685.9751 | 15442.8626
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 78979.5018 | 75558.3407 | 67264.499 | 101593.4327 | 96873.0335 | 85349.8497 | 122939.9709 | 117040.9917 | 102594.5596 | 136760.4423 | 130111.2112 | 113808.0569 | 151308.6971 | 143876.0211 | 125637.0403 | 177123.0514 | 168309.338 | 146664.0392
|  |  | Top Condr | 27 | 398309.0114 | 376703.0398 | 337993.8015 | 512410.4846 | 481586.6283 | 425865.3579 | 622664.5865 | 583427.4133 | 512061.8563 | 694904.4345 | 650329.0528 | 569018.9155 | 771461.8863 | 721334.351 | 629679.0023 | 908227.829 | 848368.0453 | 738587.5725
|  |  | TOTAL M |  | 561386.7491 | 531949.8358 | 476664.8131 | 722191.4075 | 680384.2542 | 601291.3272 | 876980.0805 | 823890.9381 | 722958.8764 | 978204.2281 | 917953.8386 | 803141.085 | 1085362.7601 | 1017660.4396 | 888402.7294 | 1276589.7055 | 1195815.9383 | 1041232.9457
|  |  | Weight kG |  | 15374.7632 | 14966.2397 | 14167.196 | 17438.2747 | 16926.0057 | 15911.8189 | 19216.4084 | 18625.6835 | 17447.538 | 20295.1434 | 19660.193 | 18389.6421 | 21377.8888 | 20700.4031 | 19341.1502 | 23184.7825 | 22439.3114 | 20938.7768
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 124527.4536 | 119657.286 | 107854.98 | 156642.3596 | 149955.067 | 133591.3684 | 186744.9581 | 178449.9196 | 158059.2911 | 206107.2877 | 196804.3047 | 173896.0659 | 226382.4806 | 216037.3651 | 190531.4122 | 262103.8428 | 249942.8252 | 219921.1055
|  |  | Top Condr | 27 | 615660.6771 | 585553.6557 | 532422.7397 | 772830.1251 | 729497.05 | 652005.1441 | 925089.1329 | 869926.5679 | 770416.9555 | 1024677.3104 | 962122.2469 | 848816.208 | 1129948.4371 | 1059787.1453 | 932280.7724 | 1317187.3835 | 1233867.6938 | 1081810.7743
|  |  | TOTAL M |  | 825235.7469 | 786239.679 | 713845.6297 | 1036268.8731 | 980501.1652 | 875861.5518 | 1239583.8281 | 1168834.9459 | 1035158.1673 | 1372201.7485 | 1292087.2124 | 1140221.9141 | 1512173.3402 | 1422416.7466 | 1251823.3045 | 1760751.7882 | 1654300.3476 | 1451300.8728
|  |  | Weight kG |  | 18640.8784 | 18195.1163 | 17337.2219 | 20888.8044 | 20318.9571 | 19204.1499 | 22846.2701 | 22184.7199 | 20877.6067 | 24037.3364 | 23325.0869 | 21911.4969 | 25233.5379 | 24473.2014 | 22958.7835 | 27228.6698 | 26392.7435 | 24720.4336
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 210154.1916 | 202560.0004 | 184162.0442 | 260130.2191 | 249745.3143 | 224281.8106 | 306693.5553 | 293894.1047 | 262328.8323 | 336474.1635 | 322182.3255 | 286857.0224 | 367515.571 | 351695.2872 | 312527.971 | 421861.366 | 403407.6671 | 357638.9035
|  |  | Top Condr | 27 | 1024265.5301 | 978177.1718 | 897934.5817 | 1262399.545 | 1195550.0754 | 1077131.0054 | 1493624.6299 | 1408523.521 | 1256105.1923 | 1644625.6186 | 1548270.0999 | 1374814.1622 | 1803876.3038 | 1696053.05 | 1501149.4366 | 2086000.7169 | 1958578.1608 | 1727044.688
|  |  | TOTAL M |  | 1328482.5045 | 1270709.3447 | 1164552.3889 | 1638546.5322 | 1555426.8984 | 1400580.4726 | 1937502.4309 | 1832141.8487 | 1634138.6974 | 2132059.5855 | 2012980.9002 | 1788290.5289 | 2336851.9356 | 2203786.7606 | 1951879.626 | 2698961.1736 | 2541969.148 | 2243536.4812
|  |  | Weight kG |  | 21023.3903 | 20561.1758 | 19683.5918 | 23348.244 | 22748.3361 | 21586.3328 | 25389.0214 | 24689.0501 | 23316.8185 | 26633.2707 | 25878.8314 | 24391.8012 | 27883.0599 | 27077.5657 | 25483.0467 | 29965.612 | 29081.0425 | 27320.6735
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 765 kV SC with Tripple ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 38834.792 | 36690.7454 | 31489.1674 | 53074.8253 | 50087.9918 | 42831.1043 | 66704.0132 | 62916.8547 | 53709.4734 | 75640.0433 | 71329.7561 | 60848.1414 | 85140.7327 | 80275.0007 | 68440.929 | 102223.3233 | 96359.8316 | 82097.2794
|  |  | All Condr | 27 | 301467.2648 | 280266.5494 | 241817.6305 | 412251.8232 | 382511.1589 | 328477.585 | 518805.7119 | 480949.7753 | 412084.882 | 588842.2847 | 545687.245 | 467135.3845 | 663407.3104 | 614631.4588 | 525805.0844 | 797660.4464 | 738801.0194 | 631546.2372
|  |  | TOTAL M |  | 401114.0343 | 373597.5634 | 322146.7227 | 548480.5206 | 509904.6189 | 437661.552 | 690140.313 | 641055.5968 | 549031.8068 | 783225.32 | 727277.9392 | 622334.182 | 882313.5784 | 819086.2438 | 700437.776 | 1060692.9993 | 984404.0951 | 841171.613
|  |  | Weight kG |  | 12514.7123 | 12077.8313 | 11215.375 | 14634.1514 | 14110.1429 | 13072.4244 | 16415.5576 | 15821.0312 | 14641.5041 | 17487.6036 | 16851.445 | 15588.3005 | 18560.874 | 17883.4686 | 16537.571 | 20350.8143 | 19605.3069 | 18122.9647
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 78979.5018 | 75558.3407 | 67264.499 | 101593.4327 | 96873.0335 | 85349.8497 | 122939.9709 | 117040.9917 | 102594.5596 | 136760.4423 | 130111.2112 | 113808.0569 | 151308.6971 | 143876.0211 | 125637.0403 | 177123.0514 | 168309.338 | 146664.0392
|  |  | Top Condr | 27 | 588818.9193 | 556379.3174 | 498864.0943 | 756541.8672 | 710263.2817 | 627447.6504 | 918628.706 | 859718.467 | 753645.4813 | 1024821.3749 | 957896.141 | 837043.8213 | 1137347.5636 | 1062085.9105 | 925862.3785 | 1338328.9718 | 1248454.1726 | 1085307.4475
|  |  | TOTAL M |  | 785464.5028 | 743285.0735 | 665880.4514 | 1009338.7397 | 949353.7339 | 838392.4196 | 1225093.0778 | 1148864.4754 | 1007109.5361 | 1366252.5334 | 1279714.2476 | 1118391.9792 | 1515717.4938 | 1418452.4239 | 1236773.6165 | 1782474.6698 | 1666397.2412 | 1449044.8627
|  |  | Weight kG |  | 18186.1445 | 17691.1092 | 16744.6274 | 20615.5928 | 19993.6179 | 18788.8859 | 22712.341 | 21994.3817 | 20592.8147 | 23985.1725 | 23213.1383 | 21700.7317 | 25263.0911 | 24439.0738 | 22820.3585 | 27396.1187 | 26489.0648 | 24701.2125
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 124527.4536 | 119657.286 | 107854.98 | 156642.3596 | 149955.067 | 133591.3684 | 186744.9581 | 178449.9196 | 158059.2911 | 206107.2877 | 196804.3047 | 173896.0659 | 226382.4806 | 216037.3651 | 190531.4122 | 262103.8428 | 249942.8252 | 219921.1055
|  |  | Top Condr | 27 | 914846.4179 | 869655.2413 | 790507.5016 | 1147171.3279 | 1082128.9142 | 966657.3297 | 1372265.5255 | 1289467.1988 | 1141178.13 | 1519480.6887 | 1425585.9321 | 1256739.7599 | 1675077.3899 | 1569765.1019 | 1379765.0336 | 1951768.3036 | 1826703.6453 | 1600142.2503
|  |  | TOTAL M |  | 1158797.9293 | 1102984.5367 | 1001584.3307 | 1453621.8802 | 1373650.4306 | 1226667.2736 | 1738140.7882 | 1636580.7953 | 1448519.8009 | 1923858.035 | 1808802.875 | 1595015.8822 | 2119937.6096 | 1990991.1704 | 1750723.5074 | 2468246.0561 | 2315253.15 | 2029188.6354
|  |  | Weight kG |  | 22089.2623 | 21550.7341 | 20536.2488 | 24740.1929 | 24050.0215 | 22726.9285 | 27053.2741 | 26251.0139 | 24696.7369 | 28461.8986 | 27597.7055 | 25915.5161 | 29877.1313 | 28954.2302 | 27151.0193 | 32238.2592 | 31223.1416 | 29230.6563
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 210154.1916 | 202560.0004 | 184162.0442 | 260130.2191 | 249745.3143 | 224281.8106 | 306693.5553 | 293894.1047 | 262328.8323 | 336474.1635 | 322182.3255 | 286857.0224 | 367515.571 | 351695.2872 | 312527.971 | 421861.366 | 403407.6671 | 357638.9035
|  |  | Top Condr | 27 | 1527753.6974 | 1458590.5154 | 1338775.2646 | 1881525.4578 | 1781208.4523 | 1604346.1217 | 2225068.771 | 2097362.6285 | 1869710.4853 | 2449403.1511 | 2304807.7115 | 2045736.6914 | 2685969.1899 | 2524163.9591 | 2233068.0299 | 3104988.3037 | 2913769.3459 | 2567993.1208
|  |  | TOTAL M |  | 1870336.4701 | 1787730.1851 | 1638985.1317 | 2304849.8396 | 2185712.4436 | 1967969.3807 | 2724682.6156 | 2573470.4962 | 2294500.7137 | 2998161.1659 | 2827166.6779 | 2510337.3547 | 3286160.2996 | 3094999.7209 | 2739570.4161 | 3795595.6146 | 3569945.9014 | 3148565.1846
|  |  | Weight kG |  | 24945.0687 | 24387.9795 | 23351.3687 | 27691.479 | 26966.299 | 25587.8622 | 30108.0615 | 29260.6811 | 27629.2396 | 31582.923 | 30669.0653 | 28899.5366 | 33065.0517 | 32088.923 | 30190.2054 | 35535.694 | 34463.2041 | 32365.4149
|  |  | Bending Moments at Ground Level - kG-m | [5 empty] | 765 kV SC with Quad ACSR Conductor
|  |  | A Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 38834.792 | 36690.7454 | 31489.1674 | 53074.8253 | 50087.9918 | 42831.1043 | 66704.0132 | 62916.8547 | 53709.4734 | 75640.0433 | 71329.7561 | 60848.1414 | 85140.7327 | 80275.0007 | 68440.929 | 102223.3233 | 96359.8316 | 82097.2794
|  |  | All Condr | 27 | 396193.2878 | 367905.2377 | 317005.7687 | 541619.8577 | 501937.1047 | 430403.189 | 681495.5 | 630984.5984 | 539814.9739 | 773432.8616 | 715851.3678 | 611857.478 | 871312.9033 | 806231.5344 | 688636.0292 | 1047538.7475 | 969002.7624 | 827012.3754
|  |  | TOTAL M |  | 512767.5977 | 476897.2853 | 410770.9812 | 700966.6229 | 650671.9812 | 557801.2615 | 881902.7662 | 817901.6428 | 699587.2661 | 1000802.2331 | 927850.3908 | 792918.1136 | 1127371.9008 | 1044925.253 | 892366.6106 | 1355224.5528 | 1255742.8895 | 1071567.5501
|  |  | Weight kG |  | 14149.6998 | 13645.8114 | 12664.4641 | 16543.8129 | 15939.2541 | 14757.9721 | 18556.5524 | 17870.532 | 16527.5275 | 19767.9245 | 19033.8182 | 17595.4796 | 20980.7275 | 20198.9853 | 18666.3153 | 23003.4286 | 22143.043 | 20454.8697
|  |  | B Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 78979.5018 | 75558.3407 | 67264.499 | 101593.4327 | 96873.0335 | 85349.8497 | 122939.9709 | 117040.9917 | 102594.5596 | 136760.4423 | 130111.2112 | 113808.0569 | 151308.6971 | 143876.0211 | 125637.0403 | 177123.0514 | 168309.338 | 146664.0392
|  |  | Top Condr | 27 | 779328.8272 | 736055.5949 | 659734.387 | 1000673.2498 | 938939.9351 | 829029.9429 | 1214592.8254 | 1136009.5206 | 995229.1063 | 1354738.3153 | 1265463.2291 | 1105068.727 | 1503233.241 | 1402837.47 | 1222045.7547 | 1768430.1147 | 1648540.3 | 1432027.3226
|  |  | TOTAL M |  | 1009542.2565 | 954620.3111 | 855096.0898 | 1296486.0719 | 1218323.2137 | 1075493.5121 | 1573206.075 | 1473838.0127 | 1291260.1958 | 1754300.8387 | 1641474.6567 | 1433642.8733 | 1946072.2275 | 1819244.4082 | 1585144.5036 | 2288359.634 | 2136978.5442 | 1856856.7797
|  |  | Weight kG |  | 20617.6711 | 20048.9989 | 18975.1325 | 23364.7578 | 22649.4998 | 21280.4719 | 25737.7254 | 24911.6351 | 23317.621 | 27178.7446 | 26290.2337 | 24569.5864 | 28625.7473 | 27677.2464 | 25835.1975 | 31041.271 | 29996.9734 | 27961.8924
|  |  | C Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 124527.4536 | 119657.286 | 107854.98 | 156642.3596 | 149955.067 | 133591.3684 | 186744.9581 | 178449.9196 | 158059.2911 | 206107.2877 | 196804.3047 | 173896.0659 | 226382.4806 | 216037.3651 | 190531.4122 | 262103.8428 | 249942.8252 | 219921.1055
|  |  | Top Condr | 27 | 1214032.1587 | 1153756.8268 | 1048592.2634 | 1521512.5307 | 1434760.7784 | 1281309.5153 | 1819441.9181 | 1709007.8297 | 1511939.3046 | 2014284.0671 | 1889049.6172 | 1664663.3119 | 2220206.3426 | 2079743.0586 | 1827249.2948 | 2586349.2238 | 2419539.5969 | 2118473.7263
|  |  | TOTAL M |  | 1492360.1117 | 1419729.3944 | 1289323.0317 | 1870974.8872 | 1766799.696 | 1577472.9953 | 2236697.7483 | 2104326.6447 | 1861881.4344 | 2475514.3215 | 2325518.5375 | 2049809.8503 | 2727701.879 | 2559565.5943 | 2249623.7102 | 3175740.324 | 2976205.9524 | 2607076.3979
|  |  | Weight kG |  | 25067.6818 | 24450.0721 | 23300.1237 | 28067.9915 | 27275.3928 | 25772.6053 | 30688.8777 | 29766.9223 | 27999.6993 | 32285.6904 | 31292.2837 | 29378.8062 | 33890.3308 | 32829.2143 | 30777.4261 | 36567.8855 | 35400.4552 | 33132.5022
|  |  | D Type |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
|  |  | Particulars | Ht. from GL | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3 | Terrain Cat-1 | Terrain Cat-2 | Terrain Cat-3
|  |  | Ground Wire | 38 | 210154.1916 | 202560.0004 | 184162.0442 | 260130.2191 | 249745.3143 | 224281.8106 | 306693.5553 | 293894.1047 | 262328.8323 | 336474.1635 | 322182.3255 | 286857.0224 | 367515.571 | 351695.2872 | 312527.971 | 421861.366 | 403407.6671 | 357638.9035
|  |  | Top Condr | 27 | 2031241.8646 | 1939003.859 | 1779615.9474 | 2500651.3706 | 2366866.8292 | 2131561.2379 | 2956512.9121 | 2786201.7359 | 2483315.7783 | 3254180.6836 | 3061345.3232 | 2716659.2205 | 3568062.076 | 3352274.8681 | 2964986.6233 | 4123975.8906 | 3868960.531 | 3408941.5537
|  |  | TOTAL M |  | 2412190.4357 | 2304751.0254 | 2113417.8746 | 2971153.1469 | 2815997.9888 | 2535358.2888 | 3511862.8003 | 3314799.1437 | 2954862.73 | 3864262.7464 | 3641352.4555 | 3232384.1805 | 4235468.6636 | 3986212.6812 | 3527261.2063 | 4892230.0555 | 4597922.6547 | 4053593.888
|  |  | Weight kG |  | 28328.9599 | 27690.8854 | 26516.5808 | 31440.3486 | 30608.4265 | 29043.2026 | 34181.6958 | 33208.8199 | 31354.0386 | 35855.6961 | 34806.1664 | 32793.3905 | 37538.3838 | 36417.0756 | 34256.5518 | 40343.9363 | 39111.6074 | 36723.575

## Wind on Tower
400 kV DC line with twin ACSR BTPS-Hiriyur
Moments due to wind on tower
Type of towe | Wind load | lever arm | Moments | Type of towe | Wind load | lever arm | Moments | Type of towe | Wind load | lever arm | Moments | Type of towe | Wind load | lever arm | Moments
A | 236 | 46.5 | 10974 | B | 544 | 46.5 | 25296 | C | 559 | 46.5 | 25993.5 | D | 389 | 46.5 | 18088.5
A | 798 | 38.5 | 30723 | B | 1381 | 38.5 | 53168.5 | C | 1379 | 38.5 | 53091.5 | D | 1655 | 38.5 | 63717.5
A | 1360 | 30.5 | 41480 | B | 2718 | 30.5 | 82899 | C | 2092 | 30.5 | 63806 | D | 2293 | 30.5 | 69936.5
A | 2621 | 22.5 | 58972.5 | B | 4320 | 22.5 | 97200 | C | 4284 | 22.5 | 96390 | D | 4454 | 22.5 | 100215
| Total |  | 142149.5 |  | Total |  | 258563.5 |  | Total |  | 239281 |  | Total |  | 251957.5
| %age of other load |  | 17.8747 |  | %age of other load |  | 17.6206 |  | %age of other load |  | 11.3104 |  | %age of other load |  | 7.505
|  |  | 1.1787 |  |  |  | 1.1762 |  |  |  | 1.1149 |  |  |  | 1.0762

## Abstract
ABSTRACT
CALCULATION OF WIND PRESSURES ON CONDUCTOR & GROUND WIRE.
AS PER THE REVISED CODE IS-802 (Part I / Section I ) :1995
WIND PRESSURE IN KG/SQ.M
(Reliability Level-1)
(FOR 400KV D/C TOWERS)
DESIGN DATA | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
PARTICULARS
I. WIND PRESSURE ON CONDUCTOR | 81.4845 | 76.6239 | 64.8293 | 113.8089 | 107.0201 | 90.5467 | 144.8613 | 136.2202 | 115.2521 | 165.2886 | 155.4289 | 131.5041 | 187.0626 | 175.9042 | 148.8277 | 226.3458 | 212.844 | 180.0815
TENSION AT 32 DEG FULL WIND IN KG | 5354.5234 | 5195.0563 | 4819.2839 | 6447.4812 | 6215.5257 | 5656.684 | 7506.135 | 7212.7829 | 6496.8328 | 8192.9641 | 7862.7393 | 7052.1395 | 8912.6403 | 8545.5434 | 7640.2799 | 10175.1366 | 9746.4899 | 8683.4
II. WIND PRESSURE ON GROUND WIRE. | 100.3948 | 95.1615 | 80.5441 | 140.2208 | 132.9116 | 112.4955 | 178.4797 | 169.1761 | 143.1896 | 203.6475 | 193.032 | 163.3811 | 230.4748 | 218.4608 | 184.9039 | 278.8745 | 264.3376 | 223.7337
TENSION AT 32 DEG FULL WIND IN KG | 2368.9911 | 2302.3636 | 2116.324 | 2867.838 | 2777.757 | 2522.4069 | 3326.5002 | 3216.9737 | 2904.2064 | 3616.4892 | 3495.2767 | 3148.1013 | 3915.997 | 3783.046 | 3401.3861 | 4433.8403 | 4281.1415 | 3841.6277
III. WIND PRESSURE ON INSULATORS. | 103.2548 | 102.8134 | 96.7629 | 144.2154 | 143.5988 | 135.1482 | 183.5641 | 182.7793 | 172.023 | 209.4489 | 208.5535 | 196.2804 | 237.0404 | 236.027 | 222.1371 | 286.8188 | 285.5927 | 268.7859
IV. WIND PRESSURE ON TOWERS. | 250.9624 | 250.3046 | 235.6153 | 350.5177 | 349.599 | 329.0825 | 446.1553 | 444.9859 | 418.8716 | 509.0688 | 507.7345 | 477.9377 | 576.1303 | 574.6203 | 540.8983 | 697.1177 | 695.2905 | 654.4869
(FOR 400KV S/C TOWERS)
DESIGN DATA | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
PARTICULARS
I. WIND PRESSURE ON CONDUCTOR | 75.896 | 69.578 | 58.0842 | 106.0036 | 97.1792 | 81.1259 | 134.9263 | 123.6942 | 103.2608 | 153.9526 | 141.1366 | 117.8219 | 174.2333 | 159.7291 | 133.343 | 210.8223 | 193.2722 | 161.3451
TENSION AT 32 DEG FULL WIND IN KG | 5171.3738 | 4968.3351 | 4614.206 | 6180.839 | 5880.6401 | 5342.6874 | 7168.7429 | 6785.4987 | 6087.3388 | 7813.0782 | 7379.8611 | 6584.7172 | 8490.262 | 8007.075 | 7114.8179 | 9681.8315 | 9115.3169 | 8061.1933
II. WIND PRESSURE ON GROUND WIRE. | 95.2666 | 88.778 | 74.5881 | 133.0583 | 123.9957 | 104.1768 | 169.3628 | 157.8275 | 132.601 | 193.2451 | 180.0832 | 151.2994 | 218.702 | 203.8062 | 171.2307 | 264.6294 | 246.6055 | 207.1891
TENSION AT 32 DEG FULL WIND IN KG | 2303.7019 | 2221.0268 | 2041.0349 | 2779.5726 | 2666.8803 | 2417.0583 | 3219.1848 | 3081.6264 | 2773.9134 | 3497.7254 | 3345.2483 | 3002.8962 | 3785.7331 | 3618.2894 | 3241.2721 | 4284.2295 | 4091.6455 | 3656.5807
III. WIND PRESSURE ON INSULATORS. | 94.4776 | 95.542 | 89.0659 | 131.9564 | 133.443 | 124.3978 | 167.9602 | 169.8525 | 158.3393 | 191.6447 | 193.8038 | 180.6671 | 216.8908 | 219.3343 | 204.4671 | 262.4379 | 265.3945 | 247.4052
IV. WIND PRESSURE ON TOWERS. | 236.1859 | 237.0231 | 222.0335 | 329.8794 | 331.0488 | 310.1128 | 419.886 | 421.3744 | 394.7261 | 479.0951 | 480.7935 | 450.3874 | 542.2081 | 544.1302 | 509.7187 | 656.0718 | 658.3976 | 616.7596
(FOR 765 KV S/C TOWERS)
DESIGN DATA | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
PARTICULARS
I. WIND PRESSURE ON CONDUCTOR | 77.663 | 71.3394 | 60.1968 | 108.4714 | 99.6394 | 84.0766 | 138.0675 | 126.8257 | 107.0166 | 157.5367 | 144.7097 | 122.1073 | 178.2897 | 163.7728 | 138.1929 | 215.7305 | 198.1651 | 167.2135
TENSION AT 32 DEG FULL WIND IN KG | 5228.9622 | 5024.4472 | 4677.4961 | 6265.0748 | 5964.1329 | 5440.3834 | 7275.6126 | 6892.4857 | 6215.4069 | 7933.5481 | 7500.9999 | 6731.2549 | 8624.3306 | 8142.3662 | 7279.8762 | 9838.5905 | 9274.2012 | 8257.1308
II. WIND PRESSURE ON GROUND WIRE. | 97.7814 | 91.9486 | 77.7952 | 136.5707 | 128.4241 | 108.6561 | 173.8336 | 163.4642 | 138.3026 | 198.3463 | 186.5147 | 157.8049 | 224.4752 | 211.085 | 178.5932 | 271.615 | 255.4128 | 216.0978
TENSION AT 32 DEG FULL WIND IN KG | 2335.7309 | 2261.4248 | 2081.5083 | 2822.9475 | 2722.0839 | 2473.8589 | 3271.9644 | 3149.0928 | 2844.2703 | 3556.1548 | 3420.0686 | 3081.3552 | 3849.8362 | 3700.4843 | 3327.8288 | 4357.8745 | 4186.2224 | 3756.6737
III. WIND PRESSURE ON INSULATORS. | 97.7321 | 98.0785 | 91.8759 | 136.5018 | 136.9857 | 128.3226 | 173.7459 | 174.3618 | 163.335 | 198.2462 | 198.949 | 186.3672 | 224.362 | 225.1573 | 210.9181 | 271.478 | 272.4404 | 255.2109
IV. WIND PRESSURE ON TOWERS. | 244.0508 | 243.153 | 228.2339 | 340.8643 | 339.6104 | 318.7729 | 433.868 | 432.272 | 405.7491 | 495.0488 | 493.2278 | 462.9647 | 560.2635 | 558.2025 | 523.9528 | 677.9188 | 675.4251 | 633.9829
ABSTRACT OF LOADING ON TOWERS
RELIABILITY CONDITIONS
(FOR 400KV D/C TOWERS) WITH TWIN ACSR MOOSE
DESIGN DATA | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'A' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 2579.2448 | 2443.9998 | 2110.1199 | 3530.432 | 3340.8919 | 2872.1901 | 4444.7961 | 4203.6725 | 3606.7638 | 5045.6241 | 4770.8129 | 4090.1729 | 5685.1989 | 5374.6485 | 4605.1914 | 6836.5656 | 6461.8845 | 5533.0947
LOAD ON THE GROUND WIRE IN KG | 523.6232 | 498.3131 | 427.6198 | 715.9513 | 680.7047 | 582.1245 | 899.9935 | 855.3092 | 730.2594 | 1020.6527 | 969.7985 | 827.4536 | 1148.9323 | 1091.5265 | 930.8227 | 1379.579 | 1310.4032 | 1116.7298
'B' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 5001.0697 | 4793.6985 | 4289.8586 | 6446.5965 | 6152.1439 | 5430.6808 | 7839.7844 | 7465.9792 | 6545.2497 | 8751.262 | 8327.0916 | 7279.8214 | 9716.3428 | 9239.7563 | 8060.8529 | 11438.7305 | 10870.1745 | 9460.5544
LOAD ON THE GROUND WIRE IN KG | 1059.3648 | 1018.987 | 906.2213 | 1364.5059 | 1308.8877 | 1152.5607 | 1652.2735 | 1582.82 | 1387.0387 | 1838.513 | 1760.2469 | 1539.3891 | 2034.5255 | 1947.0532 | 1700.0379 | 2382.2812 | 2278.573 | 1985.5046
'C' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 7748.8581 | 7459.6529 | 6762.9773 | 9755.2595 | 9341.774 | 8333.5293 | 11691.7183 | 11167.3732 | 9879.2385 | 12955.6569 | 12362.0246 | 10898.7778 | 14290.055 | 13625.0848 | 11981.6261 | 16660.3197 | 15871.7945 | 13916.627
LOAD ON THE GROUND WIRE IN KG | 1667.214 | 1609.7406 | 1449.2398 | 2100.3522 | 2021.6205 | 1799.7743 | 2505.8059 | 2408.2494 | 2132.2165 | 2766.4524 | 2657.0849 | 2347.1469 | 3039.3144 | 2917.7287 | 2572.7849 | 3519.9413 | 3377.0527 | 2971.2113
'D' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 12914.4944 | 12471.4475 | 11412.2552 | 15975.2983 | 15338.0397 | 13790.6671 | 18933.0655 | 18125.7167 | 16146.8879 | 20859.6045 | 19947.3965 | 17702.1447 | 22888.2914 | 21869.1741 | 19352.3861 | 26476.5164 | 25274.4655 | 22293.7099
LOAD ON THE GROUND WIRE IN KG | 2809.9251 | 2720.3131 | 2470.0739 | 3483.688 | 3361.5046 | 3016.4873 | 4110.3829 | 3959.995 | 3533.0951 | 4510.9091 | 4343.0733 | 3865.6711 | 4928.2422 | 4742.526 | 4213.484 | 5658.6569 | 5442.1123 | 4824.2662
(FOR 400KV D/C TOWERS) WITH TRIPPLE ACSR MOOSE
'A' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 3801.6483 | 3599.0682 | 3102.1873 | 5201.7639 | 4917.855 | 4220.3037 | 6547.6939 | 6186.5194 | 5298.1587 | 7432.085 | 7020.451 | 6007.4809 | 8373.4851 | 7908.3192 | 6763.1758 | 10068.1293 | 9506.9059 | 8124.6625
LOAD ON THE GROUND WIRE IN KG | 523.6232 | 498.3131 | 427.6198 | 715.9513 | 680.7047 | 582.1245 | 899.9935 | 855.3092 | 730.2594 | 1020.6527 | 969.7985 | 827.4536 | 1148.9323 | 1091.5265 | 930.8227 | 1379.579 | 1310.4032 | 1116.7298
'B' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 7434.3858 | 7123.6163 | 6371.7953 | 9576.0105 | 9134.7331 | 8058.0397 | 11640.1765 | 11079.9795 | 9705.8876 | 12990.5418 | 12354.8692 | 10791.9536 | 14420.201 | 13705.9809 | 11946.6681 | 16971.3767 | 16119.341 | 14015.852
LOAD ON THE GROUND WIRE IN KG | 1059.3648 | 1018.987 | 906.2213 | 1364.5059 | 1308.8877 | 1152.5607 | 1652.2735 | 1582.82 | 1387.0387 | 1838.513 | 1760.2469 | 1539.3891 | 2034.5255 | 1947.0532 | 1700.0379 | 2382.2812 | 2278.573 | 1985.5046
'C' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 11556.0683 | 11122.5479 | 10081.4733 | 14539.0051 | 13919.1782 | 12412.3125 | 17418.0773 | 16632.0705 | 14706.8708 | 19297.1342 | 18407.2687 | 16220.3881 | 21280.7693 | 20283.9737 | 17827.8279 | 24803.7605 | 23621.771 | 20699.9609
LOAD ON THE GROUND WIRE IN KG | 1667.214 | 1609.7406 | 1449.2398 | 2100.3522 | 2021.6205 | 1799.7743 | 2505.8059 | 2408.2494 | 2132.2165 | 2766.4524 | 2657.0849 | 2347.1469 | 3039.3144 | 2917.7287 | 2572.7849 | 3519.9413 | 3377.0527 | 2971.2113
'D' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 19304.5227 | 18640.2397 | 17055.3902 | 23869.0632 | 22913.5767 | 20598.0191 | 28280.0981 | 27069.5857 | 24108.3448 | 31153.0555 | 29785.3264 | 26425.4385 | 34178.1238 | 32650.1075 | 28883.9679 | 39528.0555 | 37725.7775 | 33265.5852
LOAD ON THE GROUND WIRE IN KG | 2809.9251 | 2720.3131 | 2470.0739 | 3483.688 | 3361.5046 | 3016.4873 | 4110.3829 | 3959.995 | 3533.0951 | 4510.9091 | 4343.0733 | 3865.6711 | 4928.2422 | 4742.526 | 4213.484 | 5658.6569 | 5442.1123 | 4824.2662
(FOR 400KV D/C TOWERS) WITH QUAD ACSR MOOSE
'A' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 5024.0519 | 4754.1366 | 4094.2546 | 6873.0957 | 6494.8181 | 5568.4173 | 8650.5917 | 8169.3664 | 6989.5536 | 9818.5458 | 9270.0891 | 7924.7889 | 11061.7713 | 10441.9899 | 8921.1603 | 13299.6931 | 12551.9273 | 10716.2302
LOAD ON THE GROUND WIRE IN KG | 523.6232 | 498.3131 | 427.6198 | 715.9513 | 680.7047 | 582.1245 | 899.9935 | 855.3092 | 730.2594 | 1020.6527 | 969.7985 | 827.4536 | 1148.9323 | 1091.5265 | 930.8227 | 1379.579 | 1310.4032 | 1116.7298
'B' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 9867.7018 | 9453.5341 | 8453.7319 | 12705.4246 | 12117.3222 | 10685.3986 | 15440.5685 | 14693.9797 | 12866.5254 | 17229.8215 | 16382.6467 | 14304.0858 | 19124.0591 | 18172.2054 | 15832.4832 | 22504.0228 | 21368.5075 | 18571.1495
LOAD ON THE GROUND WIRE IN KG | 1059.3648 | 1018.987 | 906.2213 | 1364.5059 | 1308.8877 | 1152.5607 | 1652.2735 | 1582.82 | 1387.0387 | 1838.513 | 1760.2469 | 1539.3891 | 2034.5255 | 1947.0532 | 1700.0379 | 2382.2812 | 2278.573 | 1985.5046
'C' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 15363.2785 | 14785.4428 | 13399.9693 | 19322.7507 | 18496.5824 | 16491.0956 | 23144.4362 | 22096.7677 | 19534.5031 | 25638.6114 | 24452.5127 | 21541.9985 | 28271.4835 | 26942.8625 | 23674.0297 | 32947.2013 | 31371.7474 | 27483.2948
LOAD ON THE GROUND WIRE IN KG | 411.3285 | 389.7521 | 334.8186 | 574.5001 | 544.3645 | 467.6392 | 731.2506 | 692.8926 | 595.233 | 834.366 | 790.599 | 679.1683 | 944.2803 | 894.7476 | 768.6377 | 1142.5791 | 1082.6446 | 930.0516
'D' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 25694.5511 | 24809.032 | 22698.5252 | 31762.8281 | 30489.1138 | 27405.3711 | 37627.1306 | 36013.4547 | 32069.8018 | 41446.5066 | 39623.2564 | 35148.7324 | 45467.9562 | 43431.041 | 38415.5497 | 52579.5947 | 50177.0894 | 44237.4605
LOAD ON THE GROUND WIRE IN KG | 2809.9251 | 2720.3131 | 2470.0739 | 3483.688 | 3361.5046 | 3016.4873 | 4110.3829 | 3959.995 | 3533.0951 | 4510.9091 | 4343.0733 | 3865.6711 | 4928.2422 | 4742.526 | 4213.484 | 5658.6569 | 5442.1123 | 4824.2662
(FOR 400KV S/C TOWERS) WITH TWIN ACSR MOOSE
DESIGN DATA | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'A' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 2412.9954 | 2239.6273 | 1914.3485 | 3297.4758 | 3054.1737 | 2596.8329 | 4148.4183 | 3838.6526 | 3255.5904 | 4707.8082 | 4354.6458 | 3689.4669 | 5303.4084 | 4904.2181 | 4151.9456 | 6375.8398 | 5894.086 | 4985.6169
LOAD ON THE GROUND WIRE IN KG | 498.8211 | 467.4374 | 398.8328 | 681.4125 | 637.676 | 541.9113 | 856.2066 | 800.7421 | 679.2067 | 970.8198 | 907.6905 | 769.3227 | 1092.6794 | 1021.4126 | 865.1812 | 1311.7926 | 1225.9095 | 1037.607
'B' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 4751.9826 | 4486.7811 | 4001.3315 | 6093.0393 | 5713.9587 | 5013.3045 | 7390.8059 | 6907.7007 | 6008.8642 | 8241.6256 | 7692.5211 | 6667.7025 | 9143.5127 | 8525.7792 | 7369.9432 | 10754.8851 | 10016.8996 | 8631.6555
LOAD ON THE GROUND WIRE IN KG | 1019.7977 | 969.7172 | 860.4079 | 1310.0061 | 1240.7846 | 1088.5231 | 1584.2174 | 1497.6444 | 1306.5205 | 1761.8219 | 1664.2103 | 1448.4204 | 1948.8138 | 1839.6799 | 1598.187 | 2280.6607 | 2151.2252 | 1864.5338
'C' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 7405.7838 | 7036.3886 | 6369.2101 | 9264.8691 | 8731.7351 | 7755.019 | 11069.5998 | 10389.8246 | 9132.7124 | 12251.074 | 11479.6548 | 10046.7911 | 13500.4724 | 12634.7812 | 11021.0643 | 15723.3243 | 14694.6196 | 12768.4294
LOAD ON THE GROUND WIRE IN KG | 1610.8947 | 1539.601 | 1384.1083 | 2023.2046 | 1925.0679 | 1708.7057 | 2410.2142 | 2288.3457 | 2018.267 | 2659.2883 | 2522.5532 | 2218.9206 | 2920.1788 | 2768.0812 | 2429.8511 | 3379.9327 | 3201.0829 | 2802.7601
'D' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 12394.7312 | 11829.4598 | 10820.6445 | 15227.6717 | 14404.9287 | 12909.2368 | 17985.4568 | 16935.9568 | 15005.3131 | 19788.5366 | 18599.1826 | 16399.2246 | 21691.2305 | 20359.3972 | 17884.8986 | 25063.6177 | 23488.3829 | 20545.2546
LOAD ON THE GROUND WIRE IN KG | 2722.1127 | 2610.9397 | 2368.6258 | 3363.9646 | 3211.4694 | 2874.6026 | 3963.0263 | 3774.8049 | 3356.2972 | 4346.4578 | 4136.1736 | 3667.4034 | 4746.2722 | 4513.4062 | 3993.3173 | 5446.4819 | 5174.7368 | 4566.5554
(FOR 400KV S/C TOWERS) WITH TRIPPLE ACSR MOOSE
'A' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 3557.9881 | 3297.2431 | 2813.5409 | 4860.3101 | 4494.3892 | 3814.2664 | 6113.2853 | 5647.4049 | 4780.3067 | 6936.9516 | 6405.8024 | 5416.586 | 7813.9167 | 7213.5406 | 6094.8103 | 9392.9126 | 8668.3572 | 7317.3646
LOAD ON THE GROUND WIRE IN KG | 498.8211 | 467.4374 | 398.8328 | 681.4125 | 637.676 | 541.9113 | 856.2066 | 800.7421 | 679.2067 | 970.8198 | 907.6905 | 769.3227 | 1092.6794 | 1021.4126 | 865.1812 | 1311.7926 | 1225.9095 | 1037.607
'B' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 7066.469 | 6667.9738 | 5944.0153 | 9053.6553 | 8484.0666 | 7438.9738 | 10976.8667 | 10250.977 | 8910.2173 | 12237.6776 | 11412.6154 | 9883.9394 | 13574.0731 | 12645.8822 | 10921.8067 | 15961.4806 | 14852.5775 | 12786.4225
LOAD ON THE GROUND WIRE IN KG | 1019.7977 | 969.7172 | 860.4079 | 1310.0061 | 1240.7846 | 1088.5231 | 1584.2174 | 1497.6444 | 1306.5205 | 1761.8219 | 1664.2103 | 1448.4204 | 1948.8138 | 1839.6799 | 1598.187 | 2280.6607 | 2151.2252 | 1864.5338
'C' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 11047.1707 | 10492.3851 | 9495.8332 | 13811.4001 | 13010.7312 | 11551.5455 | 16495.0576 | 15474.1629 | 13595.9897 | 18251.8502 | 17093.316 | 14952.5723 | 20109.5128 | 18809.3852 | 16398.4884 | 23414.1393 | 21869.1576 | 18991.5834
LOAD ON THE GROUND WIRE IN KG | 1610.8947 | 1539.601 | 1384.1083 | 2023.2046 | 1925.0679 | 1708.7057 | 2410.2142 | 2288.3457 | 2018.267 | 2659.2883 | 2522.5532 | 2218.9206 | 2920.1788 | 2768.0812 | 2429.8511 | 3379.9327 | 3201.0829 | 2802.7601
'D' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 18530.5919 | 17681.9918 | 16172.9849 | 22755.604 | 21520.5217 | 19282.8722 | 26868.8431 | 25293.3613 | 22404.8907 | 29558.0443 | 27772.6077 | 24481.2225 | 32395.6498 | 30396.3091 | 26694.2399 | 37424.5795 | 35059.8026 | 30656.8211
LOAD ON THE GROUND WIRE IN KG | 2722.1127 | 2610.9397 | 2368.6258 | 3363.9646 | 3211.4694 | 2874.6026 | 3963.0263 | 3774.8049 | 3356.2972 | 4346.4578 | 4136.1736 | 3667.4034 | 4746.2722 | 4513.4062 | 3993.3173 | 5446.4819 | 5174.7368 | 4566.5554
(FOR 400KV S/C TOWERS) WITH QUAD ACSR MOOSE
'A' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 4702.9809 | 4354.8589 | 3712.7332 | 6423.1445 | 5934.6046 | 5031.6999 | 8078.1523 | 7456.1572 | 6305.023 | 9166.095 | 8456.959 | 7143.7052 | 10324.425 | 9522.863 | 8037.6751 | 12409.9854 | 11442.6284 | 9649.1123
LOAD ON THE GROUND WIRE IN KG | 498.8211 | 467.4374 | 398.8328 | 681.4125 | 637.676 | 541.9113 | 856.2066 | 800.7421 | 679.2067 | 970.8198 | 907.6905 | 769.3227 | 1092.6794 | 1021.4126 | 865.1812 | 1311.7926 | 1225.9095 | 1037.607
'B' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 9380.9553 | 8849.1665 | 7886.6991 | 12014.2714 | 11254.1746 | 9864.6431 | 14562.9275 | 13594.2534 | 11811.5705 | 16233.7297 | 15132.7097 | 13100.1763 | 18004.6336 | 16765.9852 | 14473.6702 | 21168.0761 | 19688.2555 | 16941.1894
LOAD ON THE GROUND WIRE IN KG | 1019.7977 | 969.7172 | 860.4079 | 1310.0061 | 1240.7846 | 1088.5231 | 1584.2174 | 1497.6444 | 1306.5205 | 1761.8219 | 1664.2103 | 1448.4204 | 1948.8138 | 1839.6799 | 1598.187 | 2280.6607 | 2151.2252 | 1864.5338
'C' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 14688.5577 | 13948.3815 | 12622.4563 | 18357.9311 | 17289.7274 | 15348.072 | 21920.5154 | 20558.5013 | 18059.2669 | 24252.6265 | 22706.9772 | 19858.3535 | 26718.5531 | 24983.9892 | 21775.9125 | 31104.9544 | 29043.6956 | 25214.7373
LOAD ON THE GROUND WIRE IN KG | 1610.8947 | 1539.601 | 1384.1083 | 2023.2046 | 1925.0679 | 1708.7057 | 2410.2142 | 2288.3457 | 2018.267 | 2659.2883 | 2522.5532 | 2218.9206 | 2920.1788 | 2768.0812 | 2429.8511 | 3379.9327 | 3201.0829 | 2802.7601
'D' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 24666.4526 | 23534.5239 | 21525.3252 | 30283.5362 | 28636.1146 | 25656.5077 | 35752.2294 | 33650.7657 | 29804.4684 | 39327.5519 | 36946.0327 | 32563.2205 | 43100.0691 | 40433.2211 | 35503.5811 | 49785.5413 | 46631.2223 | 40768.3877
LOAD ON THE GROUND WIRE IN KG | 2722.1127 | 2610.9397 | 2368.6258 | 3363.9646 | 3211.4694 | 2874.6026 | 3963.0263 | 3774.8049 | 3356.2972 | 4346.4578 | 4136.1736 | 3667.4034 | 4746.2722 | 4513.4062 | 3993.3173 | 5446.4819 | 5174.7368 | 4566.5554
(FOR 765KV S/C TOWERS) WITH TWIN ACSR MOOSE
DESIGN DATA | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'A' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 2552.361 | 2378.1217 | 2057.1542 | 3492.3925 | 3247.9656 | 2796.938 | 4396.4929 | 4085.3698 | 3510.553 | 4990.7618 | 4636.0879 | 3980.411 | 5623.478 | 5222.6097 | 4481.1622 | 6762.7425 | 6279.0034 | 5383.7049
LOAD ON THE GROUND WIRE IN KG | 510.9841 | 482.773 | 414.3312 | 698.353 | 659.0525 | 563.5672 | 877.6844 | 827.8534 | 706.7036 | 995.2637 | 938.5494 | 800.6334 | 1120.2728 | 1056.25 | 900.5385 | 1345.0437 | 1267.8925 | 1080.2274
'B' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 4917.3952 | 4650.6548 | 4172.763 | 6326.0554 | 5945.5139 | 5257.597 | 7687.2171 | 7202.8076 | 6321.7513 | 8579.0671 | 8028.7537 | 7024.9249 | 9524.2208 | 8905.3624 | 7773.8148 | 11212.6892 | 10473.6796 | 9118.3651
LOAD ON THE GROUND WIRE IN KG | 1039.204 | 994.1887 | 885.0592 | 1336.7557 | 1274.6452 | 1123.0243 | 1617.6312 | 1540.013 | 1349.9284 | 1799.4795 | 1711.9896 | 1497.4744 | 1990.9039 | 1893.1055 | 1653.119 | 2330.5665 | 2214.5966 | 1929.79
'C' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 7600.7491 | 7229.0575 | 6573.1202 | 9541.1127 | 9006.1364 | 8049.4462 | 11420.8535 | 10739.8342 | 9511.3204 | 12650.3372 | 11878.0524 | 10479.2124 | 13949.9807 | 13083.7919 | 11509.6392 | 16261.5726 | 15232.9345 | 13355.6886
LOAD ON THE GROUND WIRE IN KG | 1638.5191 | 1574.438 | 1419.1445 | 2061.0837 | 1973.093 | 1757.7812 | 2457.1705 | 2348.0253 | 2079.7275 | 2711.938 | 2589.5303 | 2288.1061 | 2978.7169 | 2842.5969 | 2506.9923 | 3448.7348 | 3288.7214 | 2893.6988
'D' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 12645.2535 | 12076.2614 | 11085.6121 | 15585.1796 | 14759.8775 | 13297.9136 | 18439.8102 | 17389.1793 | 15507.4715 | 20304.02 | 19114.4457 | 16973.0143 | 22270.0778 | 20938.9265 | 18532.7091 | 25753.0953 | 24179.9773 | 21321.5394
LOAD ON THE GROUND WIRE IN KG | 2765.1867 | 2665.2632 | 2423.1848 | 3422.766 | 3286.1226 | 2951.0765 | 4035.4415 | 3867.0277 | 3451.6952 | 4427.2916 | 4239.2411 | 3774.4345 | 4835.7312 | 4627.5696 | 4112.2101 | 5550.8074 | 5307.9956 | 4705.775
(FOR 765KV D/C TOWERS) WITH TRIPPLE ACSR MOOSE
'A' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 3721.8181 | 3460.0809 | 2985.4028 | 5089.5287 | 4722.36 | 4055.2788 | 6405.0088 | 5937.6515 | 5087.4677 | 7269.6578 | 6736.8796 | 5767.1035 | 8190.2137 | 7588.0427 | 6491.4208 | 9847.6598 | 9121.0002 | 7796.8671
LOAD ON THE GROUND WIRE IN KG | 510.9841 | 482.773 | 414.3312 | 698.353 | 659.0525 | 563.5672 | 877.6844 | 827.8534 | 706.7036 | 995.2637 | 938.5494 | 800.6334 | 1120.2728 | 1056.25 | 900.5385 | 1345.0437 | 1267.8925 | 1080.2274
'B' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 7269.3694 | 6868.8805 | 6158.816 | 9340.0231 | 8768.6825 | 7746.2673 | 11341.0951 | 10613.8082 | 9304.2652 | 12652.1157 | 11825.8783 | 10333.8743 | 14041.3279 | 13112.1717 | 11430.3997 | 16522.5799 | 15413.0145 | 13398.8574
LOAD ON THE GROUND WIRE IN KG | 1039.204 | 994.1887 | 885.0592 | 1336.7557 | 1274.6452 | 1123.0243 | 1617.6312 | 1540.013 | 1349.9284 | 1799.4795 | 1711.9896 | 1497.4744 | 1990.9039 | 1893.1055 | 1653.119 | 2330.5665 | 2214.5966 | 1929.79
'C' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 11294.4002 | 10736.4845 | 9759.3519 | 14162.609 | 13359.6162 | 11934.0411 | 16941.5497 | 15919.3481 | 14088.6189 | 18759.0208 | 17599.8263 | 15515.3057 | 20679.9678 | 19379.8161 | 17034.1362 | 24095.905 | 22551.8969 | 19754.8426
LOAD ON THE GROUND WIRE IN KG | 1638.5191 | 1574.438 | 1419.1445 | 2061.0837 | 1973.093 | 1757.7812 | 2457.1705 | 2348.0253 | 2079.7275 | 2711.938 | 2589.5303 | 2288.1061 | 2978.7169 | 2842.5969 | 2506.9923 | 3448.7348 | 3288.7214 | 2893.6988
'D' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 18861.1568 | 18007.2903 | 16528.0897 | 23228.7094 | 21990.2278 | 19806.7422 | 27469.9848 | 25893.3658 | 23082.8455 | 30239.5451 | 28454.4162 | 25256.0085 | 33160.1135 | 31162.518 | 27568.7411 | 38333.1889 | 35972.4611 | 31703.6188
LOAD ON THE GROUND WIRE IN KG | 2765.1867 | 2665.2632 | 2423.1848 | 3422.766 | 3286.1226 | 2951.0765 | 4035.4415 | 3867.0277 | 3451.6952 | 4427.2916 | 4239.2411 | 3774.4345 | 4835.7312 | 4627.5696 | 4112.2101 | 5550.8074 | 5307.9956 | 4705.775
(FOR 765KV D/C TOWERS) WITH QUAD ACSR MOOSE
'A' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 4891.2752 | 4542.04 | 3913.6515 | 6686.6649 | 6196.7544 | 5313.6196 | 8413.5247 | 7789.9333 | 6664.3824 | 9548.5538 | 8837.6712 | 7553.796 | 10756.9494 | 9953.4757 | 8501.6794 | 12932.5771 | 11962.9971 | 10210.0293
LOAD ON THE GROUND WIRE IN KG | 510.9841 | 482.773 | 414.3312 | 698.353 | 659.0525 | 563.5672 | 877.6844 | 827.8534 | 706.7036 | 995.2637 | 938.5494 | 800.6334 | 1120.2728 | 1056.25 | 900.5385 | 1345.0437 | 1267.8925 | 1080.2274
'B' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 9621.3435 | 9087.1061 | 8144.869 | 12353.9907 | 11591.8511 | 10234.9376 | 14994.9732 | 14024.8089 | 12286.7791 | 16725.1644 | 15623.0028 | 13642.8238 | 18558.4351 | 17318.9811 | 15086.9846 | 21832.4706 | 20352.3494 | 17679.3497
LOAD ON THE GROUND WIRE IN KG | 1039.204 | 994.1887 | 885.0592 | 1336.7557 | 1274.6452 | 1123.0243 | 1617.6312 | 1540.013 | 1349.9284 | 1799.4795 | 1711.9896 | 1497.4744 | 1990.9039 | 1893.1055 | 1653.119 | 2330.5665 | 2214.5966 | 1929.79
'C' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 14988.0513 | 14243.9114 | 12945.5835 | 18784.1053 | 17713.096 | 15818.636 | 22462.2459 | 21098.8621 | 18665.9173 | 24867.7045 | 23321.6002 | 20551.3989 | 27409.9548 | 25675.8402 | 22558.6333 | 31930.2373 | 29870.8592 | 26153.9966
LOAD ON THE GROUND WIRE IN KG | 1638.5191 | 1574.438 | 1419.1445 | 2061.0837 | 1973.093 | 1757.7812 | 2457.1705 | 2348.0253 | 2079.7275 | 2711.938 | 2589.5303 | 2288.1061 | 2978.7169 | 2842.5969 | 2506.9923 | 3448.7348 | 3288.7214 | 2893.6988
'D' TYPE TOWER
LOAD ON THE CONDUCTOR IN KG | 25077.0601 | 23938.3192 | 21970.5673 | 30872.2391 | 29220.5781 | 26315.5708 | 36500.1594 | 34397.5523 | 30658.2195 | 40175.0702 | 37794.3867 | 33539.0027 | 44050.1491 | 41386.1095 | 36604.7731 | 50913.2826 | 47764.9448 | 42085.6982
LOAD ON THE GROUND WIRE IN KG | 2765.1867 | 2665.2632 | 2423.1848 | 3422.766 | 3286.1226 | 2951.0765 | 4035.4415 | 3867.0277 | 3451.6952 | 4427.2916 | 4239.2411 | 3774.4345 | 4835.7312 | 4627.5696 | 4112.2101 | 5550.8074 | 5307.9956 | 4705.775

## Abs-Wts.-Bersimis
ABSTRACT OF WEIGHTS OF TOWERS IN KG
AS PER RYLE'S FORMULA
(FOR 400KV D/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR BERSIMIS
'A' TYPE TOWER | 9418.3185 | 9165.1758 | 8502.1268 | 11039.8344 | 10736.956 | 9941.5707 | 12400.9217 | 12057.6633 | 11154.8985 | 13219.5481 | 12852.409 | 11886.2129 | 14038.8582 | 13648.0382 | 12619 | 15404.831 | 14974.8806 | 13842.1232
'B' TYPE TOWER | 15365.8826 | 15028.546 | 14166.2949 | 17553.1859 | 17132.487 | 16044.8505 | 19434.0887 | 18950.123 | 17690.5818 | 20574.0947 | 20054.3624 | 18697.7617 | 21717.71 | 21163.5202 | 19713.6296 | 23624.9556 | 23015.6133 | 21416.9532
'C' TYPE TOWER | 18456.7112 | 18087.9634 | 17156.4335 | 20858.4242 | 20389.7437 | 19187.1562 | 22946.278 | 22403.5518 | 20998.2138 | 24215.7674 | 23631.9916 | 22114.2414 | 25490.2037 | 24867.4276 | 23243.1036 | 27614.751 | 26930.5822 | 25139.1768
'D' TYPE TOWER | 23256.4211 | 22826.2008 | 21750.0917 | 26067.246 | 25511.93 | 24095.9905 | 28532.1595 | 27885.7649 | 26219.0368 | 30034.5173 | 29338.4186 | 27534.5948 | 31543.3219 | 30800.5574 | 28868.2216 | 34056.9235 | 33241.7836 | 31110.928
TRIPPLE ACSR MOOSE
'A' TYPE TOWER | 11279.1477 | 10970.807 | 10169.8386 | 13220.3302 | 12851.3161 | 11890.1547 | 14850.0705 | 14431.8065 | 13340.6963 | 15830.3523 | 15382.9669 | 14215.111 | 16811.4819 | 16335.2217 | 15091.3454 | 18447.271 | 17923.3035 | 16553.9805
'B' TYPE TOWER | 18441.1121 | 18031.5469 | 16992.4089 | 21064.5652 | 20553.2565 | 19240.6685 | 23322.3989 | 22733.8943 | 21212.7634 | 24691.3056 | 24059.1797 | 22420.3646 | 26064.7324 | 25390.5968 | 23638.7217 | 28355.4398 | 27614.0926 | 25682.0328
'C' TYPE TOWER | 22169.4906 | 21722.4286 | 20600.7945 | 25053.8077 | 24484.7952 | 23034.0997 | 27563.9695 | 26904.6114 | 25207.7317 | 29090.9152 | 28381.4961 | 26548.1902 | 30624.1078 | 29867.1479 | 27904.5687 | 33180.3616 | 32348.6064 | 30183.5071
'D' TYPE TOWER | 27952.6539 | 27431.6614 | 26136.7661 | 31332.5341 | 30658.9116 | 28951.2858 | 34300.3945 | 33515.6506 | 31503.2951 | 36110.2872 | 35264.9334 | 33086.0636 | 37928.401 | 37026.1699 | 34691.292 | 40957.8778 | 39967.4916 | 37391.8058
QUAD ACSR MOOSE
'A' TYPE TOWER | 13388.7074 | 13019.403 | 12064.2275 | 15692.5048 | 15250.4723 | 14104.0537 | 17626.8903 | 17125.8299 | 15824.2962 | 18790.4618 | 18254.5013 | 16861.3705 | 19955.0582 | 19384.4949 | 17900.6403 | 21896.7498 | 21269.0188 | 19635.469
'B' TYPE TOWER | 22477.0455 | 21974.7875 | 20705.4263 | 25673.616 | 25046.2463 | 23441.6696 | 28425.9117 | 27703.63 | 25843.42 | 30094.895 | 29318.9939 | 27314.5656 | 31769.5098 | 30941.9799 | 28799.0348 | 34562.6897 | 33652.577 | 31288.9486
'C' TYPE TOWER | 24839.1186 | 24329.757 | 23064.1719 | 28098.4844 | 27449.2518 | 25809.1725 | 30938.7633 | 30185.8491 | 28265.2085 | 32667.6389 | 31857.2849 | 29781.1601 | 34404.1993 | 33539.3113 | 31315.8885 | 37300.5242 | 36349.8693 | 33895.7888
'D' TYPE TOWER | 29835.1588 | 29276.8777 | 27893.9372 | 33443.4847 | 32721.0101 | 30895.1258 | 36614.1563 | 35772.145 | 33619.145 | 38548.2875 | 37641.0943 | 35309.3864 | 40491.46 | 39523.1148 | 37024.0201 | 43729.6446 | 42666.5511 | 39909.1898
(FOR 400KV S/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR BERSIMIS
'A' TYPE TOWER | 5951.4242 | 5733.878 | 5292.6894 | 6970.0722 | 6709.3234 | 6178.9185 | 7825.9461 | 7530.1442 | 6927.3556 | 8340.961 | 8024.4464 | 7378.9289 | 8856.5442 | 8519.5034 | 7831.6817 | 9716.3642 | 9345.433 | 8587.8503
'B' TYPE TOWER | 7527.4845 | 7307.4191 | 6875.3504 | 8574.2219 | 8297.8309 | 7748.1175 | 9477.8065 | 9158.5405 | 8518.5124 | 10026.5676 | 9683.0815 | 8992.0213 | 10577.6937 | 10210.9072 | 9470.8377 | 11497.8815 | 11093.8851 | 10275.8185
'C' TYPE TOWER | 9077.5699 | 8838.0506 | 8375.0359 | 10223.546 | 9916.2909 | 9311.7764 | 11224.7776 | 10867.0271 | 10155.5246 | 11835.1867 | 11449.4321 | 10678.4555 | 12448.9104 | 12036.5787 | 11209.2234 | 13473.6083 | 13019.5353 | 12103.9422
'D' TYPE TOWER | 11472.1017 | 11193.5446 | 10662.0842 | 12810.4266 | 12446.9173 | 11738.1809 | 13991.0157 | 13565.1027 | 12723.6526 | 14712.8738 | 14252.8481 | 13338.525 | 15439.1638 | 14947.127 | 13964.441 | 16651.4164 | 16109.8279 | 15021.6486
TRIPPLE ACSR MOOSE
'A' TYPE TOWER | 7045.5395 | 6781.8545 | 6255.1962 | 8251.3207 | 7935.1598 | 7301.6862 | 9264.7231 | 8905.9938 | 8185.875 | 9874.604 | 9490.7265 | 8719.4754 | 10485.1907 | 10076.3954 | 9254.5323 | 11503.4835 | 11053.5542 | 10148.2543
'B' TYPE TOWER | 8920.8059 | 8655.2588 | 8141.1763 | 10161.4171 | 9827.353 | 9171.8089 | 11233.8244 | 10847.6093 | 10083.4152 | 11885.4951 | 11469.8379 | 10644.2872 | 12540.1521 | 12096.1861 | 11211.7506 | 13633.4302 | 13144.2878 | 12166.23
'C' TYPE TOWER | 10762.2707 | 10473.8928 | 9923.8275 | 12121.6328 | 11750.8356 | 11030.381 | 13311.565 | 12879.3152 | 12029.8888 | 14037.6202 | 13571.3121 | 12650.2241 | 14767.908 | 14269.2989 | 13280.3276 | 15987.6204 | 15438.3261 | 14343.2318
'D' TYPE TOWER | 13605.3767 | 13270.6385 | 12640.0591 | 15194.176 | 14756.0568 | 13911.7805 | 16599.0501 | 16084.9567 | 15080.4355 | 17458.9485 | 16903.3522 | 15810.8644 | 18324.5724 | 17730.059 | 16555.1048 | 19770.0209 | 19115.3298 | 17813.2689
QUAD ACSR MOOSE
'A' TYPE TOWER | 7991.2329 | 7688.2862 | 7088.1872 | 9358.7755 | 8995.4711 | 8273.464 | 10508.3185 | 10096.0575 | 9275.1735 | 11200.1776 | 10758.998 | 9879.7729 | 11892.8581 | 11423.0271 | 10486.0621 | 13048.0853 | 12530.9617 | 11498.8242
'B' TYPE TOWER | 10124.1559 | 9819.8084 | 9235.0994 | 11532.1947 | 11148.9792 | 10402.4437 | 12750.2472 | 12307.0058 | 11436.1476 | 13490.6608 | 13013.5428 | 12072.4998 | 14234.5785 | 13724.8975 | 12716.5222 | 15477.0656 | 14915.4389 | 13800.0674
'C' TYPE TOWER | 12216.819 | 11886.7036 | 11261.5931 | 13760.3441 | 13335.3459 | 12515.168 | 15112.9048 | 14617.1556 | 13649.2406 | 15938.5669 | 15403.6207 | 14353.6382 | 16769.223 | 16197.1156 | 15069.423 | 18156.8139 | 17526.4237 | 16277.3211
'D' TYPE TOWER | 15446.7936 | 15064.0052 | 14347.897 | 17251.6358 | 16749.8261 | 15788.9323 | 18849.6263 | 18260.3301 | 17115.716 | 19828.2907 | 19191.2206 | 17945.7688 | 20813.7485 | 20131.8995 | 18791.9498 | 22459.6925 | 21708.6413 | 20223.1346
(FOR 765KV S/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR BERSIMIS
'A' TYPE TOWER | 10954.5555 | 10577.2398 | 9818.0044 | 12835.8023 | 12383.9047 | 11472.2547 | 14415.4655 | 13903.0298 | 12867.6633 | 15365.7585 | 14817.5386 | 13709.1018 | 16316.9743 | 15733.2841 | 14552.4733 | 17903.1033 | 17260.8334 | 15960.6151
'B' TYPE TOWER | 15484.0739 | 15049.6972 | 14203.2354 | 17661.8149 | 17117.713 | 16045.5107 | 19537.4757 | 18909.914 | 17664.7559 | 20675.4107 | 20000.6884 | 18657.7807 | 21817.6487 | 21097.5359 | 19660.688 | 23723.8985 | 22931.2498 | 21344.7158
'C' TYPE TOWER | 18607.2327 | 18132.7209 | 17222.5258 | 20987.7118 | 20380.9893 | 19199.1983 | 23061.6406 | 22356.5233 | 20970.1333 | 24324.3423 | 23564.6572 | 22064.5882 | 25593.0224 | 24781.5312 | 23173.6532 | 27709.9291 | 26817.016 | 25040.2163
'D' TYPE TOWER | 20848.1586 | 20356.2903 | 19425.4345 | 23314.683 | 22675.1484 | 21441.6758 | 25483.5081 | 24735.7607 | 23276.881 | 26807.5476 | 26000.665 | 24418.1632 | 28138.6124 | 27276.2234 | 25577.74 | 30358.5696 | 29410.2029 | 27532.5862
TRIPPLE ACSR MOOSE
'A' TYPE TOWER | 12926.2676 | 12465.2011 | 11558.699 | 15144.853 | 14592.4332 | 13503.2957 | 17008.4057 | 16381.8547 | 15144.5238 | 18129.6305 | 17459.2706 | 16134.4458 | 19252.0072 | 18538.2295 | 17126.7685 | 21123.6115 | 20338.1407 | 18783.7881
'B' TYPE TOWER | 18324.7279 | 17796.992 | 16790.3611 | 20899.093 | 20236.9563 | 18958.6625 | 23119.5661 | 22355.2224 | 20868.7456 | 24467.4916 | 23645.429 | 22041.382 | 25820.8688 | 24943.2822 | 23226.3343 | 28079.9066 | 27113.6467 | 25216.9918
'C' TYPE TOWER | 22046.6699 | 21471.7048 | 20390.9713 | 24865.4378 | 24128.626 | 22720.6523 | 27326.0032 | 26468.7408 | 24814.0455 | 28825.3327 | 27901.316 | 26109.6248 | 30332.3264 | 29344.974 | 27423.467 | 32847.6015 | 31760.7892 | 29636.1293
'D' TYPE TOWER | 24723.4832 | 24128.7888 | 23024.8127 | 27649.0312 | 26873.6789 | 25404.768 | 30227.5625 | 29319.7962 | 27578.6807 | 31803.3218 | 30823.2472 | 28932.9104 | 33388.2069 | 32340.3104 | 30310.0837 | 36032.5244 | 34879.678 | 32633.6671
QUAD ACSR MOOSE
'A' TYPE TOWER | 14634.7019 | 14102.6408 | 13069.5766 | 17145.7086 | 16508.0925 | 15266.4784 | 19255.2871 | 18532.0288 | 17121.2279 | 20524.6308 | 19750.7674 | 18240.099 | 21795.3186 | 20971.3061 | 19361.7644 | 23914.2807 | 23007.4676 | 21234.8806
'B' TYPE TOWER | 20780.6344 | 20173.5586 | 19028.94 | 23698.1955 | 22935.8387 | 21480.3015 | 26216.7068 | 25336.28 | 23642.4509 | 27746.057 | 26798.9755 | 24970.628 | 29281.8158 | 28270.632 | 26313.1631 | 31845.5484 | 30732.0266 | 28569.1523
'C' TYPE TOWER | 25017.6377 | 24357.1888 | 23129.3758 | 28215.1722 | 27367.7998 | 25765.2259 | 31009.3798 | 30022.8969 | 28137.6477 | 32712.7801 | 31649.2306 | 29607.0763 | 34425.2415 | 33288.5972 | 31097.8276 | 37283.9064 | 36032.5285 | 33609.3423
'D' TYPE TOWER | 28068.7642 | 27386.4628 | 26133.0537 | 31390.4987 | 30499.6211 | 28828.0942 | 34322.032 | 33278.2668 | 31294.6332 | 36114.5115 | 34987.2913 | 32832.6045 | 37917.8482 | 36712.382 | 34397.4064 | 40927.2877 | 39600.806 | 37038.7521
ABSTRACT OF VOLUMES AND WEIGHTS OF FOUNDATIONS
4% OF BM IN CASE OF 'A' TYPE AND 10% OF BM IN CASE OF OTHERS ASSUMED. REINFORCEMENT AT 4% OF WEIGHT OF CONCRETE ASSUMED.
(FOR 400KV D/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR BERSIMIS
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 10.9398 | 10.3596 | 8.9149 | 15.031 | 14.2176 | 12.1891 | 18.9658 | 17.9304 | 15.346 | 21.5524 | 20.3719 | 17.4241 | 24.3067 | 22.9722 | 19.6387 | 29.2669 | 27.656 | 23.6302
b) 1:3:6 Concrete | 1.094 | 1.036 | 0.89149 | 1.5031 | 1.4218 | 1.2189 | 1.8966 | 1.793 | 1.5346 | 2.1552 | 2.0372 | 1.7424 | 2.4307 | 2.2972 | 1.9639 | 2.9267 | 2.7656 | 2.363
c) Reinforcement | 787.666 | 745.8937 | 641.875 | 1082.2322 | 1023.6646 | 877.6176 | 1365.5363 | 1290.9863 | 1104.9091 | 1551.7743 | 1466.778 | 1254.5337 | 1750.084 | 1654.001 | 1413.9863 | 2107.2167 | 1991.2329 | 1701.3777
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 12.3073 | 11.6546 | 10.0293 | 16.9099 | 15.9948 | 13.7128 | 21.3365 | 20.1717 | 17.2642 | 24.2465 | 22.9184 | 19.6021 | 27.3451 | 25.8438 | 22.0935 | 32.9253 | 31.113 | 26.584
b) 1:3:6 Concrete | 1.8461 | 1.7482 | 1.5044 | 2.5365 | 2.3992 | 2.0569 | 3.2005 | 3.0257 | 2.5896 | 3.637 | 3.4378 | 2.9403 | 4.1018 | 3.8766 | 3.314 | 4.9388 | 4.667 | 3.9876
c) Reinforcement | 1476.8737 | 1398.5506 | 1203.5157 | 2029.1853 | 1919.3711 | 1645.533 | 2560.3806 | 2420.5993 | 2071.7047 | 2909.5767 | 2750.2088 | 2352.2507 | 3281.4075 | 3101.252 | 2651.2243 | 3951.0313 | 3733.5617 | 3190.0832
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 17.7772 | 16.8344 | 14.4868 | 24.4254 | 23.1035 | 19.8073 | 30.8194 | 29.1368 | 24.9372 | 35.0227 | 33.1044 | 28.3141 | 39.4984 | 37.3299 | 31.9129 | 47.5587 | 44.941 | 38.3992
b) 1:3:6 Concrete | 2.6666 | 2.5252 | 2.173 | 3.6638 | 3.4655 | 2.9711 | 4.6229 | 4.3705 | 3.7406 | 5.2534 | 4.9657 | 4.2471 | 5.9248 | 5.5995 | 4.7869 | 7.1338 | 6.7412 | 5.7599
c) Reinforcement | 2133.262 | 2020.1287 | 1738.4115 | 2931.0455 | 2772.4249 | 2376.8811 | 3698.3275 | 3496.4212 | 2992.4623 | 4202.7219 | 3972.5239 | 3397.6955 | 4739.8109 | 4479.5862 | 3829.5462 | 5707.0452 | 5392.9224 | 4607.898
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 12.6385 | 12.0897 | 10.7422 | 16.4927 | 15.7116 | 13.7801 | 20.2166 | 19.2223 | 16.7519 | 22.658 | 21.5277 | 18.7137 | 25.2469 | 23.9749 | 20.8024 | 29.876 | 28.3547 | 24.5525
b) 1:3:6 Concrete | 1.8958 | 1.8134 | 1.6113 | 2.4739 | 2.3567 | 2.067 | 3.0325 | 2.8833 | 2.5128 | 3.3987 | 3.2292 | 2.8071 | 3.787 | 3.5962 | 3.1204 | 4.4814 | 4.2532 | 3.6829
c) Reinforcement | 1516.6194 | 1450.7598 | 1289.063 | 1979.1263 | 1885.3953 | 1653.6095 | 2425.9953 | 2306.671 | 2010.2304 | 2718.9616 | 2583.3266 | 2245.6436 | 3029.6305 | 2876.9838 | 2496.2885 | 3585.1192 | 3402.5671 | 2946.3001
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 22.7493 | 21.7614 | 19.3359 | 29.6869 | 28.2809 | 24.8041 | 36.3899 | 34.6001 | 30.1535 | 40.7844 | 38.7499 | 33.6847 | 45.4445 | 43.1548 | 37.4443 | 53.7768 | 51.0385 | 44.1945
b) 1:3:6 Concrete | 3.4124 | 3.2642 | 2.9004 | 4.453 | 4.2421 | 3.7206 | 5.4585 | 5.19 | 4.523 | 6.1177 | 5.8125 | 5.0527 | 6.8167 | 6.4732 | 5.6166 | 8.0665 | 7.6558 | 6.6292
c) Reinforcement | 2729.915 | 2611.3677 | 2320.3135 | 3562.4273 | 3393.7115 | 2976.497 | 4366.7916 | 4152.0079 | 3618.4147 | 4894.1308 | 4649.9879 | 4042.1585 | 5453.3348 | 5178.5708 | 4493.3194 | 6453.2146 | 6124.6208 | 5303.3401
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 32.8601 | 31.4331 | 27.9297 | 42.8811 | 40.8502 | 35.8282 | 52.5632 | 49.9779 | 43.555 | 58.9108 | 55.9721 | 48.6556 | 65.642 | 62.3346 | 54.0863 | 77.6776 | 73.7223 | 63.8365
b) 1:3:6 Concrete | 4.929 | 4.715 | 4.1895 | 6.4322 | 6.1275 | 5.3742 | 7.8845 | 7.4967 | 6.5332 | 8.8366 | 8.3958 | 7.2983 | 9.8463 | 9.3502 | 8.1129 | 11.6516 | 11.0583 | 9.5755
c) Reinforcement | 3943.2105 | 3771.9756 | 3351.5639 | 5145.7283 | 4902.0278 | 4299.3846 | 6307.5878 | 5997.3447 | 5226.599 | 7069.3001 | 6716.6491 | 5838.6735 | 7877.0392 | 7480.1578 | 6490.3502 | 9321.3099 | 8846.6745 | 7660.3802
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 18.2343 | 17.513 | 15.7556 | 23.2886 | 22.2538 | 19.7061 | 28.1841 | 26.8667 | 23.6018 | 31.389 | 29.8938 | 26.1773 | 34.7798 | 33.1011 | 28.918 | 40.819 | 38.8215 | 33.8285
b) 1:3:6 Concrete | 2.7351 | 2.6269 | 2.3633 | 3.4933 | 3.3381 | 2.9559 | 4.2276 | 4.03 | 3.5403 | 4.7083 | 4.4841 | 3.9266 | 5.217 | 4.9652 | 4.3377 | 6.1229 | 5.8232 | 5.0743
c) Reinforcement | 2188.1154 | 2101.5559 | 1890.6695 | 2794.6318 | 2670.4542 | 2364.7369 | 3382.0973 | 3224.0024 | 2832.2156 | 3766.6743 | 3587.255 | 3141.2731 | 4173.5749 | 3972.1288 | 3470.1627 | 4898.2829 | 4658.5749 | 4059.4173
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 32.8217 | 31.5233 | 28.36 | 41.9195 | 40.0568 | 35.4711 | 50.7315 | 48.36 | 42.4832 | 56.5001 | 53.8088 | 47.1191 | 62.6036 | 59.5819 | 52.0524 | 73.4742 | 69.8786 | 60.8913
b) 1:3:6 Concrete | 4.9233 | 4.7285 | 4.254 | 6.2879 | 6.0085 | 5.3207 | 7.6097 | 7.254 | 6.3725 | 8.475 | 8.0713 | 7.0679 | 9.3905 | 8.9373 | 7.8079 | 11.0211 | 10.4818 | 9.1337
c) Reinforcement | 3938.6078 | 3782.8005 | 3403.2051 | 5030.3372 | 4806.8175 | 4256.5264 | 6087.7751 | 5803.2042 | 5097.988 | 6780.0138 | 6457.0589 | 5654.2915 | 7512.4348 | 7149.8318 | 6246.2928 | 8816.9092 | 8385.4348 | 7306.9512
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 47.4092 | 45.5337 | 40.9645 | 60.5504 | 57.8598 | 51.236 | 73.2788 | 69.8534 | 61.3647 | 81.6113 | 77.7239 | 68.0609 | 90.4275 | 86.0628 | 75.1869 | 106.1295 | 100.9358 | 87.954
b) 1:3:6 Concrete | 7.1114 | 6.8301 | 6.1447 | 9.0826 | 8.679 | 7.6854 | 10.9918 | 10.478 | 9.2047 | 12.2417 | 11.6586 | 10.2091 | 13.5641 | 12.9094 | 11.278 | 15.9194 | 15.1404 | 13.1931
c) Reinforcement | 5689.1001 | 5464.0452 | 4915.7407 | 7266.0426 | 6943.1809 | 6148.3159 | 8793.453 | 8382.4061 | 7363.7605 | 9793.3533 | 9326.8629 | 8167.3099 | 10851.2947 | 10327.5349 | 9022.4229 | 12735.5355 | 12112.2948 | 10554.4851
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 28.9512 | 27.8899 | 25.3223 | 36.3723 | 34.8391 | 31.0792 | 43.5762 | 41.6242 | 36.7971 | 48.286 | 46.0738 | 40.5824 | 53.2593 | 50.7806 | 44.6088 | 62.0856 | 59.1492 | 51.8091
b) 1:3:6 Concrete | 4.3427 | 4.1835 | 3.7983 | 5.4558 | 5.2259 | 4.6619 | 6.5364 | 6.2436 | 5.5196 | 7.2429 | 6.9111 | 6.0874 | 7.9889 | 7.6171 | 6.6913 | 9.3128 | 8.8724 | 7.7714
c) Reinforcement | 3474.1404 | 3346.7931 | 3038.6717 | 4364.6749 | 4180.6925 | 3729.5047 | 5229.1474 | 4994.8991 | 4415.6543 | 5794.3258 | 5528.8525 | 4869.888 | 6391.1124 | 6093.6675 | 5353.0544 | 7450.2771 | 7097.9058 | 6217.0954
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 52.1121 | 50.2019 | 45.5801 | 65.4701 | 62.7104 | 55.9426 | 78.4372 | 74.9235 | 66.2348 | 86.9149 | 82.9328 | 73.0483 | 95.8667 | 91.405 | 80.2958 | 111.7542 | 106.4686 | 93.2564
b) 1:3:6 Concrete | 7.8168 | 7.5303 | 6.837 | 9.8205 | 9.4066 | 8.3914 | 11.7656 | 11.2385 | 9.9352 | 13.0372 | 12.4399 | 10.9572 | 14.38 | 13.7108 | 12.0444 | 16.7631 | 15.9703 | 13.9885
c) Reinforcement | 6253.4527 | 6024.2276 | 5469.6091 | 7856.4147 | 7525.2465 | 6713.1085 | 9412.4653 | 8990.8184 | 7948.1777 | 10429.7864 | 9951.9344 | 8765.7985 | 11504.0023 | 10968.6014 | 9635.498 | 13410.4987 | 12776.2305 | 11190.7716
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 75.273 | 72.5139 | 65.8379 | 94.568 | 90.5817 | 80.8059 | 113.2982 | 108.2228 | 95.6725 | 125.5437 | 119.7918 | 105.5142 | 138.4741 | 132.0295 | 115.9828 | 161.4227 | 153.788 | 134.7037
b) 1:3:6 Concrete | 11.291 | 10.8771 | 9.8757 | 14.1852 | 13.5873 | 12.1209 | 16.9947 | 16.2334 | 14.3509 | 18.8316 | 17.9688 | 15.8271 | 20.7711 | 19.8044 | 17.3974 | 24.2134 | 23.0682 | 20.2056
c) Reinforcement | 9032.765 | 8701.662 | 7900.5464 | 11348.1546 | 10869.8006 | 9696.7123 | 13595.7833 | 12986.7377 | 11480.7011 | 15065.2471 | 14375.0164 | 12661.7089 | 16616.8922 | 15843.5354 | 13917.9415 | 19370.7204 | 18454.5551 | 16164.4479
TRIPPLE ACSR BERSIMIS
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 9.8061 | 9.2773 | 7.9721 | 13.4719 | 12.7303 | 10.8973 | 16.9981 | 16.054 | 13.7183 | 19.3163 | 18.2399 | 15.5755 | 21.7849 | 20.568 | 17.5549 | 26.2305 | 24.7616 | 21.1226
b) 1:3:6 Concrete | 1.4709 | 1.3916 | 1.1958 | 2.0208 | 1.9095 | 1.6346 | 2.5497 | 2.4081 | 2.0577 | 2.8974 | 2.736 | 2.3363 | 3.2677 | 3.0852 | 2.6332 | 3.9346 | 3.7142 | 3.1684
c) Reinforcement | 1176.7295 | 1113.2719 | 956.6481 | 1616.6228 | 1527.6339 | 1307.6728 | 2039.7696 | 1926.4844 | 1646.1943 | 2317.9563 | 2188.791 | 1869.0659 | 2614.1836 | 2468.1648 | 2106.5899 | 3147.6638 | 2971.3938 | 2534.714
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 17.6509 | 16.6991 | 14.3497 | 24.2493 | 22.9145 | 19.6151 | 30.5965 | 28.8973 | 24.6929 | 34.7693 | 32.8319 | 28.036 | 39.2128 | 37.0225 | 31.5988 | 47.215 | 44.5709 | 38.0207
b) 1:3:6 Concrete | 2.6476 | 2.5049 | 2.1525 | 3.6374 | 3.4372 | 2.9423 | 4.5895 | 4.3346 | 3.7039 | 5.2154 | 4.9248 | 4.2054 | 5.8819 | 5.5534 | 4.7398 | 7.0822 | 6.6856 | 5.7031
c) Reinforcement | 2118.1132 | 2003.8894 | 1721.9666 | 2909.921 | 2749.7411 | 2353.8111 | 3671.5853 | 3467.6718 | 2963.1497 | 4172.3214 | 3939.8239 | 3364.3185 | 4705.5305 | 4442.6966 | 3791.8619 | 5665.7949 | 5348.5088 | 4562.4853
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 25.4958 | 24.1209 | 20.7274 | 35.0268 | 33.0987 | 28.3329 | 44.195 | 41.7405 | 35.6675 | 50.2224 | 47.4238 | 40.4964 | 56.6406 | 53.4769 | 45.6428 | 68.1994 | 64.3802 | 54.9188
b) 1:3:6 Concrete | 3.8244 | 3.6181 | 3.1091 | 5.254 | 4.9648 | 4.2499 | 6.6293 | 6.2611 | 5.3501 | 7.5334 | 7.1136 | 6.0745 | 8.4961 | 8.0215 | 6.8464 | 10.2299 | 9.657 | 8.2378
c) Reinforcement | 3059.4968 | 2894.5069 | 2487.2851 | 4203.2192 | 3971.8482 | 3399.9493 | 5303.4011 | 5008.8593 | 4280.1051 | 6026.6864 | 5690.8567 | 4859.5712 | 6796.8773 | 6417.2285 | 5477.1339 | 8183.926 | 7725.6238 | 6590.2565
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 18.2035 | 17.4039 | 15.4558 | 23.7512 | 22.6121 | 19.8162 | 29.1157 | 27.6648 | 24.0866 | 32.6339 | 30.9843 | 26.907 | 36.3653 | 34.5085 | 29.9108 | 43.0381 | 40.8171 | 35.3052
b) 1:3:6 Concrete | 2.7305 | 2.6106 | 2.3184 | 3.5627 | 3.3918 | 2.9724 | 4.3674 | 4.1497 | 3.613 | 4.8951 | 4.6476 | 4.0361 | 5.4548 | 5.1763 | 4.4866 | 6.4557 | 6.1226 | 5.2958
c) Reinforcement | 2184.4183 | 2088.4668 | 1854.6907 | 2850.1427 | 2713.4566 | 2377.9456 | 3493.8804 | 3319.7797 | 2890.3877 | 3916.0633 | 3718.1185 | 3228.8431 | 4363.8332 | 4141.0208 | 3589.2985 | 5164.5724 | 4898.0493 | 4236.6286
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 32.7663 | 31.327 | 27.8204 | 42.7521 | 40.7018 | 35.6692 | 52.4082 | 49.7967 | 43.3558 | 58.741 | 55.7718 | 48.4326 | 65.4575 | 62.1153 | 53.8395 | 77.4686 | 73.4707 | 63.5494
b) 1:3:6 Concrete | 4.9149 | 4.6991 | 4.1731 | 6.4128 | 6.1053 | 5.3504 | 7.8612 | 7.4695 | 6.5034 | 8.8111 | 8.3658 | 7.2649 | 9.8186 | 9.3173 | 8.0759 | 11.6203 | 11.0206 | 9.5324
c) Reinforcement | 3931.953 | 3759.2402 | 3338.4433 | 5130.2568 | 4884.2219 | 4280.3021 | 6288.9847 | 5975.6035 | 5202.6978 | 7048.914 | 6692.6133 | 5811.9175 | 7854.8997 | 7453.8375 | 6460.7373 | 9296.2304 | 8816.4887 | 7625.9314
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 47.3291 | 45.2501 | 40.185 | 61.7531 | 58.7916 | 51.5222 | 75.7007 | 71.9286 | 62.6251 | 84.848 | 80.5592 | 69.9583 | 94.5497 | 89.7221 | 77.7681 | 111.8991 | 106.1244 | 91.7936
b) 1:3:6 Concrete | 7.0994 | 6.7875 | 6.0277 | 9.263 | 8.8187 | 7.7283 | 11.3551 | 10.7893 | 9.3938 | 12.7272 | 12.0839 | 10.4937 | 14.1825 | 13.4583 | 11.6652 | 16.7849 | 15.9187 | 13.769
c) Reinforcement | 5679.4877 | 5430.0136 | 4822.1959 | 7410.3709 | 7054.9872 | 6182.6585 | 9084.0891 | 8631.4273 | 7515.0079 | 10181.7647 | 9667.1081 | 8394.992 | 11345.9662 | 10766.6542 | 9332.176 | 13427.8883 | 12734.9281 | 11015.2343
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 26.3082 | 25.2579 | 22.7169 | 33.5991 | 32.0903 | 28.4003 | 40.669 | 38.7466 | 34.0132 | 45.2997 | 43.1172 | 37.7268 | 50.2004 | 47.7494 | 41.6803 | 58.9308 | 56.0133 | 48.7663
b) 1:3:6 Concrete | 3.9462 | 3.7887 | 3.4075 | 5.0399 | 4.8135 | 4.26 | 6.1004 | 5.812 | 5.102 | 6.795 | 6.4676 | 5.659 | 7.5301 | 7.1624 | 6.252 | 8.8396 | 8.402 | 7.3149
c) Reinforcement | 3156.9887 | 3030.9471 | 2726.0231 | 4031.8937 | 3850.8318 | 3408.0353 | 4880.2843 | 4649.5941 | 4081.5877 | 5435.9614 | 5174.0684 | 4527.2183 | 6024.0489 | 5729.9272 | 5001.6377 | 7071.7 | 6721.6013 | 5851.9553
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 47.3548 | 45.4642 | 40.8903 | 60.4784 | 57.7625 | 51.1205 | 73.2043 | 69.7439 | 61.2238 | 81.5394 | 77.611 | 67.9083 | 90.3607 | 85.9489 | 75.0246 | 106.0755 | 100.824 | 87.7793
b) 1:3:6 Concrete | 7.1032 | 6.8196 | 6.1336 | 9.0718 | 8.6644 | 7.6681 | 10.9806 | 10.4616 | 9.1836 | 12.2309 | 11.6417 | 10.1862 | 13.5541 | 12.8923 | 11.2537 | 15.9113 | 15.1236 | 13.1669
c) Reinforcement | 5682.5796 | 5455.7048 | 4906.8416 | 7257.4087 | 6931.4973 | 6134.4635 | 8784.5117 | 8369.2694 | 7346.8579 | 9784.7305 | 9313.3232 | 8148.993 | 10843.288 | 10313.869 | 9002.9478 | 12729.06 | 12098.8824 | 10533.5195
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 68.4014 | 65.6705 | 59.0638 | 87.3577 | 83.4347 | 73.8408 | 105.7395 | 100.7412 | 88.4344 | 117.7792 | 112.1048 | 98.0897 | 130.5211 | 124.1484 | 108.3688 | 153.2202 | 145.6347 | 126.7924
b) 1:3:6 Concrete | 10.2602 | 9.8506 | 8.8596 | 13.1037 | 12.5152 | 11.0761 | 15.8609 | 15.1112 | 13.2652 | 17.6669 | 16.8157 | 14.7135 | 19.5782 | 18.6223 | 16.2553 | 22.983 | 21.8452 | 19.0189
c) Reinforcement | 8208.1706 | 7880.4624 | 7087.6601 | 10482.9237 | 10012.1627 | 8860.8918 | 12688.7391 | 12088.9448 | 10612.1281 | 14133.4997 | 13452.5779 | 11770.7676 | 15662.5271 | 14897.8107 | 13004.2579 | 18386.42 | 17476.1634 | 15215.0837
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 41.8241 | 40.2795 | 36.5666 | 52.5498 | 50.3146 | 44.8659 | 62.9765 | 60.1278 | 53.1242 | 69.7979 | 66.5681 | 58.5963 | 77.0033 | 73.3834 | 64.4201 | 89.7956 | 85.5055 | 74.8399
b) 1:3:6 Concrete | 6.2736 | 6.0419 | 5.485 | 7.8825 | 7.5472 | 6.7299 | 9.4465 | 9.0192 | 7.9686 | 10.4697 | 9.9852 | 8.7895 | 11.5505 | 11.0075 | 9.663 | 13.4693 | 12.8258 | 11.226
c) Reinforcement | 5018.8902 | 4833.5456 | 4387.9867 | 6305.9808 | 6037.7491 | 5383.904 | 7557.1811 | 7215.3418 | 6374.9027 | 8375.7457 | 7988.178 | 7031.5618 | 9240.3977 | 8806.0101 | 7730.4103 | 10775.4766 | 10260.662 | 8980.7887
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 75.2834 | 72.5032 | 65.8198 | 94.5897 | 90.5662 | 80.7586 | 113.3577 | 108.2301 | 95.6235 | 125.6362 | 119.8227 | 105.4734 | 138.606 | 132.0902 | 115.9562 | 161.6321 | 153.9099 | 134.7118
b) 1:3:6 Concrete | 11.2925 | 10.8755 | 9.873 | 14.1885 | 13.5849 | 12.1138 | 17.0037 | 16.2345 | 14.3435 | 18.8454 | 17.9734 | 15.821 | 20.7909 | 19.8135 | 17.3934 | 24.2448 | 23.0865 | 20.2068
c) Reinforcement | 9034.0023 | 8700.3821 | 7898.376 | 11350.7654 | 10867.9484 | 9691.0273 | 13602.9259 | 12987.6152 | 11474.8249 | 15076.3422 | 14378.7204 | 12656.8112 | 16632.7159 | 15850.8181 | 13914.7386 | 19395.8579 | 18469.1917 | 16165.4196
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 108.7426 | 104.7268 | 95.073 | 136.6296 | 130.8179 | 116.6513 | 163.7389 | 156.3324 | 138.1229 | 181.4745 | 173.0772 | 152.3505 | 200.2086 | 190.7969 | 167.4922 | 233.4687 | 222.3143 | 194.5838
b) 1:3:6 Concrete | 16.3114 | 15.709 | 14.261 | 20.4944 | 19.6227 | 17.4977 | 24.5608 | 23.4499 | 20.7184 | 27.2212 | 25.9616 | 22.8526 | 30.0313 | 28.6195 | 25.1238 | 35.0203 | 33.3472 | 29.1876
c) Reinforcement | 13049.1145 | 12567.2185 | 11408.7653 | 16395.55 | 15698.1477 | 13998.1505 | 19648.6708 | 18759.8886 | 16574.747 | 21776.9388 | 20769.2628 | 18282.0606 | 24025.0341 | 22895.6262 | 20099.0669 | 28016.2393 | 26677.7213 | 23350.0506
QUAD ACSR BERSIMIS
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 12.7748 | 12.0798 | 10.3723 | 17.5493 | 16.5746 | 14.1763 | 22.1425 | 20.9016 | 17.8453 | 25.1623 | 23.7474 | 20.261 | 28.378 | 26.7784 | 22.8356 | 34.1693 | 32.2382 | 27.4763
b) 1:3:6 Concrete | 1.9162 | 1.812 | 1.5558 | 2.6324 | 2.4862 | 2.1265 | 3.3214 | 3.1352 | 2.6768 | 3.7744 | 3.5621 | 3.0392 | 4.2567 | 4.0168 | 3.4253 | 5.1254 | 4.8357 | 4.1214
c) Reinforcement | 1532.9737 | 1449.5712 | 1244.6764 | 2105.9204 | 1988.9506 | 1701.1606 | 2657.1056 | 2508.1913 | 2141.4415 | 3019.4811 | 2849.6883 | 2431.3258 | 3405.363 | 3213.4118 | 2740.2775 | 4100.3103 | 3868.5866 | 3297.1596
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 22.9946 | 21.7436 | 18.6701 | 31.5888 | 29.8343 | 25.5174 | 39.8566 | 37.6229 | 32.1216 | 45.2922 | 42.7453 | 36.4699 | 51.0804 | 48.2012 | 41.1042 | 61.5047 | 58.0288 | 49.4574
b) 1:3:6 Concrete | 3.4492 | 3.2615 | 2.8005 | 4.7383 | 4.4751 | 3.8276 | 5.9785 | 5.6434 | 4.8182 | 6.7938 | 6.4118 | 5.4705 | 7.6621 | 7.2302 | 6.1656 | 9.2257 | 8.7043 | 7.4186
c) Reinforcement | 2759.3527 | 2609.2282 | 2240.4175 | 3790.6567 | 3580.1111 | 3062.0891 | 4782.7901 | 4514.7444 | 3854.5948 | 5435.066 | 5129.4389 | 4376.3864 | 6129.6534 | 5784.1413 | 4932.4995 | 7380.5585 | 6963.4558 | 5934.8873
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 33.2144 | 31.4074 | 26.968 | 45.6283 | 43.0939 | 36.8585 | 57.5706 | 54.3441 | 46.3979 | 65.4221 | 61.7432 | 52.6787 | 73.7829 | 69.6239 | 59.3727 | 88.8401 | 83.8194 | 71.4385
b) 1:3:6 Concrete | 4.9822 | 4.7111 | 4.0452 | 6.8442 | 6.4641 | 5.5288 | 8.6356 | 8.1516 | 6.9597 | 9.8133 | 9.2615 | 7.9018 | 11.0674 | 10.4436 | 8.9059 | 13.326 | 12.5729 | 10.7158
c) Reinforcement | 3985.7317 | 3768.8851 | 3236.1586 | 5475.393 | 5171.2716 | 4423.0176 | 6908.4746 | 6521.2975 | 5567.748 | 7850.6509 | 7409.1895 | 6321.447 | 8853.9438 | 8354.8708 | 7124.7215 | 10660.8067 | 10058.3251 | 8572.615
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 23.7685 | 22.7181 | 20.1693 | 31.0097 | 29.5126 | 25.8523 | 38.0147 | 36.1074 | 31.4212 | 42.6097 | 40.4409 | 35.1004 | 47.4836 | 45.0421 | 39.0192 | 56.2002 | 53.2794 | 46.058
b) 1:3:6 Concrete | 3.5653 | 3.4077 | 3.0254 | 4.6514 | 4.4269 | 3.8779 | 5.7022 | 5.4161 | 4.7132 | 6.3915 | 6.0661 | 5.2651 | 7.1225 | 6.7563 | 5.8529 | 8.43 | 7.9919 | 6.9087
c) Reinforcement | 2852.2172 | 2726.1737 | 2420.3184 | 3721.159 | 3541.5179 | 3102.2817 | 4561.7655 | 4332.8884 | 3770.545 | 5113.1651 | 4852.9104 | 4212.0425 | 5698.0359 | 5405.0579 | 4682.3084 | 6744.0257 | 6393.5314 | 5526.9571
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 42.7833 | 40.8926 | 36.3048 | 55.8174 | 53.1228 | 46.5342 | 68.4265 | 64.9933 | 56.5582 | 76.6975 | 72.7937 | 63.1806 | 85.4705 | 81.0759 | 70.2346 | 101.1604 | 95.903 | 82.9044
b) 1:3:6 Concrete | 6.4175 | 6.1339 | 5.4457 | 8.3726 | 7.9684 | 6.9801 | 10.264 | 9.749 | 8.4837 | 11.5046 | 10.919 | 9.4771 | 12.8206 | 12.1614 | 10.5352 | 15.1741 | 14.3854 | 12.4357
c) Reinforcement | 5133.991 | 4907.1126 | 4356.5731 | 6698.0863 | 6374.7323 | 5584.1071 | 8211.1779 | 7799.1992 | 6786.9809 | 9203.6972 | 8735.2388 | 7581.6765 | 10256.4646 | 9729.1042 | 8428.1551 | 12139.2462 | 11508.3566 | 9948.5227
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 61.798 | 59.0671 | 52.4402 | 80.6251 | 76.7329 | 67.2161 | 98.8383 | 93.8792 | 81.6951 | 110.7852 | 105.1464 | 91.2609 | 123.4574 | 117.1096 | 101.45 | 146.1206 | 138.5265 | 119.7507
b) 1:3:6 Concrete | 9.2697 | 8.8601 | 7.866 | 12.0938 | 11.5099 | 10.0824 | 14.8257 | 14.0819 | 12.2543 | 16.6178 | 15.772 | 13.6891 | 18.5186 | 17.5664 | 15.2175 | 21.9181 | 20.779 | 17.9626
c) Reinforcement | 7415.7648 | 7088.0516 | 6292.8278 | 9675.0135 | 9207.9466 | 8065.9324 | 11860.5903 | 11265.5099 | 9803.4169 | 13294.2293 | 12617.5671 | 10951.3105 | 14814.8933 | 14053.1505 | 12174.0018 | 17534.4668 | 16623.1817 | 14370.0884
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 33.0258 | 31.6852 | 28.4745 | 42.2616 | 40.3312 | 35.6557 | 51.2373 | 48.7739 | 42.7646 | 57.1236 | 54.3248 | 47.4748 | 63.3583 | 60.2128 | 52.494 | 74.475 | 70.7271 | 61.4995
b) 1:3:6 Concrete | 4.9539 | 4.7528 | 4.2712 | 6.3392 | 6.0497 | 5.3483 | 7.6856 | 7.3161 | 6.4147 | 8.5685 | 8.1487 | 7.1212 | 9.5037 | 9.0319 | 7.8741 | 11.1712 | 10.6091 | 9.2249
c) Reinforcement | 3963.0902 | 3802.2191 | 3416.9398 | 5071.3944 | 4839.7465 | 4278.6795 | 6148.4762 | 5852.8634 | 5131.7558 | 6854.8363 | 6518.972 | 5696.9817 | 7602.9915 | 7225.5328 | 6299.2823 | 8936.994 | 8487.2561 | 7379.9444
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 59.4464 | 57.0333 | 51.2541 | 76.0709 | 72.5962 | 64.1802 | 92.2271 | 87.793 | 76.9763 | 102.8225 | 97.7846 | 85.4547 | 114.0449 | 108.383 | 94.4892 | 134.0549 | 127.3088 | 110.6992
b) 1:3:6 Concrete | 8.917 | 8.555 | 7.6881 | 11.4106 | 10.8894 | 9.627 | 13.8341 | 13.1689 | 11.5465 | 15.4234 | 14.6677 | 12.8182 | 17.1067 | 16.2574 | 14.1734 | 20.1082 | 19.0963 | 16.6049
c) Reinforcement | 7133.5624 | 6843.9944 | 6150.4917 | 9128.5099 | 8711.5438 | 7701.6231 | 11067.2572 | 10535.1542 | 9237.1605 | 12338.7054 | 11734.1497 | 10254.567 | 13685.3848 | 13005.9591 | 11338.7082 | 16086.5892 | 15277.0609 | 13283.8999
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 85.867 | 82.3814 | 74.0337 | 109.8802 | 104.8612 | 92.7047 | 133.217 | 126.812 | 111.188 | 148.5215 | 141.2444 | 123.4346 | 164.7315 | 156.5532 | 136.4845 | 193.6349 | 183.8905 | 159.8988
b) 1:3:6 Concrete | 12.88 | 12.3572 | 11.1051 | 16.482 | 15.7292 | 13.9057 | 19.9825 | 19.0218 | 16.6782 | 22.2782 | 21.1867 | 18.5152 | 24.7097 | 23.483 | 20.4727 | 29.0452 | 27.5836 | 23.9848
c) Reinforcement | 10304.0346 | 9885.7697 | 8884.0435 | 13185.6255 | 12583.341 | 11124.5668 | 15986.0382 | 15217.445 | 13342.5652 | 17822.5745 | 16949.3273 | 14812.1523 | 19767.778 | 18786.3854 | 16378.1341 | 23236.1845 | 22066.8658 | 19187.8554
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 54.697 | 52.6692 | 47.8108 | 68.7274 | 65.79 | 58.6525 | 82.3768 | 78.6315 | 69.4513 | 91.3097 | 87.0625 | 76.6103 | 100.7474 | 95.9863 | 84.2314 | 117.5056 | 111.8618 | 97.8707
b) 1:3:6 Concrete | 8.2045 | 7.9004 | 7.1716 | 10.3091 | 9.8685 | 8.7979 | 12.3565 | 11.7947 | 10.4177 | 13.6965 | 13.0594 | 11.4915 | 15.1121 | 14.3979 | 12.6347 | 17.6258 | 16.7793 | 14.6806
c) Reinforcement | 6563.64 | 6320.2981 | 5737.3016 | 8247.2867 | 7894.8057 | 7038.3033 | 9885.2147 | 9435.7844 | 8334.1511 | 10957.1656 | 10447.5035 | 9193.2355 | 12089.6831 | 11518.3527 | 10107.7662 | 14100.6762 | 13423.4183 | 11744.482
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 98.4546 | 94.8045 | 86.0595 | 123.7093 | 118.4221 | 105.5746 | 148.2782 | 141.5368 | 125.0123 | 164.3575 | 156.7126 | 137.8985 | 181.3452 | 172.7753 | 151.6165 | 211.5101 | 201.3513 | 176.1672
b) 1:3:6 Concrete | 14.7682 | 14.2207 | 12.9089 | 18.5564 | 17.7633 | 15.8362 | 22.2417 | 21.2305 | 18.7518 | 24.6536 | 23.5069 | 20.6848 | 27.2018 | 25.9163 | 22.7425 | 31.7265 | 30.2027 | 26.4251
c) Reinforcement | 11814.552 | 11376.5366 | 10327.1429 | 14845.116 | 14210.6503 | 12668.946 | 17793.3865 | 16984.412 | 15001.4721 | 19722.898 | 18805.5063 | 16547.8239 | 21761.4296 | 20733.0348 | 18193.9792 | 25381.2172 | 24162.1529 | 21140.0676
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 142.2122 | 136.9398 | 124.3082 | 178.6912 | 171.0541 | 152.4966 | 214.1797 | 204.442 | 180.5733 | 237.4053 | 226.3626 | 199.1868 | 261.9431 | 249.5643 | 219.0016 | 305.5147 | 290.8407 | 254.4638
b) 1:3:6 Concrete | 21.3318 | 20.541 | 18.6462 | 26.8037 | 25.6581 | 22.8745 | 32.1269 | 30.6663 | 27.086 | 35.6108 | 33.9544 | 29.878 | 39.2915 | 37.4346 | 32.8502 | 45.8272 | 43.6261 | 38.1696
c) Reinforcement | 17065.4639 | 16432.775 | 14916.9842 | 21442.9453 | 20526.4949 | 18299.5887 | 25701.5583 | 24533.0395 | 21668.793 | 28488.6305 | 27163.5092 | 23902.4124 | 31433.176 | 29947.717 | 26280.1922 | 36661.7581 | 34900.8875 | 30535.6532
(FOR 400KV S/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR BERSIMIS
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 2.4952 | 2.3161 | 1.9734 | 3.4224 | 3.1712 | 2.6896 | 4.3145 | 3.9946 | 3.3806 | 4.9011 | 4.5362 | 3.8357 | 5.5257 | 5.1132 | 4.3209 | 6.6507 | 6.1526 | 5.1955
b) 1:3:6 Concrete | 0.37428 | 0.34742 | 0.29601 | 0.51337 | 0.47567 | 0.40344 | 0.64718 | 0.59918 | 0.50709 | 0.73517 | 0.68043 | 0.57536 | 0.82886 | 0.76698 | 0.64813 | 0.99761 | 0.92289 | 0.77933
c) Reinforcement | 299.4227 | 277.9328 | 236.8076 | 410.6931 | 380.54 | 322.7512 | 517.7458 | 479.3464 | 405.6746 | 588.1323 | 544.3435 | 460.2879 | 663.0884 | 613.5803 | 518.505 | 798.0874 | 738.315 | 623.4646
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 4.4913 | 4.169 | 3.5521 | 6.1604 | 5.7081 | 4.8413 | 7.7662 | 7.1902 | 6.0851 | 8.822 | 8.1652 | 6.9043 | 9.9463 | 9.2037 | 7.7776 | 11.9713 | 11.0747 | 9.352
b) 1:3:6 Concrete | 0.6737 | 0.62535 | 0.53282 | 0.92406 | 0.85621 | 0.72619 | 1.1649 | 1.0785 | 0.91277 | 1.3233 | 1.2248 | 1.0356 | 1.4919 | 1.3806 | 1.1666 | 1.7957 | 1.6612 | 1.4028
c) Reinforcement | 538.9608 | 500.279 | 426.2537 | 739.2476 | 684.972 | 580.9521 | 931.9424 | 862.8235 | 730.2143 | 1058.6382 | 979.8183 | 828.5181 | 1193.5592 | 1104.4446 | 933.3089 | 1436.5573 | 1328.9671 | 1122.2363
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 6.4875 | 6.0219 | 5.1308 | 8.8984 | 8.245 | 6.9929 | 11.2178 | 10.3858 | 8.7896 | 12.7429 | 11.7941 | 9.9729 | 14.3669 | 13.2942 | 11.2343 | 17.2919 | 15.9968 | 13.5084
b) 1:3:6 Concrete | 0.97312 | 0.90328 | 0.76962 | 1.3348 | 1.2368 | 1.0489 | 1.6827 | 1.5579 | 1.3184 | 1.9114 | 1.7691 | 1.4959 | 2.155 | 1.9941 | 1.6851 | 2.5938 | 2.3995 | 2.0263
c) Reinforcement | 778.4989 | 722.6252 | 615.6998 | 1067.8021 | 989.404 | 839.153 | 1346.139 | 1246.3006 | 1054.754 | 1529.144 | 1415.2931 | 1196.7484 | 1724.0299 | 1595.3089 | 1348.1129 | 2075.0271 | 1919.6191 | 1621.0079
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 4.7054 | 4.4343 | 3.9254 | 6.105 | 5.7177 | 4.9852 | 7.4595 | 6.9654 | 6.0259 | 8.3483 | 7.7861 | 6.7144 | 9.2913 | 8.6581 | 7.4485 | 10.9781 | 10.2202 | 8.7685
b) 1:3:6 Concrete | 0.7058 | 0.66514 | 0.58881 | 0.91574 | 0.85766 | 0.74778 | 1.1189 | 1.0448 | 0.90388 | 1.2522 | 1.1679 | 1.0072 | 1.3937 | 1.2987 | 1.1173 | 1.6467 | 1.533 | 1.3153
c) Reinforcement | 564.6427 | 532.1107 | 471.0463 | 732.5941 | 686.1248 | 598.2275 | 895.1373 | 835.8465 | 723.1052 | 1001.7943 | 934.3318 | 805.7283 | 1114.9514 | 1038.9691 | 893.8214 | 1317.3756 | 1226.4259 | 1052.2206
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 8.4696 | 7.9817 | 7.0657 | 10.9889 | 10.2919 | 8.9734 | 13.4271 | 12.5377 | 10.8466 | 15.0269 | 14.015 | 12.0859 | 16.7243 | 15.5845 | 13.4073 | 19.7606 | 18.3964 | 15.7833
b) 1:3:6 Concrete | 1.2704 | 1.1972 | 1.0599 | 1.6483 | 1.5438 | 1.346 | 2.0141 | 1.8807 | 1.627 | 2.254 | 2.1022 | 1.8129 | 2.5086 | 2.3377 | 2.0111 | 2.9641 | 2.7595 | 2.3675
c) Reinforcement | 1016.3568 | 957.7993 | 847.8834 | 1318.6693 | 1235.0247 | 1076.8095 | 1611.2471 | 1504.5236 | 1301.5894 | 1803.2297 | 1681.7973 | 1450.3109 | 2006.9125 | 1870.1444 | 1608.8786 | 2371.2761 | 2207.5665 | 1893.9971
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 12.2339 | 11.5291 | 10.206 | 15.8729 | 14.866 | 12.9616 | 19.3946 | 18.11 | 15.6673 | 21.7055 | 20.2439 | 17.4574 | 24.1573 | 22.511 | 19.3661 | 28.5431 | 26.5726 | 22.7981
b) 1:3:6 Concrete | 1.8351 | 1.7294 | 1.5309 | 2.3809 | 2.2299 | 1.9442 | 2.9092 | 2.7165 | 2.3501 | 3.2558 | 3.0366 | 2.6186 | 3.6236 | 3.3766 | 2.9049 | 4.2815 | 3.9859 | 3.4197
c) Reinforcement | 1468.071 | 1383.4878 | 1224.7205 | 1904.7446 | 1783.9245 | 1555.3915 | 2327.3569 | 2173.2008 | 1880.0735 | 2604.6651 | 2429.2628 | 2094.8936 | 2898.8737 | 2701.3196 | 2323.9357 | 3425.1766 | 3188.7072 | 2735.7737
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 6.8428 | 6.4864 | 5.8246 | 8.6795 | 8.1657 | 7.2004 | 10.4628 | 9.8065 | 8.5644 | 11.6317 | 10.8858 | 9.4691 | 12.8693 | 12.0309 | 10.4338 | 15.0751 | 14.0761 | 12.166
b) 1:3:6 Concrete | 1.0264 | 0.97296 | 0.87369 | 1.3019 | 1.2248 | 1.0801 | 1.5694 | 1.471 | 1.2847 | 1.7448 | 1.6329 | 1.4204 | 1.9304 | 1.8046 | 1.5651 | 2.2613 | 2.1114 | 1.8249
c) Reinforcement | 821.1324 | 778.3715 | 698.952 | 1041.5427 | 979.8791 | 864.0503 | 1255.5368 | 1176.7805 | 1027.7292 | 1395.8032 | 1306.2968 | 1136.2944 | 1544.3177 | 1443.7104 | 1252.0597 | 1809.0135 | 1689.1372 | 1459.9153
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 12.317 | 11.6756 | 10.4843 | 15.6231 | 14.6982 | 12.9608 | 18.8331 | 17.6517 | 15.4159 | 20.937 | 19.5945 | 17.0444 | 23.1648 | 21.6557 | 18.7809 | 27.1352 | 25.3371 | 21.8987
b) 1:3:6 Concrete | 1.8475 | 1.7513 | 1.5726 | 2.3435 | 2.2047 | 1.9441 | 2.825 | 2.6478 | 2.3124 | 3.1406 | 2.9392 | 2.5567 | 3.4747 | 3.2483 | 2.8171 | 4.0703 | 3.8006 | 3.2848
c) Reinforcement | 1478.0383 | 1401.0687 | 1258.1135 | 1874.7769 | 1763.7824 | 1555.2906 | 2259.9663 | 2118.2049 | 1849.9126 | 2512.4458 | 2351.3342 | 2045.3298 | 2779.7719 | 2598.6788 | 2253.7074 | 3256.2243 | 3040.447 | 2627.8475
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 17.7912 | 16.8647 | 15.144 | 22.5668 | 21.2307 | 18.7211 | 27.2033 | 25.4969 | 22.2675 | 30.2424 | 28.3031 | 24.6197 | 33.4602 | 31.2804 | 27.128 | 39.1953 | 36.598 | 31.6315
b) 1:3:6 Concrete | 2.6687 | 2.5297 | 2.2716 | 3.385 | 3.1846 | 2.8082 | 4.0805 | 3.8245 | 3.3401 | 4.5364 | 4.2455 | 3.693 | 5.019 | 4.6921 | 4.0692 | 5.8793 | 5.4897 | 4.7447
c) Reinforcement | 2134.9442 | 2023.7659 | 1817.2751 | 2708.011 | 2547.6856 | 2246.5309 | 3264.3958 | 3059.6294 | 2672.0959 | 3629.0883 | 3396.3716 | 2954.3653 | 4015.2261 | 3753.6471 | 3255.3551 | 4703.435 | 4391.7568 | 3795.7797
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 10.929 | 10.4047 | 9.4401 | 13.6276 | 12.8652 | 11.4418 | 16.2552 | 15.2805 | 13.4436 | 17.9758 | 16.8693 | 14.7743 | 19.7943 | 18.5527 | 16.1935 | 23.0248 | 21.5514 | 18.7382
b) 1:3:6 Concrete | 1.6393 | 1.5607 | 1.416 | 2.0441 | 1.9298 | 1.7163 | 2.4383 | 2.2921 | 2.0165 | 2.6964 | 2.5304 | 2.2162 | 2.9691 | 2.7829 | 2.429 | 3.4537 | 3.2327 | 2.8107
c) Reinforcement | 1311.4748 | 1248.5595 | 1132.8129 | 1635.314 | 1543.8232 | 1373.0159 | 1950.619 | 1833.6656 | 1613.2348 | 2157.0936 | 2024.3112 | 1772.9218 | 2375.3167 | 2226.3294 | 1943.216 | 2762.971 | 2586.1622 | 2248.5843
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 19.6721 | 18.7284 | 16.9922 | 24.5297 | 23.1573 | 20.5952 | 29.2593 | 27.505 | 24.1985 | 32.3564 | 30.3647 | 26.5938 | 35.6297 | 33.3949 | 29.1482 | 41.4446 | 38.7924 | 33.7288
b) 1:3:6 Concrete | 2.9508 | 2.8093 | 2.5488 | 3.6795 | 3.4736 | 3.0893 | 4.3889 | 4.1257 | 3.6298 | 4.8535 | 4.5547 | 3.9891 | 5.3445 | 5.0092 | 4.3722 | 6.2167 | 5.8189 | 5.0593
c) Reinforcement | 2360.6546 | 2247.407 | 2039.0632 | 2943.5652 | 2778.8818 | 2471.4286 | 3511.1142 | 3300.5981 | 2903.8226 | 3882.7684 | 3643.7602 | 3191.2593 | 4275.57 | 4007.3929 | 3497.7888 | 4973.3478 | 4655.092 | 4047.4517
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 28.4153 | 27.0521 | 24.5443 | 35.4318 | 33.4495 | 29.7487 | 42.2634 | 39.7294 | 34.9534 | 46.737 | 43.8601 | 38.4133 | 51.4652 | 48.2371 | 42.103 | 59.8644 | 56.0335 | 48.7193
b) 1:3:6 Concrete | 4.2623 | 4.0578 | 3.6816 | 5.3148 | 5.0174 | 4.4623 | 6.3395 | 5.9594 | 5.243 | 7.0106 | 6.579 | 5.762 | 7.7198 | 7.2356 | 6.3155 | 8.9797 | 8.405 | 7.3079
c) Reinforcement | 3409.8344 | 3246.2546 | 2945.3135 | 4251.8164 | 4013.9404 | 3569.8413 | 5071.6095 | 4767.5306 | 4194.4104 | 5608.4433 | 5263.2092 | 4609.5967 | 6175.8233 | 5788.4564 | 5052.3616 | 7183.7247 | 6724.0218 | 5846.3191
TRIPPLE ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 3.497 | 3.2401 | 2.7564 | 4.7963 | 4.4358 | 3.7558 | 6.0468 | 5.5876 | 4.7205 | 6.8691 | 6.3454 | 5.356 | 7.7449 | 7.1527 | 6.0335 | 9.3222 | 8.6073 | 7.2551
b) 1:3:6 Concrete | 0.52454 | 0.48602 | 0.41346 | 0.71945 | 0.66537 | 0.56338 | 0.90702 | 0.83814 | 0.70808 | 1.0304 | 0.95181 | 0.8034 | 1.1617 | 1.0729 | 0.90503 | 1.3983 | 1.2911 | 1.0883
c) Reinforcement | 419.6347 | 388.8121 | 330.769 | 575.5589 | 532.2972 | 450.7017 | 725.6175 | 670.5137 | 566.465 | 824.2942 | 761.4507 | 642.7226 | 929.3847 | 858.328 | 724.0221 | 1118.669 | 1032.8726 | 870.6138
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 6.2945 | 5.8322 | 4.9615 | 8.6334 | 7.9845 | 6.7605 | 10.8843 | 10.0577 | 8.497 | 12.3644 | 11.4218 | 9.6408 | 13.9408 | 12.8749 | 10.8603 | 16.78 | 15.4931 | 13.0592
b) 1:3:6 Concrete | 0.94418 | 0.87483 | 0.74423 | 1.295 | 1.1977 | 1.0141 | 1.6326 | 1.5087 | 1.2745 | 1.8547 | 1.7133 | 1.4461 | 2.0911 | 1.9312 | 1.629 | 2.517 | 2.324 | 1.9589
c) Reinforcement | 755.3424 | 699.8618 | 595.3841 | 1036.0061 | 958.135 | 811.263 | 1306.1115 | 1206.9246 | 1019.637 | 1483.7296 | 1370.6112 | 1156.9007 | 1672.8925 | 1544.9903 | 1303.2397 | 2013.6042 | 1859.1707 | 1567.1048
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 9.0921 | 8.4243 | 7.1667 | 12.4704 | 11.5331 | 9.7652 | 15.7217 | 14.5278 | 12.2734 | 17.8597 | 16.4981 | 13.9257 | 20.1367 | 18.5971 | 15.6871 | 24.2378 | 22.3789 | 18.8633
b) 1:3:6 Concrete | 1.3638 | 1.2636 | 1.075 | 1.8706 | 1.73 | 1.4648 | 2.3583 | 2.1792 | 1.841 | 2.679 | 2.4747 | 2.0888 | 3.0205 | 2.7896 | 2.3531 | 3.6357 | 3.3568 | 2.8295
c) Reinforcement | 1091.0502 | 1010.9115 | 859.9993 | 1496.4532 | 1383.9728 | 1171.8244 | 1886.6055 | 1743.3355 | 1472.809 | 2143.1649 | 1979.7718 | 1671.0788 | 2416.4003 | 2231.6527 | 1882.4574 | 2908.5394 | 2685.4687 | 2263.5959
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 6.6085 | 6.2209 | 5.5039 | 8.5744 | 8.0198 | 6.9856 | 10.4797 | 9.7715 | 8.4432 | 11.7308 | 10.9246 | 9.4086 | 13.0587 | 12.1504 | 10.4385 | 15.4349 | 14.3472 | 12.2915
b) 1:3:6 Concrete | 0.99127 | 0.93313 | 0.82558 | 1.2862 | 1.203 | 1.0478 | 1.572 | 1.4657 | 1.2665 | 1.7596 | 1.6387 | 1.4113 | 1.9588 | 1.8226 | 1.5658 | 2.3152 | 2.1521 | 1.8437
c) Reinforcement | 793.0164 | 746.5073 | 660.4627 | 1028.9222 | 962.3811 | 838.2701 | 1257.5615 | 1172.5788 | 1013.1862 | 1407.6948 | 1310.9572 | 1129.0343 | 1567.0382 | 1458.0449 | 1252.6243 | 1852.1845 | 1721.6628 | 1474.9796
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 11.8952 | 11.1976 | 9.9069 | 15.4338 | 14.4357 | 12.5741 | 18.8634 | 17.5887 | 15.1978 | 21.1154 | 19.6644 | 16.9355 | 23.5056 | 21.8707 | 18.7894 | 27.7828 | 25.8249 | 22.1247
b) 1:3:6 Concrete | 1.7843 | 1.6796 | 1.486 | 2.3151 | 2.1654 | 1.8861 | 2.8295 | 2.6383 | 2.2797 | 3.1673 | 2.9497 | 2.5403 | 3.5258 | 3.2806 | 2.8184 | 4.1674 | 3.8737 | 3.3187
c) Reinforcement | 1427.4294 | 1343.7132 | 1188.8328 | 1852.0599 | 1732.286 | 1508.8861 | 2263.6107 | 2110.6418 | 1823.7352 | 2533.8507 | 2359.723 | 2032.2617 | 2820.6687 | 2624.4808 | 2254.7237 | 3333.9321 | 3098.993 | 2654.9633
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 17.182 | 16.1743 | 14.31 | 22.2933 | 20.8516 | 18.1625 | 27.2472 | 25.4059 | 21.9524 | 30.5001 | 28.4041 | 24.4624 | 33.9525 | 31.591 | 27.1402 | 40.1307 | 37.3027 | 31.9579
b) 1:3:6 Concrete | 2.5773 | 2.4261 | 2.1465 | 3.344 | 3.1277 | 2.7244 | 4.0871 | 3.8109 | 3.2929 | 4.575 | 4.2606 | 3.6694 | 5.0929 | 4.7386 | 4.071 | 6.0196 | 5.5954 | 4.7937
c) Reinforcement | 2061.8425 | 1940.9191 | 1717.203 | 2675.1976 | 2502.1908 | 2179.5022 | 3269.6599 | 3048.7049 | 2634.2842 | 3660.0066 | 3408.4888 | 2935.4892 | 4074.2992 | 3790.9167 | 3256.8232 | 4815.6797 | 4476.3232 | 3834.9469
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 9.6183 | 9.1098 | 8.1781 | 12.2015 | 11.4665 | 10.1035 | 14.7147 | 13.7746 | 12.0176 | 16.3636 | 15.2945 | 13.2889 | 18.1105 | 16.9082 | 14.6457 | 21.2256 | 19.7922 | 17.0839
b) 1:3:6 Concrete | 1.4428 | 1.3665 | 1.2267 | 1.8302 | 1.72 | 1.5155 | 2.2072 | 2.0662 | 1.8026 | 2.4545 | 2.2942 | 1.9933 | 2.7166 | 2.5362 | 2.1969 | 3.1838 | 2.9688 | 2.5626
c) Reinforcement | 1154.2019 | 1093.1763 | 981.3691 | 1464.1859 | 1375.9779 | 1212.4253 | 1765.7621 | 1652.9492 | 1442.106 | 1963.6358 | 1835.3447 | 1594.6685 | 2173.2612 | 2028.9869 | 1757.4847 | 2547.0744 | 2375.0589 | 2050.0668
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 17.313 | 16.3976 | 14.7205 | 21.9628 | 20.6397 | 18.1864 | 26.4864 | 24.7942 | 21.6316 | 29.4545 | 27.5302 | 23.92 | 32.5989 | 30.4348 | 26.3623 | 38.2061 | 35.6259 | 30.751
b) 1:3:6 Concrete | 2.597 | 2.4596 | 2.2081 | 3.2944 | 3.096 | 2.728 | 3.973 | 3.7191 | 3.2447 | 4.4182 | 4.1295 | 3.588 | 4.8898 | 4.5652 | 3.9543 | 5.7309 | 5.3439 | 4.6127
c) Reinforcement | 2077.5635 | 1967.7174 | 1766.4644 | 2635.5346 | 2476.7603 | 2182.3656 | 3178.3719 | 2975.3086 | 2595.7909 | 3534.5444 | 3303.6205 | 2870.4032 | 3911.8701 | 3652.1764 | 3163.4724 | 4584.7338 | 4275.1061 | 3690.1202
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 25.0077 | 23.6855 | 21.263 | 31.724 | 29.8129 | 26.2692 | 38.2582 | 35.8139 | 31.2456 | 42.5454 | 39.7658 | 34.5512 | 47.0873 | 43.9614 | 38.0788 | 55.1866 | 51.4596 | 44.4181
b) 1:3:6 Concrete | 3.7512 | 3.5528 | 3.1894 | 4.7586 | 4.4719 | 3.9404 | 5.7387 | 5.3721 | 4.6868 | 6.3818 | 5.9649 | 5.1827 | 7.0631 | 6.5942 | 5.7118 | 8.278 | 7.7189 | 6.6627
c) Reinforcement | 3000.925 | 2842.2584 | 2551.5597 | 3806.8833 | 3577.5426 | 3152.3058 | 4590.9816 | 4297.6679 | 3749.4757 | 5105.4531 | 4771.8963 | 4146.138 | 5650.4791 | 5275.3659 | 4569.4601 | 6622.3933 | 6175.1532 | 5330.1736
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 15.3714 | 14.6243 | 13.2676 | 19.1711 | 18.0815 | 16.0716 | 22.8802 | 21.4849 | 18.8852 | 25.3121 | 23.7268 | 20.7589 | 27.8843 | 26.1044 | 22.7592 | 32.4569 | 30.3428 | 26.35
b) 1:3:6 Concrete | 2.3057 | 2.1937 | 1.9901 | 2.8757 | 2.7122 | 2.4107 | 3.432 | 3.2227 | 2.8328 | 3.7968 | 3.559 | 3.1138 | 4.1827 | 3.9157 | 3.4139 | 4.8685 | 4.5514 | 3.9525
c) Reinforcement | 1844.5699 | 1754.9211 | 1592.1067 | 2300.532 | 2169.7745 | 1928.5877 | 2745.6201 | 2578.1831 | 2266.2183 | 3037.457 | 2847.211 | 2491.0658 | 3346.1212 | 3132.5234 | 2731.1015 | 3894.8275 | 3641.1415 | 3161.9953
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 27.6685 | 26.3238 | 23.8816 | 34.508 | 32.5466 | 28.9288 | 41.1843 | 38.6727 | 33.9933 | 45.5619 | 42.7082 | 37.366 | 50.1918 | 46.9879 | 40.9665 | 58.4224 | 54.6171 | 47.4299
b) 1:3:6 Concrete | 4.1503 | 3.9486 | 3.5822 | 5.1762 | 4.882 | 4.3393 | 6.1776 | 5.8009 | 5.099 | 6.8343 | 6.4062 | 5.6049 | 7.5288 | 7.0482 | 6.145 | 8.7634 | 8.1926 | 7.1145
c) Reinforcement | 3320.2257 | 3158.8581 | 2865.7921 | 4140.9575 | 3905.5941 | 3471.4579 | 4942.1161 | 4640.7296 | 4079.1929 | 5467.4226 | 5124.9797 | 4483.9184 | 6023.0181 | 5638.5422 | 4915.9826 | 7010.6895 | 6554.0547 | 5691.5915
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 39.9657 | 38.0233 | 34.4956 | 49.8449 | 47.0118 | 41.7861 | 59.4884 | 55.8606 | 49.1014 | 65.8116 | 61.6896 | 53.9731 | 72.4993 | 67.8713 | 59.1739 | 84.3879 | 78.8914 | 68.5099
b) 1:3:6 Concrete | 5.9949 | 5.7035 | 5.1743 | 7.4767 | 7.0518 | 6.2679 | 8.9233 | 8.3791 | 7.3652 | 9.8717 | 9.2534 | 8.096 | 10.8749 | 10.1807 | 8.8761 | 12.6582 | 11.8337 | 10.2765
c) Reinforcement | 4795.8816 | 4562.795 | 4139.4775 | 5981.3831 | 5641.4138 | 5014.3281 | 7138.6122 | 6703.2761 | 5892.1675 | 7897.3881 | 7402.7485 | 6476.771 | 8699.9151 | 8144.5609 | 7100.8638 | 10126.5514 | 9466.9679 | 8221.1877
QUAD ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 4.4987 | 4.1641 | 3.5394 | 6.1702 | 5.7005 | 4.8221 | 7.7791 | 7.1807 | 6.0605 | 8.8371 | 8.1546 | 6.8763 | 9.964 | 9.1923 | 7.7462 | 11.9938 | 11.0619 | 9.3147
b) 1:3:6 Concrete | 0.67481 | 0.62461 | 0.53091 | 0.92553 | 0.85507 | 0.72332 | 1.1669 | 1.0771 | 0.90907 | 1.3256 | 1.2232 | 1.0314 | 1.4946 | 1.3788 | 1.1619 | 1.7991 | 1.6593 | 1.3972
c) Reinforcement | 539.8467 | 499.6915 | 424.7303 | 740.4247 | 684.0545 | 578.6522 | 933.4892 | 861.681 | 727.2554 | 1060.4561 | 978.5579 | 825.1574 | 1195.681 | 1103.0756 | 929.5392 | 1439.2507 | 1327.4301 | 1117.763
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 8.0977 | 7.4954 | 6.371 | 11.1064 | 10.2608 | 8.6798 | 14.0023 | 12.9252 | 10.9088 | 15.9068 | 14.6784 | 12.3774 | 17.9352 | 16.5461 | 13.9431 | 21.5888 | 19.9115 | 16.7664
b) 1:3:6 Concrete | 1.2147 | 1.1243 | 0.95564 | 1.666 | 1.5391 | 1.302 | 2.1004 | 1.9388 | 1.6363 | 2.386 | 2.2018 | 1.8566 | 2.6903 | 2.4819 | 2.0915 | 3.2383 | 2.9867 | 2.515
c) Reinforcement | 971.724 | 899.4447 | 764.5145 | 1332.7645 | 1231.2981 | 1041.574 | 1680.2806 | 1551.0257 | 1309.0597 | 1908.8209 | 1761.4042 | 1485.2833 | 2152.2258 | 1985.5361 | 1673.1706 | 2590.6512 | 2389.3742 | 2011.9734
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 11.6967 | 10.8266 | 9.2025 | 16.0425 | 14.8212 | 12.5375 | 20.2256 | 18.6698 | 15.7572 | 22.9765 | 21.2021 | 17.8784 | 25.9064 | 23.9 | 20.14 | 31.1838 | 28.761 | 24.2182
b) 1:3:6 Concrete | 1.7545 | 1.624 | 1.3804 | 2.4064 | 2.2232 | 1.8806 | 3.0338 | 2.8005 | 2.3636 | 3.4465 | 3.1803 | 2.6818 | 3.886 | 3.585 | 3.021 | 4.6776 | 4.3141 | 3.6327
c) Reinforcement | 1403.6014 | 1299.1978 | 1104.2987 | 1925.1043 | 1778.5416 | 1504.4958 | 2427.072 | 2240.3705 | 1890.864 | 2757.1858 | 2544.2505 | 2145.4092 | 3108.7706 | 2867.9966 | 2416.8019 | 3742.0517 | 3451.3183 | 2906.1838
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 8.5116 | 8.0075 | 7.0823 | 11.0438 | 10.322 | 8.9859 | 13.4999 | 12.5776 | 10.8606 | 15.1133 | 14.0632 | 12.1028 | 16.826 | 15.6427 | 13.4286 | 19.8916 | 18.4742 | 15.8145
b) 1:3:6 Concrete | 1.2767 | 1.2011 | 1.0623 | 1.6566 | 1.5483 | 1.3479 | 2.025 | 1.8866 | 1.6291 | 2.267 | 2.1095 | 1.8154 | 2.5239 | 2.3464 | 2.0143 | 2.9837 | 2.7711 | 2.3722
c) Reinforcement | 1021.39 | 960.904 | 849.879 | 1325.2503 | 1238.6374 | 1078.3127 | 1619.9857 | 1509.3111 | 1303.2672 | 1813.5954 | 1687.5827 | 1452.3403 | 2019.1249 | 1877.1206 | 1611.4272 | 2386.9934 | 2216.8997 | 1897.7385
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 15.3209 | 14.4136 | 12.7482 | 19.8788 | 18.5796 | 16.1747 | 24.2998 | 22.6397 | 19.549 | 27.2039 | 25.3137 | 21.7851 | 30.2869 | 28.1568 | 24.1714 | 35.8049 | 33.2535 | 28.4661
b) 1:3:6 Concrete | 2.2981 | 2.162 | 1.9122 | 2.9818 | 2.7869 | 2.4262 | 3.645 | 3.396 | 2.9324 | 4.0806 | 3.7971 | 3.2678 | 4.543 | 4.2235 | 3.6257 | 5.3707 | 4.988 | 4.2699
c) Reinforcement | 1838.5021 | 1729.6272 | 1529.7823 | 2385.4505 | 2229.5473 | 1940.9628 | 2915.9743 | 2716.7601 | 2345.881 | 3264.4718 | 3037.6488 | 2614.2125 | 3634.4249 | 3378.8171 | 2900.5689 | 4296.5881 | 3990.4194 | 3415.9294
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 22.1301 | 20.8196 | 18.414 | 28.7138 | 26.8371 | 23.3634 | 35.0997 | 32.7017 | 28.2375 | 39.2946 | 36.5643 | 31.4674 | 43.7477 | 40.6709 | 34.9143 | 51.7182 | 48.0328 | 41.1177
b) 1:3:6 Concrete | 3.3195 | 3.1229 | 2.7621 | 4.3071 | 4.0256 | 3.5045 | 5.265 | 4.9053 | 4.2356 | 5.8942 | 5.4846 | 4.7201 | 6.5622 | 6.1006 | 5.2371 | 7.7577 | 7.2049 | 6.1677
c) Reinforcement | 2655.6141 | 2498.3504 | 2209.6855 | 3445.6507 | 3220.4572 | 2803.613 | 4211.9628 | 3924.209 | 3388.4948 | 4715.3481 | 4387.7149 | 3776.0847 | 5249.7248 | 4880.5137 | 4189.7106 | 6206.1828 | 5763.9392 | 4934.1202
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 12.3939 | 11.7332 | 10.5316 | 15.7236 | 14.7673 | 13.0067 | 18.9666 | 17.7426 | 15.4707 | 21.0956 | 19.7033 | 17.1087 | 23.3517 | 21.7855 | 18.8576 | 27.3761 | 25.5082 | 22.0018
b) 1:3:6 Concrete | 1.8591 | 1.76 | 1.5797 | 2.3585 | 2.2151 | 1.951 | 2.845 | 2.6614 | 2.3206 | 3.1643 | 2.9555 | 2.5663 | 3.5028 | 3.2678 | 2.8286 | 4.1064 | 3.8262 | 3.3003
c) Reinforcement | 1487.2715 | 1407.9811 | 1263.7863 | 1886.829 | 1772.0768 | 1560.8003 | 2275.9874 | 2129.1179 | 1856.4829 | 2531.4684 | 2364.3926 | 2053.0426 | 2802.2047 | 2614.2633 | 2262.9097 | 3285.1352 | 3060.9806 | 2640.2182
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 22.3091 | 21.1197 | 18.9568 | 28.3024 | 26.5812 | 23.412 | 34.1398 | 31.9368 | 27.8472 | 37.972 | 35.4659 | 30.7956 | 42.0331 | 39.2139 | 33.9436 | 49.277 | 45.9147 | 39.6033
b) 1:3:6 Concrete | 3.3464 | 3.168 | 2.8435 | 4.2454 | 3.9872 | 3.5118 | 5.121 | 4.7905 | 4.1771 | 5.6958 | 5.3199 | 4.6193 | 6.305 | 5.8821 | 5.0915 | 7.3916 | 6.8872 | 5.9405
c) Reinforcement | 2677.0886 | 2534.366 | 2274.8153 | 3396.2923 | 3189.7382 | 2809.4405 | 4096.7774 | 3832.4122 | 3341.6692 | 4556.6431 | 4255.9068 | 3695.4767 | 5043.9684 | 4705.674 | 4073.2374 | 5913.2434 | 5509.7651 | 4752.3928
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 32.2242 | 30.5063 | 27.382 | 40.8813 | 38.395 | 33.8173 | 49.3131 | 46.1309 | 40.2238 | 54.8485 | 51.2285 | 44.4826 | 60.7144 | 56.6424 | 49.0297 | 71.1779 | 66.3212 | 57.2047
b) 1:3:6 Concrete | 4.8336 | 4.5759 | 4.1073 | 6.1322 | 5.7592 | 5.0726 | 7.397 | 6.9196 | 6.0336 | 8.2273 | 7.6843 | 6.6724 | 9.1072 | 8.4964 | 7.3545 | 10.6767 | 9.9482 | 8.5807
c) Reinforcement | 3866.9058 | 3660.7509 | 3285.8443 | 4905.7555 | 4607.3996 | 4058.0807 | 5917.5673 | 5535.7065 | 4826.8555 | 6581.8178 | 6147.4209 | 5337.9107 | 7285.7321 | 6797.0846 | 5883.5651 | 8541.3516 | 7958.5496 | 6864.5674
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 19.8139 | 18.844 | 17.095 | 24.7146 | 23.2977 | 20.7013 | 29.5052 | 27.6892 | 24.3267 | 32.6485 | 30.5843 | 26.7434 | 35.9744 | 33.656 | 29.3249 | 41.889 | 39.1343 | 33.9617
b) 1:3:6 Concrete | 2.9721 | 2.8266 | 2.5643 | 3.7072 | 3.4947 | 3.1052 | 4.4258 | 4.1534 | 3.649 | 4.8973 | 4.5876 | 4.0115 | 5.3962 | 5.0484 | 4.3987 | 6.2834 | 5.8702 | 5.0943
c) Reinforcement | 2377.6649 | 2261.2828 | 2051.4006 | 2965.7499 | 2795.7258 | 2484.1596 | 3540.6211 | 3322.7006 | 2919.2018 | 3917.8204 | 3670.1107 | 3209.2097 | 4316.9257 | 4038.7175 | 3518.9869 | 5026.6839 | 4696.1207 | 4075.4063
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 35.665 | 33.9192 | 30.771 | 44.4862 | 41.9359 | 37.2624 | 53.1093 | 49.8405 | 43.788 | 58.7673 | 55.0517 | 48.1381 | 64.7539 | 60.5808 | 52.7848 | 75.4003 | 70.4418 | 61.1311
b) 1:3:6 Concrete | 5.3497 | 5.0879 | 4.6157 | 6.6729 | 6.2904 | 5.5894 | 7.9664 | 7.4761 | 6.5682 | 8.8151 | 8.2577 | 7.2207 | 9.7131 | 9.0871 | 7.9177 | 11.31 | 10.5663 | 9.1697
c) Reinforcement | 4279.7969 | 4070.3091 | 3692.521 | 5338.3499 | 5032.3064 | 4471.4873 | 6373.118 | 5980.8612 | 5254.5632 | 7052.0767 | 6606.1993 | 5776.5775 | 7770.4663 | 7269.6915 | 6334.1765 | 9048.0311 | 8453.0173 | 7335.7313
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 51.5161 | 48.9945 | 44.447 | 64.2579 | 60.5741 | 53.8235 | 76.7135 | 71.9918 | 63.2494 | 84.8861 | 79.5191 | 69.5329 | 93.5334 | 87.5055 | 76.2447 | 108.9115 | 101.7493 | 88.3005
b) 1:3:6 Concrete | 7.7274 | 7.3492 | 6.6671 | 9.6387 | 9.0861 | 8.0735 | 11.507 | 10.7988 | 9.4874 | 12.7329 | 11.9279 | 10.4299 | 14.03 | 13.1258 | 11.4367 | 16.3367 | 15.2624 | 13.2451
c) Reinforcement | 6181.9288 | 5879.3353 | 5333.6415 | 7710.9498 | 7268.8871 | 6458.815 | 9205.6149 | 8639.0217 | 7589.9246 | 10186.333 | 9542.2878 | 8343.9453 | 11224.0068 | 10500.6654 | 9149.366 | 13069.3782 | 12209.9139 | 10596.0564
(FOR 765KV S/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR BERSIMIS
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 5.1223 | 4.7755 | 4.1145 | 7.0327 | 6.5462 | 5.6179 | 8.8702 | 8.2508 | 7.0676 | 10.0782 | 9.3719 | 8.0222 | 11.3646 | 10.5661 | 9.0396 | 13.6814 | 12.7174 | 10.8736
b) 1:3:6 Concrete | 0.51223 | 0.47755 | 0.41145 | 0.70327 | 0.65462 | 0.56179 | 0.88702 | 0.82508 | 0.70676 | 1.0078 | 0.93719 | 0.80222 | 1.1365 | 1.0566 | 0.90396 | 1.3681 | 1.2717 | 1.0874
c) Reinforcement | 368.8051 | 343.8366 | 296.2469 | 506.353 | 471.3273 | 404.4873 | 638.6526 | 594.0545 | 508.8699 | 725.6302 | 674.7758 | 577.5976 | 818.2511 | 760.7573 | 650.8501 | 985.063 | 915.6529 | 782.9006
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 9.9244 | 9.2525 | 7.9719 | 13.6258 | 12.6833 | 10.8846 | 17.186 | 15.9858 | 13.6935 | 19.5265 | 18.158 | 15.543 | 22.0189 | 20.4718 | 17.5142 | 26.5078 | 24.64 | 21.0676
b) 1:3:6 Concrete | 0.99244 | 0.92525 | 0.79719 | 1.3626 | 1.2683 | 1.0885 | 1.7186 | 1.5986 | 1.3694 | 1.9527 | 1.8158 | 1.5543 | 2.2019 | 2.0472 | 1.7514 | 2.6508 | 2.464 | 2.1068
c) Reinforcement | 714.5598 | 666.1833 | 573.9784 | 981.059 | 913.1966 | 783.6942 | 1237.3895 | 1150.9805 | 985.9354 | 1405.9086 | 1307.3781 | 1119.0953 | 1585.3616 | 1473.9673 | 1261.0221 | 1908.5595 | 1774.0775 | 1516.8699
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 14.0863 | 13.1326 | 11.315 | 19.3399 | 18.0021 | 15.4492 | 24.393 | 22.6896 | 19.436 | 27.715 | 25.7727 | 22.061 | 31.2526 | 29.0567 | 24.8589 | 37.6239 | 34.9729 | 29.9025
b) 1:3:6 Concrete | 1.4086 | 1.3133 | 1.1315 | 1.934 | 1.8002 | 1.5449 | 2.4393 | 2.269 | 1.9436 | 2.7715 | 2.5773 | 2.2061 | 3.1253 | 2.9057 | 2.4859 | 3.7624 | 3.4973 | 2.9902
c) Reinforcement | 1014.214 | 945.5506 | 814.679 | 1392.4708 | 1296.15 | 1112.3402 | 1756.2947 | 1633.6498 | 1399.3922 | 1995.4832 | 1855.6334 | 1588.3934 | 2250.1907 | 2092.0826 | 1789.8378 | 2708.9232 | 2518.0455 | 2152.9766
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 9.49 | 8.965 | 7.9849 | 12.3471 | 11.5981 | 10.1906 | 15.1088 | 14.1538 | 12.3512 | 16.9201 | 15.8338 | 13.7789 | 18.8413 | 17.618 | 15.3 | 22.2775 | 20.8137 | 18.0333
b) 1:3:6 Concrete | 0.949 | 0.8965 | 0.79849 | 1.2347 | 1.1598 | 1.0191 | 1.5109 | 1.4154 | 1.2351 | 1.692 | 1.5834 | 1.3779 | 1.8841 | 1.7618 | 1.53 | 2.2277 | 2.0814 | 1.8033
c) Reinforcement | 683.2773 | 645.4789 | 574.9116 | 888.9906 | 835.0606 | 733.7255 | 1087.836 | 1019.0738 | 889.2867 | 1218.2455 | 1140.0304 | 992.0796 | 1356.5707 | 1268.4986 | 1101.6001 | 1603.9789 | 1498.5871 | 1298.3963
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 18.3868 | 17.3697 | 15.4707 | 23.9225 | 22.4712 | 19.7443 | 29.2734 | 27.423 | 23.9305 | 32.7826 | 30.6779 | 26.6966 | 36.5049 | 34.1349 | 29.6438 | 43.1626 | 40.3266 | 34.9395
b) 1:3:6 Concrete | 1.8387 | 1.737 | 1.5471 | 2.3922 | 2.2471 | 1.9744 | 2.9273 | 2.7423 | 2.393 | 3.2783 | 3.0678 | 2.6697 | 3.6505 | 3.4135 | 2.9644 | 4.3163 | 4.0327 | 3.4939
c) Reinforcement | 1323.8498 | 1250.6154 | 1113.8913 | 1722.4194 | 1617.93 | 1421.5932 | 2107.6823 | 1974.4555 | 1722.9931 | 2360.3507 | 2208.8089 | 1922.1541 | 2628.3557 | 2457.7161 | 2134.3501 | 3107.7091 | 2903.5125 | 2515.6429
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 26.0974 | 24.6537 | 21.9584 | 33.9545 | 31.8947 | 28.0242 | 41.5493 | 38.923 | 33.9658 | 46.5302 | 43.5428 | 37.8919 | 51.8135 | 48.4496 | 42.075 | 61.2631 | 57.2377 | 49.5915
b) 1:3:6 Concrete | 2.6097 | 2.4654 | 2.1958 | 3.3955 | 3.1895 | 2.8024 | 4.1549 | 3.8923 | 3.3966 | 4.653 | 4.3543 | 3.7892 | 5.1813 | 4.845 | 4.2075 | 6.1263 | 5.7238 | 4.9592
c) Reinforcement | 1879.0126 | 1775.067 | 1581.007 | 2444.7243 | 2296.4168 | 2017.7452 | 2991.549 | 2802.453 | 2445.5385 | 3350.1752 | 3135.0835 | 2728.2188 | 3730.5693 | 3488.3712 | 3029.4002 | 4410.9419 | 4121.1145 | 3570.59
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 13.7043 | 13.0143 | 11.7405 | 17.4351 | 16.4416 | 14.5902 | 21.0511 | 19.7835 | 17.4059 | 23.4194 | 21.9794 | 19.2702 | 25.9261 | 24.3081 | 21.2561 | 30.3924 | 28.4652 | 24.8182
b) 1:3:6 Concrete | 1.3704 | 1.3014 | 1.1741 | 1.7435 | 1.6442 | 1.459 | 2.1051 | 1.9783 | 1.7406 | 2.3419 | 2.1979 | 1.927 | 2.5926 | 2.4308 | 2.1256 | 3.0392 | 2.8465 | 2.4818
c) Reinforcement | 986.7113 | 937.0278 | 845.3182 | 1255.3266 | 1183.7965 | 1050.4919 | 1515.678 | 1424.4102 | 1253.2246 | 1686.1987 | 1582.5185 | 1387.4527 | 1866.6792 | 1750.1804 | 1530.4373 | 2188.2521 | 2049.4977 | 1786.91
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 26.5521 | 25.2152 | 22.7473 | 33.7805 | 31.8556 | 28.2684 | 40.7865 | 38.3305 | 33.7239 | 45.3751 | 42.5851 | 37.336 | 50.2318 | 47.0969 | 41.1836 | 58.8853 | 55.1514 | 48.0853
b) 1:3:6 Concrete | 2.6552 | 2.5215 | 2.2747 | 3.378 | 3.1856 | 2.8268 | 4.0786 | 3.833 | 3.3724 | 4.5375 | 4.2585 | 3.7336 | 5.0232 | 4.7097 | 4.1184 | 5.8885 | 5.5151 | 4.8085
c) Reinforcement | 1911.7532 | 1815.4914 | 1637.804 | 2432.1952 | 2293.6057 | 2035.3281 | 2936.626 | 2759.7947 | 2428.1227 | 3267.0099 | 3066.1295 | 2688.1896 | 3616.6909 | 3390.9744 | 2965.2222 | 4239.7385 | 3970.9018 | 3462.1382
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 37.6869 | 35.7893 | 32.2865 | 47.9465 | 45.2144 | 40.123 | 57.8905 | 54.4046 | 47.8662 | 64.4034 | 60.4434 | 52.993 | 71.2968 | 66.8472 | 58.4542 | 83.5791 | 78.2794 | 68.25
b) 1:3:6 Concrete | 3.7687 | 3.5789 | 3.2286 | 4.7947 | 4.5214 | 4.0123 | 5.789 | 5.4405 | 4.7866 | 6.4403 | 6.0443 | 5.2993 | 7.1297 | 6.6847 | 5.8454 | 8.3579 | 7.8279 | 6.825
c) Reinforcement | 2713.4561 | 2576.8265 | 2324.6251 | 3452.148 | 3255.4404 | 2888.8528 | 4168.1144 | 3917.128 | 3446.3677 | 4637.0464 | 4351.9258 | 3815.4949 | 5133.3678 | 4812.996 | 4208.7025 | 6017.6934 | 5636.1187 | 4914.0026
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 21.7738 | 20.7585 | 18.9034 | 27.2307 | 25.7572 | 23.0312 | 32.5325 | 30.6514 | 27.1424 | 36.0009 | 33.8663 | 29.8693 | 39.6647 | 37.2707 | 32.7735 | 46.1702 | 43.3306 | 37.9746
b) 1:3:6 Concrete | 2.1774 | 2.0759 | 1.8903 | 2.7231 | 2.5757 | 2.3031 | 3.2533 | 3.0651 | 2.7142 | 3.6001 | 3.3866 | 2.9869 | 3.9665 | 3.7271 | 3.2774 | 4.617 | 4.3331 | 3.7975
c) Reinforcement | 1567.7145 | 1494.6133 | 1361.0468 | 1960.6073 | 1854.5214 | 1658.2463 | 2342.3404 | 2206.8973 | 1954.2546 | 2592.0642 | 2438.375 | 2150.5897 | 2855.8601 | 2683.4905 | 2359.6952 | 3324.2539 | 3119.8062 | 2734.1705
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 42.1868 | 40.2196 | 36.6254 | 52.7594 | 49.9047 | 44.6229 | 63.0317 | 59.387 | 52.5884 | 69.7517 | 65.616 | 57.8718 | 76.8504 | 72.212 | 63.4987 | 89.4547 | 83.9531 | 73.5758
b) 1:3:6 Concrete | 4.2187 | 4.022 | 3.6625 | 5.2759 | 4.9905 | 4.4623 | 6.3032 | 5.9387 | 5.2588 | 6.9752 | 6.5616 | 5.7872 | 7.685 | 7.2212 | 6.3499 | 8.9455 | 8.3953 | 7.3576
c) Reinforcement | 3037.4469 | 2895.8133 | 2637.0282 | 3798.6766 | 3593.1352 | 3212.8521 | 4538.2845 | 4275.8635 | 3786.3683 | 5022.1243 | 4724.3515 | 4166.7676 | 5533.229 | 5199.2628 | 4571.9095 | 6440.7419 | 6044.6246 | 5297.4553
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 59.878 | 57.0859 | 51.9844 | 74.8843 | 70.8324 | 63.3358 | 89.4644 | 84.2912 | 74.6417 | 99.0025 | 93.1324 | 82.1406 | 109.078 | 102.4944 | 90.1272 | 126.968 | 119.1593 | 104.4301
b) 1:3:6 Concrete | 5.9878 | 5.7086 | 5.1984 | 7.4884 | 7.0832 | 6.3336 | 8.9464 | 8.4291 | 7.4642 | 9.9002 | 9.3132 | 8.2141 | 10.9078 | 10.2494 | 9.0127 | 12.6968 | 11.9159 | 10.443
c) Reinforcement | 4311.215 | 4110.1866 | 3742.8787 | 5391.67 | 5099.9339 | 4560.1772 | 6441.436 | 6068.9675 | 5374.2002 | 7128.1765 | 6705.5311 | 5914.1217 | 7853.6153 | 7379.5988 | 6489.1619 | 9141.6982 | 8579.4671 | 7518.9689
TRIPPLE ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 7.1322 | 6.6324 | 5.7029 | 9.7905 | 9.0893 | 7.7831 | 12.3482 | 11.4552 | 9.7901 | 14.0298 | 13.0115 | 11.1118 | 15.8207 | 14.6694 | 12.5206 | 19.0463 | 17.6562 | 15.0606
b) 1:3:6 Concrete | 0.71322 | 0.66324 | 0.57029 | 0.97905 | 0.90893 | 0.77831 | 1.2348 | 1.1455 | 0.97901 | 1.403 | 1.3011 | 1.1112 | 1.5821 | 1.4669 | 1.2521 | 1.9046 | 1.7656 | 1.5061
c) Reinforcement | 513.5156 | 477.5358 | 410.606 | 704.9162 | 654.4294 | 560.3855 | 889.0672 | 824.7712 | 704.8856 | 1010.1486 | 936.8273 | 800.0469 | 1139.0936 | 1056.1944 | 901.4844 | 1371.3355 | 1271.2468 | 1084.3606
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 13.8186 | 12.8504 | 11.0493 | 18.9691 | 17.6105 | 15.0798 | 23.9246 | 22.1944 | 18.9683 | 27.1828 | 25.2098 | 21.529 | 30.6527 | 28.4219 | 24.2587 | 36.9023 | 34.2089 | 29.1798
b) 1:3:6 Concrete | 1.3819 | 1.285 | 1.1049 | 1.8969 | 1.7611 | 1.508 | 2.3925 | 2.2194 | 1.8968 | 2.7183 | 2.521 | 2.1529 | 3.0653 | 2.8422 | 2.4259 | 3.6902 | 3.4209 | 2.918
c) Reinforcement | 994.9365 | 925.2256 | 795.5491 | 1365.7751 | 1267.9569 | 1085.747 | 1722.5677 | 1597.9943 | 1365.7158 | 1957.1629 | 1815.103 | 1550.091 | 2206.9938 | 2046.3767 | 1746.626 | 2656.9625 | 2463.0406 | 2100.9486
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 19.6134 | 18.2392 | 15.6829 | 26.9239 | 24.9956 | 21.4036 | 33.9574 | 31.5017 | 26.9227 | 38.5821 | 35.7816 | 30.5573 | 43.507 | 40.3408 | 34.4317 | 52.3774 | 48.5546 | 41.4166
b) 1:3:6 Concrete | 1.9613 | 1.8239 | 1.5683 | 2.6924 | 2.4996 | 2.1404 | 3.3957 | 3.1502 | 2.6923 | 3.8582 | 3.5782 | 3.0557 | 4.3507 | 4.0341 | 3.4432 | 5.2377 | 4.8555 | 4.1417
c) Reinforcement | 1412.1679 | 1313.2235 | 1129.1664 | 1938.5195 | 1799.6808 | 1541.0602 | 2444.9347 | 2268.1209 | 1938.4353 | 2777.9087 | 2576.2752 | 2200.1291 | 3132.5073 | 2904.5347 | 2479.0821 | 3771.1726 | 3495.9286 | 2981.9916
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 13.2914 | 12.5368 | 11.1587 | 17.2882 | 16.2101 | 14.2269 | 21.157 | 19.7812 | 17.238 | 23.6959 | 22.1304 | 19.2297 | 26.3898 | 24.6264 | 21.3528 | 31.2094 | 29.0985 | 25.1698
b) 1:3:6 Concrete | 1.3291 | 1.2537 | 1.1159 | 1.7288 | 1.621 | 1.4227 | 2.1157 | 1.9781 | 1.7238 | 2.3696 | 2.213 | 1.923 | 2.639 | 2.4626 | 2.1353 | 3.1209 | 2.9098 | 2.517
c) Reinforcement | 956.9772 | 902.6507 | 803.4273 | 1244.7479 | 1167.1238 | 1024.3348 | 1523.3016 | 1424.2444 | 1241.1356 | 1706.1037 | 1593.3857 | 1384.5358 | 1900.064 | 1773.1021 | 1537.4035 | 2247.0765 | 2095.0886 | 1812.2291
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 25.752 | 24.2901 | 21.62 | 33.4958 | 31.407 | 27.5646 | 40.9916 | 38.326 | 33.3986 | 45.9108 | 42.8776 | 37.2575 | 51.1302 | 47.7137 | 41.3711 | 60.4682 | 56.3783 | 48.7666
b) 1:3:6 Concrete | 2.5752 | 2.429 | 2.162 | 3.3496 | 3.1407 | 2.7565 | 4.0992 | 3.8326 | 3.3399 | 4.5911 | 4.2878 | 3.7257 | 5.113 | 4.7714 | 4.1371 | 6.0468 | 5.6378 | 4.8767
c) Reinforcement | 1854.1434 | 1748.8858 | 1556.6405 | 2411.6991 | 2261.3023 | 1984.6487 | 2951.3968 | 2759.4735 | 2404.7002 | 3305.5759 | 3087.1849 | 2682.538 | 3681.374 | 3435.3852 | 2978.7194 | 4353.7107 | 4059.2342 | 3511.1938
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 36.5512 | 34.4762 | 30.6865 | 47.5425 | 44.5776 | 39.1239 | 58.1817 | 54.3982 | 47.4045 | 65.1637 | 60.8585 | 52.8816 | 72.5719 | 67.7226 | 58.7203 | 85.8258 | 80.0207 | 69.2171
b) 1:3:6 Concrete | 3.6551 | 3.4476 | 3.0686 | 4.7542 | 4.4578 | 3.9124 | 5.8182 | 5.4398 | 4.7404 | 6.5164 | 6.0858 | 5.2882 | 7.2572 | 6.7723 | 5.872 | 8.5826 | 8.0021 | 6.9217
c) Reinforcement | 2631.6874 | 2482.2896 | 2209.4252 | 3423.0568 | 3209.5904 | 2816.9207 | 4189.0793 | 3916.6721 | 3413.1228 | 4691.7852 | 4381.8108 | 3807.4733 | 5225.1761 | 4876.0307 | 4227.8597 | 6179.4603 | 5761.4937 | 4983.6299
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 19.2389 | 18.2485 | 16.4577 | 24.4729 | 23.0441 | 20.4332 | 29.556 | 27.7307 | 24.3719 | 32.8884 | 30.8137 | 26.9833 | 36.4171 | 34.0849 | 29.7673 | 42.7072 | 39.9279 | 34.7646
b) 1:3:6 Concrete | 1.9239 | 1.8248 | 1.6458 | 2.4473 | 2.3044 | 2.0433 | 2.9556 | 2.7731 | 2.4372 | 3.2888 | 3.0814 | 2.6983 | 3.6417 | 3.4085 | 2.9767 | 4.2707 | 3.9928 | 3.4765
c) Reinforcement | 1385.2002 | 1313.8918 | 1184.9564 | 1762.0521 | 1659.1732 | 1471.1878 | 2128.035 | 1996.6093 | 1754.776 | 2367.9645 | 2218.5842 | 1942.7987 | 2622.0319 | 2454.1098 | 2143.2422 | 3074.9203 | 2874.8097 | 2503.0498
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 37.2754 | 35.3565 | 31.8868 | 47.4163 | 44.6479 | 39.5893 | 57.2648 | 53.7282 | 47.2205 | 63.7213 | 59.7015 | 52.2802 | 70.5582 | 66.0394 | 57.6741 | 82.7453 | 77.3603 | 67.3564
b) 1:3:6 Concrete | 3.7275 | 3.5356 | 3.1887 | 4.7416 | 4.4648 | 3.9589 | 5.7265 | 5.3728 | 4.7221 | 6.3721 | 5.9701 | 5.228 | 7.0558 | 6.6039 | 5.7674 | 8.2745 | 7.736 | 6.7356
c) Reinforcement | 2683.8253 | 2545.6653 | 2295.853 | 3413.976 | 3214.648 | 2850.4264 | 4123.0678 | 3868.4306 | 3399.8785 | 4587.9312 | 4298.5068 | 3764.1724 | 5080.1868 | 4754.8377 | 4152.5318 | 5957.658 | 5569.9438 | 4849.659
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 52.907 | 50.1834 | 45.2588 | 67.3006 | 63.3712 | 56.1912 | 81.2791 | 76.2594 | 67.0227 | 90.4431 | 84.7376 | 74.2041 | 100.1471 | 93.7334 | 81.8599 | 117.4449 | 109.8018 | 95.6026
b) 1:3:6 Concrete | 5.2907 | 5.0183 | 4.5259 | 6.7301 | 6.3371 | 5.6191 | 8.1279 | 7.6259 | 6.7023 | 9.0443 | 8.4738 | 7.4204 | 10.0147 | 9.3733 | 8.186 | 11.7445 | 10.9802 | 9.5603
c) Reinforcement | 3809.3004 | 3613.2023 | 3258.63 | 4845.6434 | 4562.7262 | 4045.7665 | 5852.0962 | 5490.6756 | 4825.634 | 6511.9024 | 6101.1064 | 5342.6963 | 7210.5878 | 6748.802 | 5893.916 | 8456.0307 | 7905.7267 | 6883.387
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 30.6209 | 29.1655 | 26.5578 | 38.2965 | 36.1787 | 32.3318 | 45.7726 | 43.0647 | 38.1018 | 50.6692 | 47.5944 | 41.9356 | 55.8451 | 52.3947 | 46.0228 | 65.0412 | 60.9458 | 53.3496
b) 1:3:6 Concrete | 3.0621 | 2.9166 | 2.6558 | 3.8296 | 3.6179 | 3.2332 | 4.5773 | 4.3065 | 3.8102 | 5.0669 | 4.7594 | 4.1936 | 5.5845 | 5.2395 | 4.6023 | 6.5041 | 6.0946 | 5.335
c) Reinforcement | 2204.7071 | 2099.9194 | 1912.1581 | 2757.3469 | 2604.8686 | 2327.8878 | 3295.6253 | 3100.6552 | 2743.3331 | 3648.1824 | 3426.7968 | 3019.3664 | 4020.8491 | 3772.4192 | 3313.644 | 4682.9655 | 4388.1 | 3841.1683
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 59.3281 | 56.5082 | 51.4556 | 74.1994 | 70.0963 | 62.6428 | 88.6844 | 83.4378 | 73.8223 | 98.1716 | 92.2142 | 81.2503 | 108.1999 | 101.5148 | 89.1692 | 126.0173 | 118.0826 | 103.3648
b) 1:3:6 Concrete | 5.9328 | 5.6508 | 5.1456 | 7.4199 | 7.0096 | 6.2643 | 8.8684 | 8.3438 | 7.3822 | 9.8172 | 9.2214 | 8.125 | 10.82 | 10.1515 | 8.9169 | 12.6017 | 11.8083 | 10.3365
c) Reinforcement | 4271.6199 | 4068.5938 | 3704.8063 | 5342.3597 | 5046.933 | 4510.2826 | 6385.2741 | 6007.5194 | 5315.208 | 7068.3534 | 6639.4189 | 5850.0225 | 7790.3951 | 7309.0622 | 6420.1853 | 9073.2456 | 8501.9437 | 7442.2636
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 84.2076 | 80.2053 | 73.0338 | 105.3153 | 99.4915 | 88.9124 | 125.8746 | 118.4278 | 104.7801 | 139.3403 | 130.8846 | 115.323 | 153.5741 | 144.0855 | 126.5628 | 178.8633 | 167.601 | 146.7113
b) 1:3:6 Concrete | 8.4208 | 8.0205 | 7.3034 | 10.5315 | 9.9492 | 8.8912 | 12.5875 | 11.8428 | 10.478 | 13.934 | 13.0885 | 11.5323 | 15.3574 | 14.4085 | 12.6563 | 17.8863 | 16.7601 | 14.6711
c) Reinforcement | 6062.9444 | 5774.7783 | 5258.4347 | 7582.7041 | 7163.3887 | 6401.6915 | 9062.9697 | 8526.8018 | 7544.1662 | 10032.5016 | 9423.6913 | 8303.2577 | 11057.3349 | 10374.1528 | 9112.521 | 12878.1551 | 12067.2749 | 10563.2128
QUAD ACSR BERSIMIS
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 9.142 | 8.4894 | 7.2912 | 12.5483 | 11.6324 | 9.9484 | 15.8261 | 14.6596 | 12.5125 | 17.9815 | 16.6511 | 14.2013 | 20.2769 | 18.7727 | 16.0016 | 24.4112 | 22.595 | 19.2475
b) 1:3:6 Concrete | 0.9142 | 0.84894 | 0.72912 | 1.2548 | 1.1632 | 0.99484 | 1.5826 | 1.466 | 1.2513 | 1.7981 | 1.6651 | 1.4201 | 2.0277 | 1.8773 | 1.6002 | 2.4411 | 2.2595 | 1.9248
c) Reinforcement | 658.2261 | 611.2351 | 524.9651 | 903.4794 | 837.5315 | 716.2838 | 1139.4817 | 1055.488 | 900.9012 | 1294.667 | 1198.8789 | 1022.4963 | 1459.936 | 1351.6316 | 1152.1187 | 1757.608 | 1626.8406 | 2309.701
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 17.7127 | 16.4482 | 14.1267 | 24.3124 | 22.5377 | 19.275 | 30.6631 | 28.4029 | 24.243 | 34.8391 | 32.2615 | 27.5151 | 39.2865 | 36.372 | 31.0032 | 47.2967 | 43.7778 | 37.292
b) 1:3:6 Concrete | 1.7713 | 1.6448 | 1.4127 | 2.4312 | 2.2538 | 1.9275 | 3.0663 | 2.8403 | 2.4243 | 3.4839 | 3.2261 | 2.7515 | 3.9286 | 3.6372 | 3.1003 | 4.7297 | 4.3778 | 3.7292
c) Reinforcement | 1275.3131 | 1184.2679 | 1017.1198 | 1750.4913 | 1622.7173 | 1387.7998 | 2207.7458 | 2045.008 | 1745.4961 | 2508.4173 | 2322.8279 | 1981.0866 | 2828.6259 | 2618.7861 | 2232.23 | 3405.3654 | 3152.0037 | 2685.0274
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 25.1406 | 23.3458 | 20.0507 | 34.5079 | 31.9891 | 27.3581 | 43.5219 | 40.3138 | 34.4094 | 49.4491 | 45.7905 | 39.0537 | 55.7614 | 51.6248 | 44.0045 | 67.1309 | 62.1363 | 52.9306
b) 1:3:6 Concrete | 2.5141 | 2.3346 | 2.0051 | 3.4508 | 3.1989 | 2.7358 | 4.3522 | 4.0314 | 3.4409 | 4.9449 | 4.5791 | 3.9054 | 5.5761 | 5.1625 | 4.4005 | 6.7131 | 6.2136 | 5.2931
c) Reinforcement | 1810.1219 | 1680.8964 | 1443.6539 | 2484.5683 | 2303.2116 | 1969.7803 | 3133.5747 | 2902.592 | 2477.4784 | 3560.3342 | 3296.917 | 2811.8649 | 4014.8239 | 3716.9868 | 3168.3264 | 4833.4219 | 4473.8116 | 3811.0067
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 17.0927 | 16.1086 | 14.3325 | 22.2292 | 20.822 | 18.2631 | 27.2051 | 25.4085 | 22.1248 | 30.4717 | 28.427 | 24.6804 | 33.9383 | 31.6348 | 27.4057 | 40.1413 | 37.3832 | 32.3064
b) 1:3:6 Concrete | 1.7093 | 1.6109 | 1.4333 | 2.2229 | 2.0822 | 1.8263 | 2.7205 | 2.5409 | 2.2125 | 3.0472 | 2.8427 | 2.468 | 3.3938 | 3.1635 | 2.7406 | 4.0141 | 3.7383 | 3.2306
c) Reinforcement | 1230.6771 | 1159.8226 | 1031.943 | 1600.5052 | 1499.1869 | 1314.9441 | 1958.7671 | 1829.415 | 1592.9844 | 2193.9619 | 2046.7411 | 1776.992 | 2443.5574 | 2277.7055 | 1973.207 | 2890.174 | 2691.5902 | 2326.0618
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 33.1172 | 31.2105 | 27.7693 | 43.0692 | 40.3427 | 35.3848 | 52.7099 | 49.229 | 42.8668 | 59.0389 | 55.0772 | 47.8184 | 65.7555 | 61.2924 | 53.0985 | 77.7738 | 72.4299 | 62.5937
b) 1:3:6 Concrete | 3.3117 | 3.1211 | 2.7769 | 4.3069 | 4.0343 | 3.5385 | 5.271 | 4.9229 | 4.2867 | 5.9039 | 5.5077 | 4.7818 | 6.5755 | 6.1292 | 5.3098 | 7.7774 | 7.243 | 6.2594
c) Reinforcement | 2384.437 | 2247.1563 | 1999.3896 | 3100.9788 | 2904.6747 | 2547.7041 | 3795.1113 | 3544.4915 | 3086.4073 | 4250.8012 | 3965.5609 | 3442.9219 | 4734.3924 | 4413.0544 | 3823.0886 | 5599.7122 | 5214.956 | 4506.7447
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 47.005 | 44.2988 | 39.4145 | 61.1304 | 57.2606 | 50.2236 | 74.814 | 69.8735 | 60.8432 | 83.7972 | 78.1741 | 67.8712 | 93.3303 | 86.9957 | 75.3655 | 110.3886 | 102.8038 | 88.8426
b) 1:3:6 Concrete | 4.7005 | 4.4299 | 3.9414 | 6.113 | 5.7261 | 5.0224 | 7.4814 | 6.9873 | 6.0843 | 8.3797 | 7.8174 | 6.7871 | 9.333 | 8.6996 | 7.5366 | 11.0389 | 10.2804 | 8.8843
c) Reinforcement | 3384.3621 | 3189.5121 | 2837.8434 | 4401.3893 | 4122.764 | 3616.0962 | 5386.6096 | 5030.8912 | 4380.7071 | 6033.3952 | 5628.5381 | 4886.7279 | 6719.7828 | 6263.6901 | 5426.3193 | 7947.9786 | 7401.873 | 6396.6698
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 24.7735 | 23.4827 | 21.1749 | 31.5108 | 29.6465 | 26.2762 | 38.061 | 35.6779 | 31.3379 | 42.3574 | 39.6479 | 34.6965 | 46.9081 | 43.8617 | 38.2784 | 55.0221 | 51.3906 | 44.711
b) 1:3:6 Concrete | 2.4773 | 2.3483 | 2.1175 | 3.1511 | 2.9647 | 2.6276 | 3.8061 | 3.5678 | 3.1338 | 4.2357 | 3.9648 | 3.4696 | 4.6908 | 4.3862 | 3.8278 | 5.5022 | 5.1391 | 4.4711
c) Reinforcement | 1783.689 | 1690.7557 | 1524.5945 | 2268.7777 | 2134.5498 | 1891.8837 | 2740.392 | 2568.8085 | 2256.3274 | 3049.7304 | 2854.6499 | 2498.1446 | 3377.3846 | 3158.0392 | 2756.0471 | 3961.5884 | 3700.1217 | 3219.1896
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 47.9986 | 45.4978 | 41.0264 | 61.0522 | 57.4401 | 50.9101 | 73.7432 | 69.1259 | 60.7171 | 82.0674 | 76.8178 | 67.2244 | 90.8845 | 84.982 | 74.1645 | 106.6052 | 99.5692 | 86.6275
b) 1:3:6 Concrete | 4.7999 | 4.5498 | 4.1026 | 6.1052 | 5.744 | 5.091 | 7.3743 | 6.9126 | 6.0717 | 8.2067 | 7.6818 | 6.7224 | 9.0884 | 8.4982 | 7.4164 | 10.6605 | 9.9569 | 8.6627
c) Reinforcement | 3455.8974 | 3275.8391 | 2953.9019 | 4395.7568 | 4135.6903 | 3665.5247 | 5309.5095 | 4977.0664 | 4371.6342 | 5908.8526 | 5530.8841 | 4840.1552 | 6543.6827 | 6118.701 | 5339.8413 | 7675.5775 | 7168.9858 | 6237.1799
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 68.127 | 64.5775 | 58.231 | 86.6547 | 81.5279 | 72.2594 | 104.6678 | 98.1142 | 86.1792 | 116.4828 | 109.0318 | 95.4152 | 128.9973 | 120.6196 | 105.2657 | 151.3107 | 141.3241 | 122.9552
b) 1:3:6 Concrete | 6.8127 | 6.4577 | 5.8231 | 8.6655 | 8.1528 | 7.2259 | 10.4668 | 9.8114 | 8.6179 | 11.6483 | 10.9032 | 9.5415 | 12.8997 | 12.062 | 10.5266 | 15.1311 | 14.1324 | 12.2955
c) Reinforcement | 4905.1447 | 4649.5781 | 4192.635 | 6239.1387 | 5870.0121 | 5202.6803 | 7536.0781 | 7064.2233 | 6204.9002 | 8386.7585 | 7850.2871 | 6869.8977 | 9287.8078 | 8684.6079 | 7579.1295 | 10894.3681 | 10175.3347 | 8852.7715
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 39.468 | 37.5726 | 34.2121 | 49.3623 | 46.6002 | 41.6324 | 59.0126 | 55.478 | 49.0613 | 65.3375 | 61.3225 | 54.002 | 72.0255 | 67.5187 | 59.2721 | 83.9122 | 78.561 | 68.7245
b) 1:3:6 Concrete | 3.9468 | 3.7573 | 3.4212 | 4.9362 | 4.66 | 4.1632 | 5.9013 | 5.5478 | 4.9061 | 6.5338 | 6.1322 | 5.4002 | 7.2026 | 6.7519 | 5.9272 | 8.3912 | 7.8561 | 6.8725
c) Reinforcement | 2841.6996 | 2705.2254 | 2463.2693 | 3554.0866 | 3355.2159 | 2997.5293 | 4248.9103 | 3994.4131 | 3532.4117 | 4704.3006 | 4415.2187 | 3888.1432 | 5185.838 | 4861.3479 | 4267.5928 | 6041.6771 | 5656.3937 | 4948.1661
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 76.4693 | 72.7969 | 66.2859 | 95.6395 | 90.2879 | 80.6627 | 114.337 | 107.4885 | 95.0562 | 126.5914 | 118.8123 | 104.6289 | 139.5495 | 130.8175 | 114.8397 | 162.5799 | 152.212 | 133.1538
b) 1:3:6 Concrete | 7.6469 | 7.2797 | 6.6286 | 9.5639 | 9.0288 | 8.0663 | 11.4337 | 10.7489 | 9.5056 | 12.6591 | 11.8812 | 10.4629 | 13.9549 | 13.0818 | 11.484 | 16.258 | 15.2212 | 13.3154
c) Reinforcement | 5505.7929 | 5241.3743 | 4772.5843 | 6886.0428 | 6500.7307 | 5807.7131 | 8232.2637 | 7739.1754 | 6844.0476 | 9114.5825 | 8554.4862 | 7533.2774 | 10047.5611 | 9418.8616 | 8268.4611 | 11705.7493 | 10959.2628 | 9587.0718
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 108.5371 | 103.3246 | 94.0832 | 135.7464 | 128.1506 | 114.489 | 162.2848 | 152.5644 | 134.9185 | 179.6781 | 168.6368 | 148.5055 | 198.0702 | 185.6765 | 162.9983 | 230.7585 | 216.0428 | 188.9925
b) 1:3:6 Concrete | 10.8537 | 10.3325 | 9.4083 | 13.5746 | 12.8151 | 11.4489 | 16.2285 | 15.2564 | 13.4919 | 17.9678 | 16.8637 | 14.8505 | 19.807 | 18.5676 | 16.2998 | 23.0758 | 21.6043 | 18.8992
c) Reinforcement | 7814.6738 | 7439.37 | 6773.9907 | 9773.7382 | 9226.8436 | 8243.2057 | 11684.5033 | 10984.636 | 9714.1321 | 12936.8268 | 12141.8514 | 10692.3937 | 14261.0545 | 13368.7068 | 11735.8802 | 16614.6119 | 15555.0826 | 13607.4568

## Abstract of Weights- Moose
ABSTRACT OF WEIGHTS OF TOWERS IN KG
AS PER RYLE'S FORMULA
(FOR 400KV D/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR MOOSE
'A' TYPE TOWER | 9107.2629 | 8867.0675 | 8236.8076 | 10654.511 | 10366.8386 | 9609.8005 | 11954.0295 | 11627.9013 | 10768.2702 | 12735.795 | 12386.9423 | 11466.7742 | 13518.3019 | 13146.9197 | 12166.8019 | 14823.082 | 14414.4716 | 13335.426
'B' TYPE TOWER | 15232.5669 | 14915.9441 | 14106.0464 | 17293.8018 | 16898.4575 | 15874.8267 | 19067.1948 | 18612.4108 | 17426.6329 | 20142.0348 | 19653.708 | 18376.6076 | 21220.2389 | 20699.6057 | 19334.8028 | 23018.4072 | 22446.03 | 20941.3655
'C' TYPE TOWER | 18474.3521 | 18128.9653 | 17255.7237 | 20729.2958 | 20290.3432 | 19162.2094 | 22688.5458 | 22180.6901 | 20863.1044 | 23879.1302 | 23333.1622 | 21910.8597 | 25073.8831 | 24491.7184 | 22970.244 | 27064.861 | 26425.6671 | 24748.7139
'D' TYPE TOWER | 23445.4466 | 23042.6433 | 22033.9503 | 26079.1107 | 25560.0611 | 24234.1148 | 28384.5969 | 27781.5378 | 26223.2464 | 29787.9639 | 29139.1942 | 27454.3786 | 31196.1938 | 30504.5356 | 28701.2944 | 33540.2872 | 32782.0608 | 30795.9328
TRIPPLE ACSR MOOSE
'A' TYPE TOWER | 10889.2352 | 10596.946 | 9836.8631 | 12737.2729 | 12387.0901 | 11473.7062 | 14289.8054 | 13892.743 | 12855.3492 | 15223.8657 | 14799.1065 | 13688.5595 | 16158.8472 | 15706.6322 | 14523.6554 | 17717.9067 | 17220.3287 | 15917.8544
'B' TYPE TOWER | 18274.4558 | 17890.7511 | 16917.0598 | 20740.2453 | 20260.5525 | 19027.9444 | 22863.6274 | 22311.476 | 20882.4713 | 24151.0426 | 23558.0201 | 22018.4666 | 25442.6746 | 24810.3011 | 23164.6341 | 27596.9886 | 26901.6137 | 25086.8325
'C' TYPE TOWER | 22191.5201 | 21773.639 | 20724.814 | 24892.5299 | 24360.6192 | 23002.9282 | 27242.0644 | 26626.1888 | 25038.8887 | 28670.4646 | 28008.1678 | 26294.0213 | 30104.1471 | 29397.7805 | 27563.5688 | 32493.6107 | 31717.8462 | 29695.5392
'D' TYPE TOWER | 28188.5195 | 27701.7688 | 26491.0034 | 31347.3404 | 30718.9858 | 29123.7067 | 34116.2554 | 33385.5624 | 31508.5504 | 35802.6352 | 35016.2858 | 32985.9226 | 37495.2747 | 36656.7292 | 34482.9068 | 40313.3105 | 39393.7989 | 36998.6027
QUAD ACSR MOOSE
'A' TYPE TOWER | 12914.8006 | 12564.8891 | 11659.2653 | 15105.3561 | 14686.0616 | 13597.5218 | 16945.8819 | 16470.413 | 15233.9362 | 18053.2647 | 17544.611 | 16220.8801 | 19161.7622 | 18620.2144 | 17210.101 | 21010.1797 | 20414.2874 | 18861.6721
'B' TYPE TOWER | 22269.5982 | 21799.5082 | 20611.6126 | 25269.8708 | 24681.8025 | 23176.7598 | 27854.7701 | 27177.6554 | 25432.0643 | 29422.2971 | 28694.9666 | 26814.015 | 30995.0803 | 30219.4103 | 28208.5631 | 33618.4583 | 32765.4126 | 30547.6189
'C' TYPE TOWER | 24865.3336 | 24390.7156 | 23211.8418 | 27906.7109 | 27301.5417 | 25772.0778 | 30556.2425 | 29854.8697 | 28064.3955 | 32168.2073 | 31413.6509 | 29478.9706 | 33786.7901 | 32981.753 | 30910.6028 | 36485.5253 | 35601.0146 | 33316.1487
'D' TYPE TOWER | 30091.8057 | 29570.8014 | 28279.4078 | 33459.5963 | 32786.3866 | 31082.7783 | 36413.7871 | 35630.5755 | 33624.8647 | 38213.5275 | 37370.507 | 35200.3951 | 40020.1835 | 39121.0861 | 36797.2206 | 43028.3383 | 42042.2822 | 39481.2546
(FOR 400KV S/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR MOOSE
'A' TYPE TOWER | 5772.4343 | 5565.668 | 5144.8712 | 6747.738 | 6499.645 | 5993.0248 | 7567.7061 | 7286.1673 | 6710.1083 | 8061.2245 | 7759.9424 | 7142.9455 | 8555.3413 | 8234.5004 | 7576.9953 | 9379.4581 | 9026.3279 | 8302.0465
'B' TYPE TOWER | 7476.868 | 7269.6752 | 6862.1269 | 8467.7543 | 8207.1803 | 7687.4711 | 9323.6025 | 9022.6213 | 8417.2601 | 9843.3608 | 9519.6092 | 8865.9929 | 10365.3204 | 10019.6795 | 9319.781 | 11236.7539 | 10856.1528 | 10082.6419
'C' TYPE TOWER | 9098.1364 | 8872.8989 | 8436.7247 | 10179.7065 | 9890.756 | 9320.6812 | 11124.2347 | 10788.1079 | 10117.4296 | 11699.7146 | 11337.5055 | 10611.1061 | 12278.0606 | 11891.1235 | 11111.9919 | 13243.2412 | 12817.4635 | 11955.87
'D' TYPE TOWER | 11573.8778 | 11311.835 | 10810.9017 | 12835.1631 | 12493.7308 | 11826.0873 | 13945.9258 | 13546.6486 | 12755.1548 | 14624.1897 | 14193.4161 | 13334.2235 | 15306.0152 | 14845.7285 | 13923.1676 | 16442.9769 | 15937.0151 | 14916.7969
TRIPPLE ACSR MOOSE
'A' TYPE TOWER | 6818.5004 | 6568.2955 | 6067.3871 | 7969.2777 | 7668.9183 | 7065.4503 | 8937.1254 | 8596.1892 | 7909.7722 | 9519.7358 | 9154.8532 | 8419.5529 | 10103.0915 | 9714.4908 | 8930.8341 | 11076.0951 | 10648.3461 | 9785.0023
'B' TYPE TOWER | 8856.7249 | 8607.4509 | 8124.424 | 10026.6031 | 9712.4964 | 9094.9388 | 11038.5657 | 10675.3864 | 9955.0532 | 11653.5203 | 11262.7048 | 10484.5087 | 12271.2595 | 11853.8915 | 11020.2395 | 13302.8365 | 12843.0897 | 11921.3249
'C' TYPE TOWER | 10788.2893 | 10517.9953 | 10001.8998 | 12066.1625 | 11718.5101 | 11041.6567 | 13184.3548 | 12779.4072 | 11981.6434 | 13866.2287 | 13429.6246 | 12564.928 | 14551.7768 | 14085.1793 | 13157.1885 | 15696.241 | 15182.5729 | 14155.7203
'D' TYPE TOWER | 13734.0661 | 13420.2497 | 12828.2667 | 15225.4576 | 14815.281 | 14023.0101 | 16542.036 | 16061.6111 | 15120.3006 | 17346.8236 | 16828.1724 | 15805.421 | 18156.2506 | 17601.8057 | 16502.8776 | 19506.5747 | 18896.79 | 17680.6082
QUAD ACSR MOOSE
'A' TYPE TOWER | 7724.1762 | 7436.9584 | 6867.0717 | 9027.0042 | 8682.1213 | 7995.3005 | 10122.9563 | 9731.4286 | 8950.0524 | 10782.7361 | 10363.6851 | 9526.5981 | 11443.3846 | 10997.0754 | 10104.8869 | 12545.339 | 12054.0431 | 11071.0688
'B' TYPE TOWER | 10048.8605 | 9763.6184 | 9215.408 | 11373.7714 | 11013.9621 | 10312.0614 | 12520.7947 | 12104.5468 | 11285.2072 | 13218.0679 | 12770.0462 | 11884.6126 | 13918.6117 | 13440.0711 | 12491.3186 | 15088.6143 | 14561.3821 | 13512.0799
'C' TYPE TOWER | 12247.3787 | 11938.514 | 11353.3111 | 13695.1863 | 13297.3646 | 12528.4184 | 14963.483 | 14499.7664 | 13592.5411 | 15737.2575 | 15237.1455 | 14253.3945 | 16515.376 | 15980.7926 | 14924.7063 | 17814.6155 | 17225.9592 | 16056.9613
'D' TYPE TOWER | 15597.9003 | 15239.7045 | 14568.9142 | 17288.369 | 16819.3874 | 15919.5881 | 18782.6799 | 18232.9101 | 17162.5467 | 19696.6406 | 19102.9242 | 17939.3743 | 20616.129 | 19981.2781 | 18730.5991 | 22150.4272 | 21452.0139 | 20067.3113
(FOR 765KV S/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR MOOSE
'A' TYPE TOWER | 10631.1825 | 10273.2588 | 9548.8544 | 12434.5901 | 12005.5174 | 11134.5775 | 13949.7463 | 13463.066 | 12473.4966 | 14861.4171 | 14340.7169 | 13281.1641 | 15774.066 | 15219.6548 | 14090.819 | 17296.0562 | 16685.9751 | 15442.8626
'B' TYPE TOWER | 15374.7632 | 14966.2397 | 14167.196 | 17438.2747 | 16926.0057 | 15911.8189 | 19216.4084 | 18625.6835 | 17447.538 | 20295.1434 | 19660.193 | 18389.6421 | 21377.8888 | 20700.4031 | 19341.1502 | 23184.7825 | 22439.3114 | 20938.7768
'C' TYPE TOWER | 18640.8784 | 18195.1163 | 17337.2219 | 20888.8044 | 20318.9571 | 19204.1499 | 22846.2701 | 22184.7199 | 20877.6067 | 24037.3364 | 23325.0869 | 21911.4969 | 25233.5379 | 24473.2014 | 22958.7835 | 27228.6698 | 26392.7435 | 24720.4336
'D' TYPE TOWER | 21023.3903 | 20561.1758 | 19683.5918 | 23348.244 | 22748.3361 | 21586.3328 | 25389.0214 | 24689.0501 | 23316.8185 | 26633.2707 | 25878.8314 | 24391.8012 | 27883.0599 | 27077.5657 | 25483.0467 | 29965.612 | 29081.0425 | 27320.6735
TRIPPLE ACSR MOOSE
'A' TYPE TOWER | 12514.7123 | 12077.8313 | 11215.375 | 14634.1514 | 14110.1429 | 13072.4244 | 16415.5576 | 15821.0312 | 14641.5041 | 17487.6036 | 16851.445 | 15588.3005 | 18560.874 | 17883.4686 | 16537.571 | 20350.8143 | 19605.3069 | 18122.9647
'B' TYPE TOWER | 18186.1445 | 17691.1092 | 16744.6274 | 20615.5928 | 19993.6179 | 18788.8859 | 22712.341 | 21994.3817 | 20592.8147 | 23985.1725 | 23213.1383 | 21700.7317 | 25263.0911 | 24439.0738 | 22820.3585 | 27396.1187 | 26489.0648 | 24701.2125
'C' TYPE TOWER | 22089.2623 | 21550.7341 | 20536.2488 | 24740.1929 | 24050.0215 | 22726.9285 | 27053.2741 | 26251.0139 | 24696.7369 | 28461.8986 | 27597.7055 | 25915.5161 | 29877.1313 | 28954.2302 | 27151.0193 | 32238.2592 | 31223.1416 | 29230.6563
'D' TYPE TOWER | 24945.0687 | 24387.9795 | 23351.3687 | 27691.479 | 26966.299 | 25587.8622 | 30108.0615 | 29260.6811 | 27629.2396 | 31582.923 | 30669.0653 | 28899.5366 | 33065.0517 | 32088.923 | 30190.2054 | 35535.694 | 34463.2041 | 32365.4149
QUAD ACSR MOOSE
'A' TYPE TOWER | 14149.6998 | 13645.8114 | 12664.4641 | 16543.8129 | 15939.2541 | 14757.9721 | 18556.5524 | 17870.532 | 16527.5275 | 19767.9245 | 19033.8182 | 17595.4796 | 20980.7275 | 20198.9853 | 18666.3153 | 23003.4286 | 22143.043 | 20454.8697
'B' TYPE TOWER | 20617.6711 | 20048.9989 | 18975.1325 | 23364.7578 | 22649.4998 | 21280.4719 | 25737.7254 | 24911.6351 | 23317.621 | 27178.7446 | 26290.2337 | 24569.5864 | 28625.7473 | 27677.2464 | 25835.1975 | 31041.271 | 29996.9734 | 27961.8924
'C' TYPE TOWER | 25067.6818 | 24450.0721 | 23300.1237 | 28067.9915 | 27275.3928 | 25772.6053 | 30688.8777 | 29766.9223 | 27999.6993 | 32285.6904 | 31292.2837 | 29378.8062 | 33890.3308 | 32829.2143 | 30777.4261 | 36567.8855 | 35400.4552 | 33132.5022
'D' TYPE TOWER | 28328.9599 | 27690.8854 | 26516.5808 | 31440.3486 | 30608.4265 | 29043.2026 | 34181.6958 | 33208.8199 | 31354.0386 | 35855.6961 | 34806.1664 | 32793.3905 | 37538.3838 | 36417.0756 | 34256.5518 | 40343.9363 | 39111.6074 | 36723.575
ABSTRACT OF VOLUMES AND WEIGHTS OF FOUNDATIONS
4% OF BM IN CASE OF 'A' TYPE AND 10% OF BM IN CASE OF OTHERS ASSUMED. REINFORCEMENT AT 4% OF WEIGHT OF CONCRETE ASSUMED.
(FOR 400KV D/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 6.3932 | 6.0604 | 5.2295 | 8.75 | 8.2839 | 7.1182 | 11.0147 | 10.4219 | 8.9379 | 12.5024 | 11.8269 | 10.135 | 14.086 | 13.3227 | 11.4103 | 16.9364 | 16.0155 | 13.7074
b) 1:3:6 Concrete | 0.95898 | 0.90906 | 0.78443 | 1.3125 | 1.2426 | 1.0677 | 1.6522 | 1.5633 | 1.3407 | 1.8754 | 1.774 | 1.5203 | 2.1129 | 1.9984 | 1.7115 | 2.5405 | 2.4023 | 2.0561
c) Reinforcement | 767.1845 | 727.2506 | 627.5407 | 1050.0044 | 994.0695 | 854.1868 | 1321.7604 | 1250.624 | 1072.5461 | 1500.2934 | 1419.2285 | 1216.2045 | 1690.3178 | 1598.7189 | 1369.2318 | 2032.3622 | 1921.8591 | 1644.8938
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 11.5078 | 10.9088 | 9.4131 | 15.7501 | 14.911 | 12.8128 | 19.8264 | 18.7594 | 16.0882 | 22.5044 | 21.2884 | 18.2431 | 25.3548 | 23.9808 | 20.5385 | 30.4854 | 28.8279 | 24.6734
b) 1:3:6 Concrete | 1.7262 | 1.6363 | 1.412 | 2.3625 | 2.2367 | 1.9219 | 2.974 | 2.8139 | 2.4132 | 3.3757 | 3.1933 | 2.7365 | 3.8032 | 3.5971 | 3.0808 | 4.5728 | 4.3242 | 3.701
c) Reinforcement | 1380.9321 | 1309.0512 | 1129.5733 | 1890.008 | 1789.3252 | 1537.5362 | 2379.1687 | 2251.1232 | 1930.583 | 2700.5282 | 2554.6113 | 2189.1681 | 3042.5721 | 2877.694 | 2464.6172 | 3658.252 | 3459.3464 | 2960.8089
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 16.6223 | 15.7571 | 13.5967 | 22.7501 | 21.5382 | 18.5074 | 28.6381 | 27.0969 | 23.2385 | 32.5064 | 30.75 | 26.3511 | 36.6236 | 34.6389 | 29.6667 | 44.0345 | 41.6403 | 35.6394
b) 1:3:6 Concrete | 2.4933 | 2.3636 | 2.0395 | 3.4125 | 3.2307 | 2.7761 | 4.2957 | 4.0645 | 3.4858 | 4.876 | 4.6125 | 3.9527 | 5.4935 | 5.1958 | 4.45 | 6.6052 | 6.246 | 5.3459
c) Reinforcement | 1994.6798 | 1890.8517 | 1631.6059 | 2730.0115 | 2584.5808 | 2220.8856 | 3436.5771 | 3251.6224 | 2788.6199 | 3900.7629 | 3689.9941 | 3162.1318 | 4394.8264 | 4156.6692 | 3560.0026 | 5284.1417 | 4996.8337 | 4276.724
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 12.4201 | 11.9092 | 10.651 | 16.0089 | 15.2853 | 13.4896 | 19.4605 | 18.5432 | 16.2558 | 21.7164 | 20.6761 | 18.0764 | 24.1035 | 22.9353 | 20.0106 | 28.3616 | 26.9687 | 23.4742
b) 1:3:6 Concrete | 1.863 | 1.7864 | 1.5977 | 2.4013 | 2.2928 | 2.0234 | 2.9191 | 2.7815 | 2.4384 | 3.2575 | 3.1014 | 2.7115 | 3.6155 | 3.4403 | 3.0016 | 4.2542 | 4.0453 | 3.5211
c) Reinforcement | 1490.417 | 1429.1016 | 1278.1217 | 1921.0672 | 1834.2382 | 1618.7493 | 2335.2598 | 2225.1887 | 1950.6914 | 2605.9632 | 2481.1362 | 2169.1635 | 2892.4252 | 2752.2365 | 2401.2705 | 3403.3933 | 3236.2397 | 2816.9011
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 22.3563 | 21.4365 | 19.1718 | 28.816 | 27.5136 | 24.2812 | 35.0289 | 33.3778 | 29.2604 | 39.0894 | 37.217 | 32.5375 | 43.3864 | 41.2835 | 36.0191 | 51.0509 | 48.5436 | 42.2535
b) 1:3:6 Concrete | 3.3534 | 3.2155 | 2.8758 | 4.3224 | 4.127 | 3.6422 | 5.2543 | 5.0067 | 4.3891 | 5.8634 | 5.5826 | 4.8806 | 6.508 | 6.1925 | 5.4029 | 7.6576 | 7.2815 | 6.338
c) Reinforcement | 2682.7505 | 2572.3828 | 2300.6191 | 3457.9209 | 3301.6287 | 2913.7487 | 4203.4677 | 4005.3397 | 3511.2445 | 4690.7338 | 4466.0451 | 3904.4943 | 5206.3654 | 4954.0256 | 4322.2869 | 6126.1079 | 5825.2314 | 5070.4219
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 32.2924 | 30.9639 | 27.6926 | 41.6231 | 39.7418 | 35.0729 | 50.5973 | 48.2124 | 42.265 | 56.4625 | 53.758 | 46.9985 | 62.6692 | 59.6318 | 52.0275 | 73.7402 | 70.1185 | 61.0329
b) 1:3:6 Concrete | 4.8439 | 4.6446 | 4.1539 | 6.2435 | 5.9613 | 5.2609 | 7.5896 | 7.2319 | 6.3397 | 8.4694 | 8.0637 | 7.0498 | 9.4004 | 8.9448 | 7.8041 | 11.061 | 10.5178 | 9.1549
c) Reinforcement | 3875.0841 | 3715.664 | 3323.1165 | 4994.7747 | 4769.0193 | 4208.7481 | 6071.6755 | 5785.4907 | 5071.7976 | 6775.5043 | 6450.954 | 5639.825 | 7520.3055 | 7155.8148 | 6243.3034 | 8848.8225 | 8414.2231 | 7323.9427
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 18.2692 | 17.5925 | 15.9385 | 23.0011 | 22.0373 | 19.6549 | 27.5546 | 26.3348 | 23.299 | 30.5223 | 29.1426 | 25.698 | 33.653 | 32.1084 | 28.243 | 39.2096 | 37.3794 | 32.7858
b) 1:3:6 Concrete | 2.7404 | 2.6389 | 2.3908 | 3.4502 | 3.3056 | 2.9482 | 4.1332 | 3.9502 | 3.4949 | 4.5783 | 4.3714 | 3.8547 | 5.0479 | 4.8163 | 4.2365 | 5.8814 | 5.6069 | 4.9179
c) Reinforcement | 2192.3002 | 2111.0943 | 1912.6167 | 2760.1374 | 2644.4806 | 2358.5917 | 3306.5487 | 3160.1792 | 2795.886 | 3662.6769 | 3497.106 | 3083.759 | 4038.3578 | 3853.0098 | 3389.1658 | 4705.147 | 4485.5274 | 3934.2945
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 32.8845 | 31.6664 | 28.6893 | 41.4021 | 39.6672 | 35.3789 | 49.5982 | 47.4027 | 41.9383 | 54.9402 | 52.4566 | 46.2564 | 60.5754 | 57.7951 | 50.8375 | 70.5772 | 67.2829 | 59.0144
b) 1:3:6 Concrete | 4.9327 | 4.75 | 4.3034 | 6.2103 | 5.9501 | 5.3068 | 7.4397 | 7.1104 | 6.2907 | 8.241 | 7.8685 | 6.9385 | 9.0863 | 8.6693 | 7.6256 | 10.5866 | 10.0924 | 8.8522
c) Reinforcement | 3946.1404 | 3799.9698 | 3442.7101 | 4968.2473 | 4760.065 | 4245.465 | 5951.7876 | 5688.3225 | 5032.5948 | 6592.8183 | 6294.7908 | 5550.7663 | 7269.044 | 6935.4176 | 6100.4984 | 8469.2647 | 8073.9494 | 7081.7301
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 47.4998 | 45.7404 | 41.44 | 59.803 | 57.2971 | 51.1028 | 71.6419 | 68.4705 | 60.5775 | 79.358 | 75.7706 | 66.8148 | 87.4978 | 83.4819 | 73.4319 | 101.9449 | 97.1864 | 85.243
b) 1:3:6 Concrete | 7.125 | 6.8611 | 6.216 | 8.9704 | 8.5946 | 7.6654 | 10.7463 | 10.2706 | 9.0866 | 11.9037 | 11.3656 | 10.0222 | 13.1247 | 12.5223 | 11.0148 | 15.2917 | 14.578 | 12.7865
c) Reinforcement | 5699.9806 | 5488.8452 | 4972.8035 | 7176.3572 | 6875.6495 | 6132.3384 | 8597.0266 | 8216.4658 | 7269.3036 | 9522.9598 | 9092.4756 | 8017.7735 | 10499.7302 | 10017.8255 | 8811.8311 | 12233.3823 | 11662.3713 | 10229.1658
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 29.4237 | 28.4214 | 25.9875 | 36.4054 | 34.9707 | 31.4365 | 43.1267 | 41.3136 | 36.8089 | 47.4965 | 45.4502 | 40.3463 | 52.0935 | 49.8092 | 44.0944 | 60.2163 | 57.5245 | 50.7653
b) 1:3:6 Concrete | 4.4136 | 4.2632 | 3.8981 | 5.4608 | 5.2456 | 4.7155 | 6.469 | 6.197 | 5.5213 | 7.1245 | 6.8175 | 6.0519 | 7.814 | 7.4714 | 6.6142 | 9.0324 | 8.6287 | 7.6148
c) Reinforcement | 3530.8447 | 3410.5639 | 3118.5042 | 4368.649 | 4196.4821 | 3772.3842 | 5175.1991 | 4957.6306 | 4417.0723 | 5699.585 | 5454.0193 | 4841.5546 | 6251.2205 | 5977.0988 | 5291.3265 | 7225.9533 | 6902.94 | 6091.8377
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 52.9627 | 51.1585 | 46.7776 | 65.5297 | 62.9472 | 56.5858 | 77.628 | 74.3645 | 66.2561 | 85.4938 | 81.8103 | 72.6233 | 93.7683 | 89.6565 | 79.3699 | 108.3893 | 103.5441 | 91.3776
b) 1:3:6 Concrete | 7.9444 | 7.6738 | 7.0166 | 9.8295 | 9.4421 | 8.4879 | 11.6442 | 11.1547 | 9.9384 | 12.8241 | 12.2715 | 10.8935 | 14.0652 | 13.4485 | 11.9055 | 16.2584 | 15.5316 | 13.7066
c) Reinforcement | 6355.5205 | 6139.015 | 5613.3075 | 7863.5682 | 7553.6678 | 6790.2916 | 9315.3583 | 8923.735 | 7950.7302 | 10259.253 | 9817.2348 | 8714.7983 | 11252.1969 | 10758.7778 | 9524.3878 | 13006.716 | 12425.292 | 10965.3079
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 76.5016 | 73.8956 | 67.5676 | 94.6541 | 90.9238 | 81.735 | 112.1293 | 107.4153 | 95.7032 | 123.491 | 118.1704 | 104.9003 | 135.4431 | 129.5038 | 114.6454 | 156.5623 | 149.5637 | 131.9898
b) 1:3:6 Concrete | 11.4752 | 11.0843 | 10.1351 | 14.1981 | 13.6386 | 12.2602 | 16.8194 | 16.1123 | 14.3555 | 18.5237 | 17.7256 | 15.7351 | 20.3165 | 19.4256 | 17.1968 | 23.4843 | 22.4346 | 19.7985
c) Reinforcement | 9180.1963 | 8867.4662 | 8108.1109 | 11358.4874 | 10910.8534 | 9808.199 | 13455.5176 | 12889.8395 | 11484.388 | 14818.921 | 14180.4502 | 12588.042 | 16253.1733 | 15540.4569 | 13757.449 | 18787.4787 | 17947.6441 | 15838.7781
TRIPPLE ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 9.1398 | 8.6557 | 7.4586 | 12.5053 | 11.8272 | 10.1473 | 15.7397 | 14.8771 | 12.7383 | 17.8646 | 16.8816 | 14.443 | 20.1263 | 19.0156 | 16.259 | 24.1973 | 22.8573 | 19.5304
b) 1:3:6 Concrete | 1.371 | 1.2984 | 1.1188 | 1.8758 | 1.7741 | 1.5221 | 2.3609 | 2.2316 | 1.9107 | 2.6797 | 2.5322 | 2.1665 | 3.0189 | 2.8523 | 2.4389 | 3.6296 | 3.4286 | 2.9296
c) Reinforcement | 1096.7783 | 1038.689 | 895.0295 | 1500.6417 | 1419.2624 | 1217.6754 | 1888.7598 | 1785.2543 | 1528.5929 | 2143.7492 | 2025.7931 | 1733.1637 | 2415.1541 | 2281.8665 | 1951.084 | 2903.6811 | 2742.881 | 2343.6521
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 16.4517 | 15.5803 | 13.4254 | 22.5096 | 21.2889 | 18.2651 | 28.3314 | 26.7788 | 22.9289 | 32.1562 | 30.3869 | 25.9975 | 36.2273 | 34.228 | 29.2663 | 43.5552 | 41.1432 | 35.1548
b) 1:3:6 Concrete | 2.4678 | 2.3371 | 2.0138 | 3.3764 | 3.1933 | 2.7398 | 4.2497 | 4.0168 | 3.4393 | 4.8234 | 4.558 | 3.8996 | 5.4341 | 5.1342 | 4.3899 | 6.5333 | 6.1715 | 5.2732
c) Reinforcement | 1974.2009 | 1869.6402 | 1611.0531 | 2701.155 | 2554.6722 | 2191.8158 | 3399.7676 | 3213.4578 | 2751.4673 | 3858.7486 | 3646.4275 | 3119.6947 | 4347.2773 | 4107.3597 | 3511.9511 | 5226.6259 | 4937.1858 | 4218.5738
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 23.7635 | 22.5049 | 19.3923 | 32.5139 | 30.7507 | 26.383 | 40.9231 | 38.6805 | 33.1195 | 46.4479 | 43.8922 | 37.5519 | 52.3283 | 49.4404 | 42.2735 | 62.9131 | 59.4291 | 50.7791
b) 1:3:6 Concrete | 3.5645 | 3.3757 | 2.9088 | 4.8771 | 4.6126 | 3.9574 | 6.1385 | 5.8021 | 4.9679 | 6.9672 | 6.5838 | 5.6328 | 7.8493 | 7.4161 | 6.341 | 9.437 | 8.9144 | 7.6169
c) Reinforcement | 2851.6236 | 2700.5914 | 2327.0767 | 3901.6683 | 3690.0821 | 3165.9561 | 4910.7754 | 4641.6612 | 3974.3416 | 5573.748 | 5267.062 | 4506.2257 | 6279.4006 | 5932.853 | 5072.8183 | 7549.5708 | 7131.4906 | 6093.4955
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 17.876 | 17.1332 | 15.319 | 23.0255 | 21.9727 | 19.3805 | 27.9815 | 26.6463 | 23.3423 | 31.2214 | 29.7069 | 25.951 | 34.6502 | 32.9492 | 28.7231 | 40.7665 | 38.738 | 33.6878
b) 1:3:6 Concrete | 2.6814 | 2.57 | 2.2978 | 3.4538 | 3.2959 | 2.9071 | 4.1972 | 3.9969 | 3.5013 | 4.6832 | 4.456 | 3.8927 | 5.1975 | 4.9424 | 4.3085 | 6.115 | 5.8107 | 5.0532
c) Reinforcement | 2145.1146 | 2055.9793 | 1838.2787 | 2763.054 | 2636.7209 | 2325.6553 | 3357.7771 | 3197.5563 | 2801.0792 | 3746.5658 | 3564.8329 | 3114.1228 | 4158.0253 | 3953.8999 | 3446.7714 | 4891.9835 | 4648.5581 | 4042.5301
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 32.1767 | 30.8397 | 27.5742 | 41.4458 | 39.5508 | 34.8848 | 50.3667 | 47.9633 | 42.0162 | 56.1985 | 53.4725 | 46.7118 | 62.3704 | 59.3085 | 51.7016 | 73.3798 | 69.7284 | 60.638
b) 1:3:6 Concrete | 4.8265 | 4.626 | 4.1361 | 6.2169 | 5.9326 | 5.2327 | 7.555 | 7.1945 | 6.3024 | 8.4298 | 8.0209 | 7.0068 | 9.3556 | 8.8963 | 7.7552 | 11.007 | 10.4593 | 9.0957
c) Reinforcement | 3861.2063 | 3700.7628 | 3308.9017 | 4973.4972 | 4746.0977 | 4186.1795 | 6043.9988 | 5755.6013 | 5041.9425 | 6743.8185 | 6416.6991 | 5605.4211 | 7484.4455 | 7117.0198 | 6204.1886 | 8805.5704 | 8367.4045 | 7276.5541
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 46.4775 | 44.5462 | 39.8294 | 59.8662 | 57.129 | 50.3892 | 72.7518 | 69.2804 | 60.69 | 81.1756 | 77.238 | 67.4727 | 90.0905 | 85.6678 | 74.68 | 105.993 | 100.7188 | 87.5882
b) 1:3:6 Concrete | 6.9716 | 6.6819 | 5.9744 | 8.9799 | 8.5693 | 7.5584 | 10.9128 | 10.3921 | 9.1035 | 12.1763 | 11.5857 | 10.1209 | 13.5136 | 12.8502 | 11.202 | 15.8989 | 15.1078 | 13.1382
c) Reinforcement | 5577.298 | 5345.5463 | 4779.5247 | 7183.9405 | 6855.4744 | 6046.7038 | 8730.2205 | 8313.6464 | 7282.8058 | 9741.0711 | 9268.5654 | 8096.7194 | 10810.8657 | 10280.1396 | 8961.6058 | 12719.1572 | 12086.251 | 10510.5782
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 26.3605 | 25.3771 | 22.9912 | 33.1679 | 31.7656 | 28.3235 | 39.7247 | 37.9488 | 33.5591 | 43.9997 | 41.9904 | 37.0079 | 48.5102 | 46.2604 | 40.6679 | 56.5166 | 53.8503 | 47.2023
b) 1:3:6 Concrete | 3.9541 | 3.8066 | 3.4487 | 4.9752 | 4.7648 | 4.2485 | 5.9587 | 5.6923 | 5.0339 | 6.6 | 6.2986 | 5.5512 | 7.2765 | 6.9391 | 6.1002 | 8.4775 | 8.0775 | 7.0803
c) Reinforcement | 3163.2659 | 3045.2548 | 2758.944 | 3980.1521 | 3811.8714 | 3398.8175 | 4766.9613 | 4553.8593 | 4027.0934 | 5279.9652 | 5038.845 | 4440.9473 | 5821.2232 | 5551.2487 | 4880.1424 | 6781.9962 | 6462.0301 | 5664.2711
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 47.449 | 45.6788 | 41.3842 | 59.7023 | 57.1781 | 50.9823 | 71.5044 | 68.3079 | 60.4064 | 79.1995 | 75.5827 | 66.6142 | 87.3183 | 83.2687 | 73.2021 | 101.7299 | 96.9305 | 84.9641
b) 1:3:6 Concrete | 7.1173 | 6.8518 | 6.2076 | 8.9553 | 8.5767 | 7.6473 | 10.7257 | 10.2462 | 9.061 | 11.8799 | 11.3374 | 9.9921 | 13.0978 | 12.4903 | 10.9803 | 15.2595 | 14.5396 | 12.7446
c) Reinforcement | 5693.8786 | 5481.4586 | 4966.0991 | 7164.2739 | 6861.3685 | 6117.8715 | 8580.5304 | 8196.9468 | 7248.768 | 9503.9374 | 9069.921 | 7993.7051 | 10478.2018 | 9992.2476 | 8784.2563 | 12207.5932 | 11631.6541 | 10195.6879
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 68.5374 | 65.9805 | 59.7771 | 86.2366 | 82.5905 | 73.641 | 103.2842 | 98.667 | 87.2537 | 114.3992 | 109.175 | 96.2205 | 126.1265 | 120.2771 | 105.7364 | 146.9433 | 140.0107 | 122.7259
b) 1:3:6 Concrete | 10.2806 | 9.8971 | 8.9666 | 12.9355 | 12.3886 | 11.0462 | 15.4926 | 14.8 | 13.0881 | 17.1599 | 16.3762 | 14.4331 | 18.919 | 18.0416 | 15.8605 | 22.0415 | 21.0016 | 18.4089
c) Reinforcement | 8224.4914 | 7917.6624 | 7173.2543 | 10348.3956 | 9910.8657 | 8836.9255 | 12394.0995 | 11840.0343 | 10470.4427 | 13727.9095 | 13100.997 | 11546.463 | 15135.1803 | 14433.2466 | 12688.3702 | 17633.1902 | 16801.2782 | 14727.1048
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 42.5329 | 41.0767 | 37.5645 | 52.5995 | 50.5119 | 45.4019 | 62.3022 | 59.662 | 53.1419 | 68.6136 | 65.6327 | 58.2422 | 75.2547 | 71.9263 | 63.6485 | 86.9916 | 83.0684 | 73.2742
b) 1:3:6 Concrete | 6.3799 | 6.1615 | 5.6347 | 7.8899 | 7.5768 | 6.8103 | 9.3453 | 8.9493 | 7.9713 | 10.292 | 9.8449 | 8.7363 | 11.2882 | 10.7889 | 9.5473 | 13.0487 | 12.4603 | 10.9911
c) Reinforcement | 5103.9467 | 4929.2018 | 4507.7354 | 6311.942 | 6061.4335 | 5448.2232 | 7476.2586 | 7159.4389 | 6377.0298 | 8233.6345 | 7875.9283 | 6989.0616 | 9030.5599 | 8631.1571 | 7637.8185 | 10438.991 | 9968.2133 | 8792.9022
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 76.5592 | 73.938 | 67.616 | 94.6791 | 90.9215 | 81.7233 | 112.1439 | 107.3916 | 95.6554 | 123.5045 | 118.1389 | 104.8359 | 135.4584 | 129.4674 | 114.5673 | 156.5849 | 149.5232 | 131.8935
b) 1:3:6 Concrete | 11.4839 | 11.0907 | 10.1424 | 14.2019 | 13.6382 | 12.2585 | 16.8216 | 16.1087 | 14.3483 | 18.5257 | 17.7208 | 15.7254 | 20.3188 | 19.4201 | 17.1851 | 23.4877 | 22.4285 | 19.784
c) Reinforcement | 9187.104 | 8872.5633 | 8113.9237 | 11361.4956 | 10910.5802 | 9806.8018 | 13457.2654 | 12886.9901 | 11478.6536 | 14820.5421 | 14176.6709 | 12580.3109 | 16255.0078 | 15536.0827 | 13748.0733 | 18790.1839 | 17942.784 | 15827.224
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 110.5855 | 106.7994 | 97.6676 | 136.7587 | 131.3311 | 118.0448 | 161.9856 | 155.1212 | 138.169 | 178.3954 | 170.6451 | 151.4297 | 195.6621 | 187.0084 | 165.4861 | 226.1781 | 215.978 | 190.5129
b) 1:3:6 Concrete | 16.5878 | 16.0199 | 14.6501 | 20.5138 | 19.6997 | 17.7067 | 24.2978 | 23.2682 | 20.7253 | 26.7593 | 25.5968 | 22.7145 | 29.3493 | 28.0513 | 24.8229 | 33.9267 | 32.3967 | 28.5769
c) Reinforcement | 13270.2614 | 12815.9247 | 11720.112 | 16411.0492 | 15759.727 | 14165.3804 | 19438.2723 | 18614.5413 | 16580.2774 | 21407.4497 | 20477.4136 | 18171.5602 | 23479.4558 | 22441.0084 | 19858.3281 | 27141.3767 | 25917.3547 | 22861.5458
QUAD ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 11.8864 | 11.2511 | 9.6877 | 16.2607 | 15.3705 | 13.1764 | 20.4647 | 19.3324 | 16.5387 | 23.2267 | 21.9363 | 18.751 | 26.1666 | 24.7085 | 21.1078 | 31.4583 | 29.6992 | 25.3534
b) 1:3:6 Concrete | 1.783 | 1.6877 | 1.4531 | 2.4391 | 2.3056 | 1.9765 | 3.0697 | 2.8999 | 2.4808 | 3.484 | 3.2904 | 2.8127 | 3.925 | 3.7063 | 3.1662 | 4.7187 | 4.4549 | 3.803
c) Reinforcement | 1426.3721 | 1350.1273 | 1162.5182 | 1951.2789 | 1844.4552 | 1581.1641 | 2455.7591 | 2319.8846 | 1984.6397 | 2787.205 | 2632.3577 | 2250.1229 | 3139.9903 | 2965.0141 | 2532.9362 | 3774.9999 | 3563.9029 | 3042.4104
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 21.3956 | 20.2519 | 17.4378 | 29.2692 | 27.6668 | 23.7175 | 36.8364 | 34.7983 | 29.7696 | 41.8081 | 39.4854 | 33.7518 | 47.0999 | 44.4752 | 37.994 | 56.625 | 53.4585 | 45.6362
b) 1:3:6 Concrete | 3.2093 | 3.0378 | 2.6157 | 4.3904 | 4.15 | 3.5576 | 5.5255 | 5.2197 | 4.4654 | 6.2712 | 5.9228 | 5.0628 | 7.065 | 6.6713 | 5.6991 | 8.4937 | 8.0188 | 6.8454
c) Reinforcement | 2567.4697 | 2430.2292 | 2092.5328 | 3512.302 | 3320.0193 | 2846.0953 | 4420.3664 | 4175.7923 | 3572.3515 | 5016.969 | 4738.2438 | 4050.2212 | 5651.9825 | 5337.0254 | 4559.2851 | 6794.9999 | 6415.0252 | 5476.3386
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 30.9047 | 29.2528 | 25.1879 | 42.2777 | 39.9632 | 34.2586 | 53.2081 | 50.2642 | 43.0005 | 60.3894 | 57.0344 | 48.7527 | 68.0331 | 64.242 | 54.8803 | 81.7917 | 77.2179 | 65.9189
b) 1:3:6 Concrete | 4.6357 | 4.3879 | 3.7782 | 6.3417 | 5.9945 | 5.1388 | 7.9812 | 7.5396 | 6.4501 | 9.0584 | 8.5552 | 7.3129 | 10.205 | 9.6363 | 8.232 | 12.2687 | 11.5827 | 9.8878
c) Reinforcement | 3708.5673 | 3510.3311 | 3022.5474 | 5073.3251 | 4795.5834 | 4111.0266 | 6384.9737 | 6031.7 | 5160.0633 | 7246.733 | 6844.1299 | 5850.3196 | 8163.9747 | 7709.0367 | 6585.6341 | 9814.9998 | 9266.1475 | 7910.2669
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 23.3318 | 22.3571 | 19.987 | 30.042 | 28.66 | 25.2713 | 36.5025 | 34.7494 | 30.4289 | 40.7264 | 38.7377 | 33.8257 | 45.1969 | 42.963 | 37.4356 | 53.1714 | 50.5073 | 43.9013
b) 1:3:6 Concrete | 3.4998 | 3.3536 | 2.998 | 4.5063 | 4.299 | 3.7907 | 5.4754 | 5.2124 | 4.5643 | 6.109 | 5.8107 | 5.0739 | 6.7795 | 6.4445 | 5.6153 | 7.9757 | 7.5761 | 6.5852
c) Reinforcement | 2799.8123 | 2682.8571 | 2398.4358 | 3605.0409 | 3439.2037 | 3032.5613 | 4380.2945 | 4169.9239 | 3651.467 | 4887.1684 | 4648.5296 | 4059.0822 | 5423.6254 | 5155.5633 | 4492.2724 | 6380.5738 | 6060.8765 | 5268.1591
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 41.9972 | 40.2429 | 35.9765 | 54.0756 | 51.5881 | 45.4884 | 65.7044 | 62.5489 | 54.772 | 73.3075 | 69.7279 | 60.8862 | 81.3544 | 77.3334 | 67.3841 | 95.7086 | 90.9131 | 79.0224
b) 1:3:6 Concrete | 6.2996 | 6.0364 | 5.3965 | 8.1113 | 7.7382 | 6.8233 | 9.8557 | 9.3823 | 8.2158 | 10.9961 | 10.4592 | 9.1329 | 12.2032 | 11.6 | 10.1076 | 14.3563 | 13.637 | 11.8534
c) Reinforcement | 5039.6621 | 4829.1428 | 4317.1844 | 6489.0736 | 6190.5666 | 5458.6104 | 7884.53 | 7505.8629 | 6572.6405 | 8796.9031 | 8367.3532 | 7306.348 | 9762.5256 | 9280.0139 | 8086.0902 | 11485.0328 | 10909.5777 | 9482.6863
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 60.6626 | 58.1286 | 51.9661 | 78.1092 | 74.5161 | 65.7055 | 94.9064 | 90.3484 | 79.1151 | 105.8886 | 100.7181 | 87.9468 | 117.5119 | 111.7039 | 97.3326 | 138.2458 | 131.319 | 114.1434
b) 1:3:6 Concrete | 9.0994 | 8.7193 | 7.7949 | 11.7164 | 11.1774 | 9.8558 | 14.236 | 13.5523 | 11.8673 | 15.8833 | 15.1077 | 13.192 | 17.6268 | 16.7556 | 14.5999 | 20.7369 | 19.6978 | 17.1215
c) Reinforcement | 7279.5119 | 6975.4285 | 6235.933 | 9373.1063 | 8941.9296 | 7884.6594 | 11388.7656 | 10841.802 | 9493.8141 | 12706.6379 | 12086.1769 | 10553.6137 | 14101.4259 | 13404.4645 | 11679.9081 | 16589.4919 | 15758.2789 | 13697.2136
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 33.0955 | 31.8441 | 28.8403 | 41.6867 | 39.8983 | 35.5532 | 49.9782 | 47.7101 | 42.1591 | 55.3903 | 52.8223 | 46.5163 | 61.1046 | 58.2275 | 51.1441 | 71.256 | 67.843 | 59.4142
b) 1:3:6 Concrete | 4.9643 | 4.7766 | 4.326 | 6.253 | 5.9847 | 5.333 | 7.4967 | 7.1565 | 6.3239 | 8.3086 | 7.9233 | 6.9774 | 9.1657 | 8.7341 | 7.6716 | 10.6884 | 10.1765 | 8.9121
c) Reinforcement | 3971.4599 | 3821.296 | 3460.8343 | 5002.4056 | 4787.7993 | 4266.3891 | 5997.379 | 5725.2171 | 5059.0967 | 6646.8414 | 6338.6741 | 5581.9536 | 7332.5573 | 6987.2948 | 6137.2886 | 8550.7223 | 8141.1611 | 7129.6988
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 59.5719 | 57.3194 | 51.9125 | 75.0361 | 71.817 | 63.9958 | 89.9607 | 85.8783 | 75.8865 | 99.7026 | 95.0801 | 83.7293 | 109.9884 | 104.8094 | 92.0593 | 128.2608 | 122.1174 | 106.9455
b) 1:3:6 Concrete | 8.9358 | 8.5979 | 7.7869 | 11.2554 | 10.7725 | 9.5994 | 13.4941 | 12.8817 | 11.383 | 14.9554 | 14.262 | 12.5594 | 16.4983 | 15.7214 | 13.8089 | 19.2391 | 18.3176 | 16.0418
c) Reinforcement | 7148.6277 | 6878.3329 | 6229.5017 | 9004.3301 | 8618.0388 | 7679.5005 | 10795.2822 | 10305.3907 | 9106.3741 | 11964.3145 | 11409.6134 | 10047.5165 | 13198.6031 | 12577.1307 | 11047.1195 | 15391.3002 | 14654.09 | 12833.4578
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 86.0483 | 82.7947 | 74.9847 | 108.3855 | 103.7357 | 92.4384 | 129.9432 | 124.0464 | 109.6138 | 144.0149 | 137.3379 | 120.9423 | 158.8721 | 151.3914 | 132.9746 | 185.2657 | 176.3918 | 154.4768
b) 1:3:6 Concrete | 12.9072 | 12.4192 | 11.2477 | 16.2578 | 15.5603 | 13.8658 | 19.4915 | 18.607 | 16.4421 | 21.6022 | 20.6007 | 18.1413 | 23.8308 | 22.7087 | 19.9462 | 27.7898 | 26.4588 | 23.1715
c) Reinforcement | 10325.7956 | 9935.3697 | 8998.1691 | 13006.2546 | 12448.2783 | 11092.6118 | 15593.1854 | 14885.5644 | 13153.6514 | 17281.7876 | 16480.5527 | 14513.0794 | 19064.649 | 18166.9666 | 15956.9504 | 22231.8781 | 21167.0188 | 18537.2168
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 55.6421 | 53.732 | 49.1414 | 68.7936 | 66.0532 | 59.3672 | 81.4777 | 78.0104 | 69.4749 | 89.7307 | 85.8153 | 76.1381 | 98.4158 | 94.0435 | 83.2026 | 113.7669 | 108.6124 | 95.7831
b) 1:3:6 Concrete | 8.3463 | 8.0598 | 7.3712 | 10.319 | 9.908 | 8.9051 | 12.2216 | 11.7016 | 10.4212 | 13.4596 | 12.8723 | 11.4207 | 14.7624 | 14.1065 | 12.4804 | 17.065 | 16.2919 | 14.3675
c) Reinforcement | 6677.0487 | 6447.8397 | 5896.9666 | 8255.235 | 7926.3849 | 7124.0623 | 9777.318 | 9361.2473 | 8336.9872 | 10767.684 | 10297.8373 | 9136.5686 | 11809.8993 | 11285.2154 | 9984.3104 | 13652.0287 | 13033.4866 | 11493.9667
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 100.1557 | 96.7176 | 88.4545 | 123.8285 | 118.8958 | 106.8609 | 146.6598 | 140.4187 | 125.0548 | 161.5153 | 154.4676 | 137.0485 | 177.1485 | 169.2782 | 149.7647 | 204.7804 | 195.5023 | 172.4095
b) 1:3:6 Concrete | 15.0234 | 14.5076 | 13.2682 | 18.5743 | 17.8344 | 16.0291 | 21.999 | 21.0628 | 18.7582 | 24.2273 | 23.1701 | 20.5573 | 26.5723 | 25.3917 | 22.4647 | 30.7171 | 29.3253 | 25.8614
c) Reinforcement | 12018.6876 | 11606.1115 | 10614.5398 | 14859.4229 | 14267.4927 | 12823.3121 | 17599.1725 | 16850.2452 | 15006.577 | 19381.8312 | 18536.1071 | 16445.8235 | 21257.8188 | 20313.3877 | 17971.7588 | 24573.6517 | 23460.276 | 20689.1401
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 144.6694 | 139.7032 | 127.7676 | 178.8634 | 171.7383 | 154.3547 | 211.8419 | 202.827 | 180.6347 | 233.2998 | 223.1198 | 197.959 | 255.8812 | 244.513 | 216.3267 | 295.794 | 282.3922 | 249.0359
b) 1:3:6 Concrete | 21.7004 | 20.9555 | 19.1651 | 26.8295 | 25.7608 | 23.1532 | 31.7763 | 30.4241 | 27.0952 | 34.995 | 33.468 | 29.6938 | 38.3822 | 36.6769 | 32.449 | 44.3691 | 42.3588 | 37.3554
c) Reinforcement | 17360.3265 | 16764.3833 | 15332.1131 | 21463.6109 | 20608.6006 | 18522.5619 | 25421.0269 | 24339.2431 | 21676.1667 | 27995.9784 | 26774.3769 | 23755.0785 | 30705.7382 | 29341.56 | 25959.2072 | 35495.2747 | 33887.0653 | 29884.3134
(FOR 400KV S/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 2.3474 | 2.1822 | 1.8647 | 3.2076 | 2.9761 | 2.5302 | 4.0345 | 3.7399 | 3.1719 | 4.5779 | 4.2421 | 3.5943 | 5.1563 | 4.7768 | 4.0444 | 6.1975 | 5.7396 | 4.8555
b) 1:3:6 Concrete | 0.3521 | 0.32733 | 0.27971 | 0.48114 | 0.44641 | 0.37953 | 0.60518 | 0.56098 | 0.47579 | 0.68668 | 0.63631 | 0.53915 | 0.77344 | 0.71652 | 0.60666 | 0.92963 | 0.86094 | 0.72832
c) Reinforcement | 281.6831 | 261.865 | 223.7649 | 384.9101 | 357.1265 | 303.6232 | 484.1405 | 448.7879 | 380.629 | 549.3446 | 509.0493 | 431.318 | 618.7533 | 573.2148 | 485.3297 | 743.701 | 688.7555 | 582.6573
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 4.2252 | 3.928 | 3.3565 | 5.7737 | 5.3569 | 4.5543 | 7.2621 | 6.7318 | 5.7094 | 8.2402 | 7.6357 | 6.4698 | 9.2813 | 8.5982 | 7.2799 | 11.1555 | 10.3313 | 8.7399
b) 1:3:6 Concrete | 0.63379 | 0.5892 | 0.50347 | 0.86605 | 0.80353 | 0.68315 | 1.0893 | 1.0098 | 0.85642 | 1.236 | 1.1454 | 0.97047 | 1.3922 | 1.2897 | 1.092 | 1.6733 | 1.5497 | 1.311
c) Reinforcement | 507.0297 | 471.357 | 402.7767 | 692.8382 | 642.8278 | 546.5218 | 871.4528 | 807.8182 | 685.1323 | 988.8204 | 916.2888 | 776.3723 | 1113.756 | 1031.7866 | 873.5935 | 1338.6618 | 1239.7599 | 1048.7831
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 6.1031 | 5.6737 | 4.8482 | 8.3397 | 7.7377 | 6.5785 | 10.4897 | 9.7237 | 8.247 | 11.9025 | 11.0294 | 9.3452 | 13.4063 | 12.4197 | 10.5155 | 16.1135 | 14.923 | 12.6242
b) 1:3:6 Concrete | 0.91547 | 0.85106 | 0.72724 | 1.251 | 1.1607 | 0.98678 | 1.5735 | 1.4586 | 1.237 | 1.7854 | 1.6544 | 1.4018 | 2.0109 | 1.8629 | 1.5773 | 2.417 | 2.2385 | 1.8936
c) Reinforcement | 732.3762 | 680.849 | 581.7886 | 1000.7662 | 928.529 | 789.4204 | 1258.7652 | 1166.8486 | 989.6355 | 1428.2961 | 1323.5282 | 1121.4267 | 1608.7586 | 1490.3584 | 1261.8573 | 1933.6226 | 1790.7643 | 1514.9089
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 4.6423 | 4.3886 | 3.9103 | 5.9543 | 5.5935 | 4.9075 | 7.2187 | 6.7602 | 5.8835 | 8.046 | 7.5254 | 6.5275 | 8.9219 | 8.3368 | 7.2128 | 10.4851 | 9.7869 | 8.4419
b) 1:3:6 Concrete | 0.69634 | 0.65829 | 0.58655 | 0.89314 | 0.83902 | 0.73612 | 1.0828 | 1.014 | 0.88252 | 1.2069 | 1.1288 | 0.97913 | 1.3383 | 1.2505 | 1.0819 | 1.5728 | 1.468 | 1.2663
c) Reinforcement | 557.0746 | 526.628 | 469.2361 | 714.5135 | 671.2154 | 588.8992 | 866.2465 | 811.2214 | 706.0175 | 965.5189 | 903.0509 | 783.3011 | 1070.6301 | 1000.4183 | 865.5365 | 1258.2175 | 1174.4266 | 1013.0308
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 8.3561 | 7.8994 | 7.0385 | 10.7177 | 10.0682 | 8.8335 | 12.9937 | 12.1683 | 10.5903 | 14.4828 | 13.5458 | 11.7495 | 16.0595 | 15.0063 | 12.983 | 18.8733 | 17.6164 | 15.1955
b) 1:3:6 Concrete | 1.2534 | 1.1849 | 1.0558 | 1.6077 | 1.5102 | 1.325 | 1.9491 | 1.8252 | 1.5885 | 2.1724 | 2.0319 | 1.7624 | 2.4089 | 2.2509 | 1.9475 | 2.831 | 2.6425 | 2.2793
c) Reinforcement | 1002.7344 | 947.9305 | 844.6251 | 1286.1244 | 1208.1877 | 1060.0186 | 1559.2436 | 1460.1986 | 1270.8315 | 1737.934 | 1625.4915 | 1409.9419 | 1927.1341 | 1800.7529 | 1557.9657 | 2264.7914 | 2113.9678 | 1823.4555
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 12.07 | 11.4103 | 10.1668 | 15.4811 | 14.543 | 12.7595 | 18.7687 | 17.5765 | 15.297 | 20.9196 | 19.5661 | 16.9715 | 23.197 | 21.6757 | 18.7533 | 27.2614 | 25.4459 | 21.949
b) 1:3:6 Concrete | 1.8105 | 1.7115 | 1.525 | 2.3222 | 2.1815 | 1.9139 | 2.8153 | 2.6365 | 2.2946 | 3.1379 | 2.9349 | 2.5457 | 3.4795 | 3.2514 | 2.813 | 4.0892 | 3.8169 | 3.2924
c) Reinforcement | 1448.3941 | 1369.2329 | 1220.014 | 1857.7352 | 1745.1601 | 1531.1379 | 2252.2408 | 2109.1758 | 1835.6455 | 2510.3491 | 2347.9322 | 2036.5828 | 2783.6381 | 2601.0876 | 2250.3949 | 3271.3654 | 3053.5091 | 2633.8801
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 6.8738 | 6.5377 | 5.9107 | 8.6052 | 8.1237 | 7.2142 | 10.2762 | 9.6646 | 8.5003 | 11.3669 | 10.674 | 9.3501 | 12.5185 | 11.7419 | 10.2536 | 14.564 | 13.6426 | 11.8701
b) 1:3:6 Concrete | 1.0311 | 0.98065 | 0.88661 | 1.2908 | 1.2185 | 1.0821 | 1.5414 | 1.4497 | 1.275 | 1.705 | 1.6011 | 1.4025 | 1.8778 | 1.7613 | 1.538 | 2.1846 | 2.0464 | 1.7805
c) Reinforcement | 824.8574 | 784.5218 | 709.2866 | 1032.6294 | 974.8391 | 865.7037 | 1233.1453 | 1159.7504 | 1020.0333 | 1364.0318 | 1280.8816 | 1122.0063 | 1502.2199 | 1409.0284 | 1230.4325 | 1747.6825 | 1637.1111 | 1424.4143
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 12.3729 | 11.7678 | 10.6393 | 15.4894 | 14.6226 | 12.9856 | 18.4972 | 17.3963 | 15.3005 | 20.4605 | 19.2132 | 16.8301 | 22.5333 | 21.1354 | 18.4565 | 26.2152 | 24.5567 | 21.3662
b) 1:3:6 Concrete | 1.8559 | 1.7652 | 1.5959 | 2.3234 | 2.1934 | 1.9478 | 2.7746 | 2.6094 | 2.2951 | 3.0691 | 2.882 | 2.5245 | 3.38 | 3.1703 | 2.7685 | 3.9323 | 3.6835 | 3.2049
c) Reinforcement | 1484.7432 | 1412.1393 | 1276.7158 | 1858.7329 | 1754.7104 | 1558.2667 | 2219.6616 | 2087.5507 | 1836.06 | 2455.2573 | 2305.5869 | 2019.6113 | 2703.9959 | 2536.2511 | 2214.7785 | 3145.8286 | 2946.7999 | 2563.9458
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 17.8719 | 16.998 | 15.3679 | 22.3736 | 21.1215 | 18.7569 | 26.7181 | 25.1279 | 22.1007 | 29.554 | 27.7524 | 24.3101 | 32.5481 | 30.5289 | 26.6594 | 37.8665 | 35.4707 | 30.8623
b) 1:3:6 Concrete | 2.6808 | 2.5497 | 2.3052 | 3.356 | 3.1682 | 2.8135 | 4.0077 | 3.7692 | 3.3151 | 4.4331 | 4.1629 | 3.6465 | 4.8822 | 4.5793 | 3.9989 | 5.68 | 5.3206 | 4.6293
c) Reinforcement | 2144.6291 | 2039.7568 | 1844.145 | 2684.8364 | 2534.5817 | 2250.8296 | 3206.1778 | 3015.351 | 2652.0866 | 3546.4828 | 3330.2922 | 2917.2163 | 3905.7718 | 3663.4738 | 3199.1245 | 4543.9746 | 4256.4888 | 3703.4773
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 11.1237 | 10.6257 | 9.7055 | 13.6803 | 12.9621 | 11.6138 | 16.1506 | 15.239 | 13.5103 | 17.7597 | 16.7289 | 14.7648 | 19.4544 | 18.3019 | 16.0979 | 22.4519 | 21.0915 | 18.4775
b) 1:3:6 Concrete | 1.6686 | 1.5939 | 1.4558 | 2.052 | 1.9443 | 1.7421 | 2.4226 | 2.2858 | 2.0265 | 2.664 | 2.5093 | 2.2147 | 2.9182 | 2.7453 | 2.4147 | 3.3678 | 3.1637 | 2.7716
c) Reinforcement | 1334.8478 | 1275.0878 | 1164.6564 | 1641.6356 | 1555.4579 | 1393.6577 | 1938.0665 | 1828.6799 | 1621.233 | 2131.1675 | 2007.4643 | 1771.7785 | 2334.5235 | 2196.2258 | 1931.7462 | 2694.2312 | 2530.9755 | 2217.3034
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 20.0227 | 19.1263 | 17.4698 | 24.6245 | 23.3319 | 20.9049 | 29.071 | 27.4302 | 24.3185 | 31.9675 | 30.112 | 26.5767 | 35.0179 | 32.9434 | 28.9762 | 40.4135 | 37.9646 | 33.2596
b) 1:3:6 Concrete | 3.0034 | 2.8689 | 2.6205 | 3.6937 | 3.4998 | 3.1357 | 4.3606 | 4.1145 | 3.6478 | 4.7951 | 4.5168 | 3.9865 | 5.2527 | 4.9415 | 4.3464 | 6.062 | 5.6947 | 4.9889
c) Reinforcement | 2402.7261 | 2295.158 | 2096.3814 | 2954.944 | 2799.8242 | 2508.5839 | 3488.5197 | 3291.6239 | 2918.2194 | 3836.1016 | 3613.4358 | 3189.2013 | 4202.1423 | 3953.2065 | 3477.1432 | 4849.6162 | 4555.7558 | 3991.1461
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 28.9217 | 27.6269 | 25.2342 | 35.5688 | 33.7016 | 30.1959 | 41.9914 | 39.6214 | 35.1267 | 46.1753 | 43.4951 | 38.3885 | 50.5813 | 47.5849 | 41.8545 | 58.375 | 54.8378 | 48.0416
b) 1:3:6 Concrete | 4.3383 | 4.144 | 3.7851 | 5.3353 | 5.0552 | 4.5294 | 6.2987 | 5.9432 | 5.269 | 6.9263 | 6.5243 | 5.7583 | 7.5872 | 7.1377 | 6.2782 | 8.7563 | 8.2257 | 7.2062
c) Reinforcement | 3470.6043 | 3315.2283 | 3028.1065 | 4268.2525 | 4044.1905 | 3623.5101 | 5038.9728 | 4754.5678 | 4215.2058 | 5541.0356 | 5219.4072 | 4606.6241 | 6069.7611 | 5710.1872 | 5022.5401 | 7005.0011 | 6580.5362 | 5764.9888
TRIPPLE ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 3.2752 | 3.0393 | 2.5934 | 4.474 | 4.1431 | 3.5167 | 5.6267 | 5.2056 | 4.4075 | 6.3843 | 5.9042 | 4.9939 | 7.1907 | 6.6482 | 5.6188 | 8.6424 | 7.9878 | 6.745
b) 1:3:6 Concrete | 0.49128 | 0.45589 | 0.38901 | 0.67111 | 0.62147 | 0.52751 | 0.84401 | 0.78084 | 0.66112 | 0.95764 | 0.88564 | 0.74908 | 1.0786 | 0.99722 | 0.84282 | 1.2964 | 1.1982 | 1.0118
c) Reinforcement | 393.0254 | 364.7105 | 311.2048 | 536.8844 | 497.1771 | 422.0098 | 675.2095 | 624.676 | 528.8966 | 766.1127 | 708.5094 | 599.2678 | 862.882 | 797.7796 | 674.2592 | 1037.0894 | 958.5333 | 809.4028
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 5.8954 | 5.4707 | 4.6681 | 8.0533 | 7.4577 | 6.3301 | 10.1281 | 9.3701 | 7.9334 | 11.4917 | 10.6276 | 8.989 | 12.9432 | 11.9667 | 10.1139 | 15.5563 | 14.378 | 12.141
b) 1:3:6 Concrete | 0.88431 | 0.8206 | 0.70021 | 1.208 | 1.1186 | 0.94952 | 1.5192 | 1.4055 | 1.19 | 1.7238 | 1.5941 | 1.3484 | 1.9415 | 1.795 | 1.5171 | 2.3335 | 2.1567 | 1.8212
c) Reinforcement | 707.4457 | 656.4788 | 560.1686 | 966.3919 | 894.9187 | 759.6177 | 1215.3772 | 1124.4167 | 952.014 | 1379.0028 | 1275.317 | 1078.682 | 1553.1877 | 1436.0034 | 1213.6666 | 1866.761 | 1725.3599 | 1456.9251
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 8.5156 | 7.9021 | 6.7428 | 11.6325 | 10.7722 | 9.1435 | 14.6295 | 13.5346 | 11.4594 | 16.5991 | 15.351 | 12.9841 | 18.6958 | 17.2852 | 14.609 | 22.4703 | 20.7682 | 17.5371
b) 1:3:6 Concrete | 1.2773 | 1.1853 | 1.0114 | 1.7449 | 1.6158 | 1.3715 | 2.1944 | 2.0302 | 1.7189 | 2.4899 | 2.3027 | 1.9476 | 2.8044 | 2.5928 | 2.1913 | 3.3705 | 3.1152 | 2.6306
c) Reinforcement | 1021.866 | 948.2472 | 809.1325 | 1395.8994 | 1292.6604 | 1097.2255 | 1755.5448 | 1624.1575 | 1375.1313 | 1991.893 | 1842.1245 | 1558.0962 | 2243.4933 | 2074.2271 | 1753.074 | 2696.4326 | 2492.1865 | 2104.4474
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 6.5139 | 6.1524 | 5.4812 | 8.3483 | 7.8335 | 6.869 | 10.1185 | 9.4637 | 8.2296 | 11.2773 | 10.5336 | 9.1283 | 12.5046 | 11.6685 | 10.085 | 14.6954 | 13.6972 | 11.8016
b) 1:3:6 Concrete | 0.97708 | 0.92285 | 0.82218 | 1.2523 | 1.175 | 1.0303 | 1.5178 | 1.4196 | 1.2344 | 1.6916 | 1.58 | 1.3692 | 1.8757 | 1.7503 | 1.5127 | 2.2043 | 2.0546 | 1.7702
c) Reinforcement | 781.6643 | 738.2834 | 657.7474 | 1001.8014 | 940.017 | 824.2777 | 1214.2252 | 1135.6413 | 987.5547 | 1353.2818 | 1264.0358 | 1095.3934 | 1500.5561 | 1400.2187 | 1210.1969 | 1763.4473 | 1643.6638 | 1416.1949
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 11.725 | 11.0743 | 9.8662 | 15.027 | 14.1003 | 12.3642 | 18.2134 | 17.0346 | 14.8133 | 20.2992 | 18.9605 | 16.4309 | 22.5083 | 21.0033 | 18.153 | 26.4517 | 24.655 | 21.2429
b) 1:3:6 Concrete | 1.7587 | 1.6611 | 1.4799 | 2.2541 | 2.115 | 1.8546 | 2.732 | 2.5552 | 2.222 | 3.0449 | 2.8441 | 2.4646 | 3.3763 | 3.1505 | 2.7229 | 3.9678 | 3.6982 | 3.1864
c) Reinforcement | 1406.9957 | 1328.91 | 1183.9453 | 1803.2424 | 1692.0306 | 1483.6998 | 2185.6054 | 2044.1543 | 1777.5984 | 2435.9072 | 2275.2644 | 1971.7082 | 2701.001 | 2520.3936 | 2178.3544 | 3174.2051 | 2958.5949 | 2549.1507
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 16.9361 | 15.9961 | 14.2512 | 21.7057 | 20.367 | 17.8593 | 26.3082 | 24.6056 | 21.397 | 29.3211 | 27.3874 | 23.7335 | 32.512 | 30.3381 | 26.2209 | 38.208 | 35.6127 | 30.6842
b) 1:3:6 Concrete | 2.5404 | 2.3994 | 2.1377 | 3.2559 | 3.0551 | 2.6789 | 3.9462 | 3.6908 | 3.2096 | 4.3982 | 4.1081 | 3.56 | 4.8768 | 4.5507 | 3.9331 | 5.7312 | 5.3419 | 4.6026
c) Reinforcement | 2032.3272 | 1919.5367 | 1710.1432 | 2604.6835 | 2444.0442 | 2143.1219 | 3156.9856 | 2952.6673 | 2567.6421 | 3518.5327 | 3286.493 | 2848.023 | 3901.4459 | 3640.5685 | 3146.5119 | 4584.9629 | 4273.5259 | 3682.1066
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 9.6649 | 9.1867 | 8.3073 | 12.0901 | 11.4035 | 10.1242 | 14.4348 | 13.5617 | 11.9214 | 15.9665 | 14.9768 | 13.1103 | 17.5843 | 16.4747 | 14.3754 | 20.459 | 19.1418 | 16.6401
b) 1:3:6 Concrete | 1.4497 | 1.378 | 1.2461 | 1.8135 | 1.7105 | 1.5186 | 2.1652 | 2.0343 | 1.7882 | 2.395 | 2.2465 | 1.9665 | 2.6376 | 2.4712 | 2.1563 | 3.0688 | 2.8713 | 2.496
c) Reinforcement | 1159.7894 | 1102.4018 | 996.871 | 1450.8159 | 1368.418 | 1214.9054 | 1732.1748 | 1627.404 | 1430.5622 | 1915.9787 | 1797.222 | 1573.2364 | 2110.1145 | 1976.9638 | 1725.0439 | 2455.0779 | 2297.0197 | 1996.8154
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 17.3968 | 16.536 | 14.9531 | 21.7622 | 20.5263 | 18.2236 | 25.9826 | 24.4111 | 21.4584 | 28.7397 | 26.9583 | 23.5985 | 31.6517 | 29.6545 | 25.8757 | 36.8262 | 34.4553 | 29.9522
b) 1:3:6 Concrete | 2.6095 | 2.4804 | 2.243 | 3.2643 | 3.0789 | 2.7335 | 3.8974 | 3.6617 | 3.2188 | 4.311 | 4.0437 | 3.5398 | 4.7478 | 4.4482 | 3.8813 | 5.5239 | 5.1683 | 4.4928
c) Reinforcement | 2087.6209 | 1984.3232 | 1794.3678 | 2611.4686 | 2463.1523 | 2186.8297 | 3117.9147 | 2929.3273 | 2575.012 | 3448.7617 | 3234.9995 | 2831.8254 | 3798.2061 | 3558.5349 | 3105.0791 | 4419.1403 | 4134.6355 | 3594.2677
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 25.1288 | 23.8854 | 21.5989 | 31.4343 | 29.6491 | 26.3229 | 37.5305 | 35.2604 | 30.9955 | 41.5129 | 38.9398 | 34.0868 | 45.7191 | 42.8342 | 37.376 | 53.1934 | 49.7688 | 43.2643
b) 1:3:6 Concrete | 3.7693 | 3.5828 | 3.2398 | 4.7152 | 4.4474 | 3.9484 | 5.6296 | 5.2891 | 4.6493 | 6.2269 | 5.841 | 5.113 | 6.8579 | 6.4251 | 5.6064 | 7.979 | 7.4653 | 6.4896
c) Reinforcement | 3015.4524 | 2866.2447 | 2591.8646 | 3772.1213 | 3557.8867 | 3158.754 | 4503.6546 | 4231.2505 | 3719.4617 | 4981.5447 | 4672.7771 | 4090.4145 | 5486.2977 | 5140.106 | 4485.1143 | 6383.2026 | 5972.2512 | 5191.72
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 15.6636 | 14.9559 | 13.6656 | 19.2501 | 18.2269 | 16.3296 | 22.7233 | 21.4225 | 18.9851 | 24.9881 | 23.5162 | 20.7446 | 27.3744 | 25.7281 | 22.6158 | 31.5976 | 29.653 | 25.959
b) 1:3:6 Concrete | 2.3495 | 2.2434 | 2.0498 | 2.8875 | 2.734 | 2.4494 | 3.4085 | 3.2134 | 2.8478 | 3.7482 | 3.5274 | 3.1117 | 4.1062 | 3.8592 | 3.3924 | 4.7396 | 4.448 | 3.8938
c) Reinforcement | 1879.6294 | 1794.7136 | 1639.8719 | 2310.0143 | 2187.2265 | 1959.5505 | 2726.7913 | 2570.7046 | 2278.2156 | 2998.5679 | 2821.9406 | 2489.3508 | 3284.9314 | 3087.3681 | 2713.8968 | 3791.7177 | 3558.3613 | 3115.074
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 28.1944 | 26.9207 | 24.5981 | 34.6502 | 32.8084 | 29.3933 | 40.9019 | 38.5606 | 34.1732 | 44.9785 | 42.3291 | 37.3403 | 49.274 | 46.3105 | 40.7085 | 56.8758 | 53.3754 | 46.7261
b) 1:3:6 Concrete | 4.2292 | 4.0381 | 3.6897 | 5.1975 | 4.9213 | 4.409 | 6.1353 | 5.7841 | 5.126 | 6.7468 | 6.3494 | 5.601 | 7.3911 | 6.9466 | 6.1063 | 8.5314 | 8.0063 | 7.0089
c) Reinforcement | 3383.3329 | 3230.4845 | 2951.7695 | 4158.0258 | 3937.0076 | 3527.1909 | 4908.2243 | 4627.2683 | 4100.7881 | 5397.4223 | 5079.4931 | 4480.8315 | 5912.8765 | 5557.2626 | 4885.0142 | 6825.0919 | 6405.0504 | 5607.1332
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 40.7253 | 38.8855 | 35.5306 | 50.0503 | 47.3899 | 42.4569 | 59.0805 | 55.6986 | 49.3613 | 64.969 | 61.142 | 53.9359 | 71.1735 | 66.893 | 58.8011 | 82.1539 | 77.0978 | 67.4933
b) 1:3:6 Concrete | 6.1088 | 5.8328 | 5.3296 | 7.5075 | 7.1085 | 6.3685 | 8.8621 | 8.3548 | 7.4042 | 9.7453 | 9.1713 | 8.0904 | 10.676 | 10.0339 | 8.8202 | 12.3231 | 11.5647 | 10.124
c) Reinforcement | 4887.0365 | 4666.2554 | 4263.667 | 6006.0372 | 5686.7888 | 5094.8313 | 7089.6573 | 6683.832 | 5923.3605 | 7796.2766 | 7337.0456 | 6472.3121 | 8540.8217 | 8027.1571 | 7056.1316 | 9858.4661 | 9251.7394 | 8099.1924
QUAD ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 4.2031 | 3.8963 | 3.322 | 5.7405 | 5.3102 | 4.5033 | 7.219 | 6.6714 | 5.643 | 8.1907 | 7.5664 | 6.3935 | 9.2251 | 8.5195 | 7.1932 | 11.0873 | 10.2359 | 8.6346
b) 1:3:6 Concrete | 0.63046 | 0.58444 | 0.49831 | 0.86107 | 0.79653 | 0.6755 | 1.0828 | 1.0007 | 0.84646 | 1.2286 | 1.135 | 0.95902 | 1.3838 | 1.2779 | 1.079 | 1.6631 | 1.5354 | 1.2952
c) Reinforcement | 504.3676 | 467.5559 | 398.6447 | 688.8587 | 637.2276 | 540.3964 | 866.2786 | 800.564 | 677.1643 | 982.8807 | 907.9695 | 767.2176 | 1107.0108 | 1022.3445 | 863.1888 | 1330.4779 | 1228.311 | 1036.1484
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 7.5655 | 7.0133 | 5.9797 | 10.3329 | 9.5584 | 8.1059 | 12.9942 | 12.0085 | 10.1575 | 14.7432 | 13.6195 | 11.5083 | 16.6052 | 15.3352 | 12.9478 | 19.9572 | 18.4247 | 15.5422
b) 1:3:6 Concrete | 1.1348 | 1.052 | 0.89695 | 1.5499 | 1.4338 | 1.2159 | 1.9491 | 1.8013 | 1.5236 | 2.2115 | 2.0429 | 1.7262 | 2.4908 | 2.3003 | 1.9422 | 2.9936 | 2.7637 | 2.3313
c) Reinforcement | 907.8617 | 841.6007 | 717.5605 | 1239.9457 | 1147.0096 | 972.7135 | 1559.3015 | 1441.0152 | 1218.8957 | 1769.1853 | 1634.3452 | 1380.9917 | 1992.6194 | 1840.2201 | 1553.7398 | 2394.8602 | 2210.9598 | 1865.0671
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 10.928 | 10.1304 | 8.6373 | 14.9253 | 13.8066 | 11.7086 | 18.7694 | 17.3456 | 14.6719 | 21.2957 | 19.6727 | 16.623 | 23.9852 | 22.1508 | 18.7024 | 28.827 | 26.6134 | 22.4499
b) 1:3:6 Concrete | 1.6392 | 1.5196 | 1.2956 | 2.2388 | 2.071 | 1.7563 | 2.8154 | 2.6018 | 2.2008 | 3.1944 | 2.9509 | 2.4935 | 3.5978 | 3.3226 | 2.8054 | 4.3241 | 3.992 | 3.3675
c) Reinforcement | 1311.3558 | 1215.6454 | 1036.4763 | 1791.0326 | 1656.7917 | 1405.0306 | 2252.3244 | 2081.4664 | 1760.6271 | 2555.4899 | 2360.7208 | 1994.7657 | 2878.228 | 2658.0957 | 2244.2908 | 3459.2425 | 3193.6086 | 2693.9858
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 8.3854 | 7.9162 | 7.0522 | 10.7424 | 10.0735 | 8.8305 | 13.0184 | 12.1672 | 10.5758 | 14.5087 | 13.5418 | 11.729 | 16.0874 | 15.0002 | 12.9571 | 18.9056 | 17.6075 | 15.1613
b) 1:3:6 Concrete | 1.2578 | 1.1874 | 1.0578 | 1.6114 | 1.511 | 1.3246 | 1.9528 | 1.8251 | 1.5864 | 2.1763 | 2.0313 | 1.7594 | 2.4131 | 2.25 | 1.9436 | 2.8358 | 2.6411 | 2.2742
c) Reinforcement | 1006.254 | 949.9387 | 846.2586 | 1289.0892 | 1208.8186 | 1059.6561 | 1562.204 | 1460.0611 | 1269.0918 | 1741.0447 | 1625.0207 | 1407.4858 | 1930.4822 | 1800.019 | 1554.8573 | 2268.6771 | 2112.9011 | 1819.3589
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 15.0938 | 14.2491 | 12.6939 | 19.3363 | 18.1323 | 15.8948 | 23.4331 | 21.9009 | 19.0364 | 26.1157 | 24.3753 | 21.1123 | 28.9572 | 27.0003 | 23.3229 | 34.0302 | 31.6935 | 27.2904
b) 1:3:6 Concrete | 2.2641 | 2.1374 | 1.9041 | 2.9005 | 2.7198 | 2.3842 | 3.515 | 3.2851 | 2.8555 | 3.9174 | 3.6563 | 3.1668 | 4.3436 | 4.05 | 3.4984 | 5.1045 | 4.754 | 4.0936
c) Reinforcement | 1811.2571 | 1709.8896 | 1523.2655 | 2320.3605 | 2175.8734 | 1907.381 | 2811.9673 | 2628.11 | 2284.3653 | 3133.8805 | 2925.0373 | 2533.4745 | 3474.868 | 3240.0343 | 2798.7432 | 4083.6187 | 3803.222 | 3274.846
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 21.8022 | 20.582 | 18.3356 | 27.9303 | 26.1911 | 22.9592 | 33.8478 | 31.6347 | 27.497 | 37.7226 | 35.2088 | 30.4955 | 41.8271 | 39.0004 | 33.6886 | 49.1547 | 45.7795 | 39.4194
b) 1:3:6 Concrete | 3.2703 | 3.0873 | 2.7503 | 4.1895 | 3.9287 | 3.4439 | 5.0772 | 4.7452 | 4.1245 | 5.6584 | 5.2813 | 4.5743 | 6.2741 | 5.8501 | 5.0533 | 7.3732 | 6.8669 | 5.9129
c) Reinforcement | 2616.2603 | 2469.8405 | 2200.2724 | 3351.6318 | 3142.9283 | 2755.1059 | 4061.7305 | 3796.1589 | 3299.6387 | 4526.7163 | 4225.0539 | 3659.4631 | 5019.2537 | 4680.0495 | 4042.629 | 5898.5604 | 5493.5428 | 4730.3331
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 12.456 | 11.8357 | 10.7038 | 15.575 | 14.6833 | 13.0342 | 18.5934 | 17.4588 | 15.3424 | 20.566 | 19.2797 | 16.8706 | 22.6501 | 21.2075 | 18.4971 | 26.3539 | 24.6411 | 21.4101
b) 1:3:6 Concrete | 1.8684 | 1.7754 | 1.6056 | 2.3363 | 2.2025 | 1.9551 | 2.789 | 2.6188 | 2.3014 | 3.0849 | 2.892 | 2.5306 | 3.3975 | 3.1811 | 2.7746 | 3.9531 | 3.6962 | 3.2115
c) Reinforcement | 1494.7214 | 1420.2818 | 1284.4555 | 1869.0024 | 1761.9968 | 1564.107 | 2231.2044 | 2095.0577 | 1841.0911 | 2467.9256 | 2313.5623 | 2024.4664 | 2718.0091 | 2544.8993 | 2219.6554 | 3162.4733 | 2956.9283 | 2569.2164
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 22.4208 | 21.3042 | 19.2668 | 28.035 | 26.43 | 23.4616 | 33.4681 | 31.4259 | 27.6164 | 37.0189 | 34.7034 | 30.367 | 40.7701 | 38.1735 | 33.2948 | 47.4371 | 44.3539 | 38.5382
b) 1:3:6 Concrete | 3.3631 | 3.1956 | 2.89 | 4.2053 | 3.9645 | 3.5192 | 5.0202 | 4.7139 | 4.1425 | 5.5528 | 5.2055 | 4.555 | 6.1155 | 5.726 | 4.9942 | 7.1156 | 6.6531 | 5.7807
c) Reinforcement | 2690.4986 | 2556.5072 | 2312.0198 | 3364.2043 | 3171.5943 | 2815.3927 | 4016.1679 | 3771.1038 | 3313.964 | 4442.2661 | 4164.4121 | 3644.0396 | 4892.4163 | 4580.8187 | 3995.3797 | 5692.452 | 5322.471 | 4624.5895
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 32.3856 | 30.7728 | 27.8299 | 40.4951 | 38.1766 | 33.889 | 48.3428 | 45.3929 | 39.8903 | 53.4717 | 50.1272 | 43.8634 | 58.8902 | 55.1395 | 48.0925 | 68.5203 | 64.0668 | 55.6664
b) 1:3:6 Concrete | 4.8578 | 4.6159 | 4.1745 | 6.0743 | 5.7265 | 5.0833 | 7.2514 | 6.8089 | 5.9835 | 8.0208 | 7.5191 | 6.5795 | 8.8335 | 8.2709 | 7.2139 | 10.278 | 9.61 | 8.35
c) Reinforcement | 3886.2757 | 3692.7326 | 3339.5842 | 4859.4062 | 4581.1917 | 4066.6783 | 5801.1314 | 5447.1499 | 4786.8369 | 6416.6067 | 6015.262 | 5263.6127 | 7066.8236 | 6616.7381 | 5771.104 | 8222.4307 | 7688.0136 | 6679.9627
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 20.2034 | 19.2862 | 17.6257 | 24.8199 | 23.4916 | 21.0454 | 29.296 | 27.6061 | 24.46 | 32.2164 | 30.3035 | 26.7244 | 35.2945 | 33.1543 | 29.1337 | 40.7434 | 38.2146 | 33.4404
b) 1:3:6 Concrete | 3.0305 | 2.8929 | 2.6439 | 3.723 | 3.5237 | 3.1568 | 4.3944 | 4.1409 | 3.669 | 4.8325 | 4.5455 | 4.0087 | 5.2942 | 4.9731 | 4.3701 | 6.1115 | 5.7322 | 5.0161
c) Reinforcement | 2424.411 | 2314.3395 | 2115.0875 | 2978.3931 | 2818.9951 | 2525.4433 | 3515.516 | 3312.7293 | 2935.1982 | 3865.9683 | 3636.4169 | 3206.9231 | 4235.3393 | 3978.5104 | 3496.0474 | 4889.2043 | 4585.7472 | 4012.8446
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 36.3662 | 34.7151 | 31.7263 | 44.6759 | 42.2849 | 37.8816 | 52.7327 | 49.6909 | 44.028 | 57.9895 | 54.5463 | 48.1038 | 63.5301 | 59.6777 | 52.4407 | 73.3381 | 68.7862 | 60.1927
b) 1:3:6 Concrete | 5.4549 | 5.2073 | 4.7589 | 6.7014 | 6.3427 | 5.6822 | 7.9099 | 7.4536 | 6.6042 | 8.6984 | 8.1819 | 7.2156 | 9.5295 | 8.9516 | 7.8661 | 11.0007 | 10.3179 | 9.0289
c) Reinforcement | 4363.9398 | 4165.811 | 3807.1575 | 5361.1076 | 5074.1911 | 4545.7979 | 6327.9289 | 5962.9128 | 5283.3567 | 6958.743 | 6545.5505 | 5772.4616 | 7623.6108 | 7161.3187 | 6292.8852 | 8800.5677 | 8254.3449 | 7223.1203
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 52.5289 | 50.144 | 45.8269 | 64.5319 | 61.0782 | 54.7179 | 76.1695 | 71.7758 | 63.596 | 83.7626 | 78.789 | 69.4833 | 91.7657 | 86.2011 | 75.7477 | 105.9328 | 99.3579 | 86.945
b) 1:3:6 Concrete | 7.8793 | 7.5216 | 6.874 | 9.6798 | 9.1617 | 8.2077 | 11.4254 | 10.7664 | 9.5394 | 12.5644 | 11.8184 | 10.4225 | 13.7649 | 12.9302 | 11.3622 | 15.8899 | 14.9037 | 13.0417
c) Reinforcement | 6303.4686 | 6017.2826 | 5499.2275 | 7743.822 | 7329.3872 | 6566.1526 | 9140.3417 | 8613.0962 | 7631.5153 | 10051.5176 | 9454.684 | 8338.0002 | 11011.8823 | 10344.127 | 9089.7231 | 12711.9311 | 11922.9426 | 10433.396
(FOR 765KV S/C TOWERS)
PARTICULARS | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
TWIN ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 4.8243 | 4.505 | 3.892 | 6.5999 | 6.1523 | 5.292 | 8.3063 | 7.7368 | 6.6413 | 9.4275 | 8.7784 | 7.5292 | 10.6209 | 9.8875 | 8.4751 | 12.7694 | 11.8844 | 10.1796
b) 1:3:6 Concrete | 0.48243 | 0.4505 | 0.3892 | 0.65999 | 0.61523 | 0.5292 | 0.83063 | 0.77368 | 0.66413 | 0.94275 | 0.87784 | 0.75292 | 1.0621 | 0.98875 | 0.84751 | 1.2769 | 1.1884 | 1.018
c) Reinforcement | 347.3526 | 324.3574 | 280.227 | 475.1933 | 442.9647 | 381.0262 | 598.0534 | 557.0515 | 478.1716 | 678.7781 | 632.0466 | 542.1003 | 764.7063 | 711.8967 | 610.2107 | 919.3937 | 855.6784 | 732.9308
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 9.3472 | 8.7284 | 7.5408 | 12.7873 | 11.9201 | 10.2533 | 16.0935 | 14.9901 | 12.8675 | 18.2657 | 17.0082 | 14.5878 | 20.578 | 19.1569 | 16.4206 | 24.7406 | 23.0261 | 19.723
b) 1:3:6 Concrete | 0.93472 | 0.87284 | 0.75408 | 1.2787 | 1.192 | 1.0253 | 1.6093 | 1.499 | 1.2867 | 1.8266 | 1.7008 | 1.4588 | 2.0578 | 1.9157 | 1.6421 | 2.4741 | 2.3026 | 1.9723
c) Reinforcement | 672.9956 | 628.4425 | 542.9397 | 920.687 | 858.2441 | 738.2383 | 1158.7285 | 1079.2872 | 926.4575 | 1315.1325 | 1224.5903 | 1050.3193 | 1481.6185 | 1379.2998 | 1182.2833 | 1781.3254 | 1657.8768 | 1420.0534
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 13.2669 | 12.3887 | 10.7031 | 18.1497 | 16.9188 | 14.5531 | 22.8423 | 21.2763 | 18.2635 | 25.9256 | 24.1407 | 20.7052 | 29.2075 | 27.1905 | 23.3067 | 35.1157 | 32.6822 | 27.9939
b) 1:3:6 Concrete | 1.3267 | 1.2389 | 1.0703 | 1.815 | 1.6919 | 1.4553 | 2.2842 | 2.1276 | 1.8263 | 2.5926 | 2.4141 | 2.0705 | 2.9208 | 2.719 | 2.3307 | 3.5116 | 3.2682 | 2.7994
c) Reinforcement | 955.2196 | 891.9829 | 770.6241 | 1306.7816 | 1218.1529 | 1047.8221 | 1644.6469 | 1531.8915 | 1314.9719 | 1866.6397 | 1738.1281 | 1490.7758 | 2102.9423 | 1957.7159 | 1678.0795 | 2528.3328 | 2353.1155 | 2015.5597
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 9.3564 | 8.8658 | 7.9444 | 12.0365 | 11.3397 | 10.0215 | 14.6163 | 13.7315 | 12.0493 | 16.3034 | 15.2992 | 13.3857 | 18.0894 | 16.961 | 14.8067 | 21.2765 | 19.9303 | 17.3539
b) 1:3:6 Concrete | 0.93564 | 0.88658 | 0.79444 | 1.2037 | 1.134 | 1.0022 | 1.4616 | 1.3732 | 1.2049 | 1.6303 | 1.5299 | 1.3386 | 1.8089 | 1.6961 | 1.4807 | 2.1276 | 1.993 | 1.7354
c) Reinforcement | 673.6641 | 638.3398 | 571.9978 | 866.6297 | 816.4611 | 721.5496 | 1052.3761 | 988.6691 | 867.5507 | 1173.8451 | 1101.5446 | 963.7693 | 1302.4353 | 1221.1925 | 1066.0833 | 1531.9076 | 1434.9791 | 1249.4795
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 18.1281 | 17.1775 | 15.3923 | 23.3208 | 21.9707 | 19.4167 | 28.3191 | 26.6048 | 23.3455 | 31.5878 | 29.6423 | 25.9348 | 35.0482 | 32.862 | 28.688 | 41.2232 | 38.6149 | 33.6231
b) 1:3:6 Concrete | 1.8128 | 1.7178 | 1.5392 | 2.3321 | 2.1971 | 1.9417 | 2.8319 | 2.6605 | 2.3346 | 3.1588 | 2.9642 | 2.5935 | 3.5048 | 3.2862 | 2.8688 | 4.1223 | 3.8615 | 3.3623
c) Reinforcement | 1305.2242 | 1236.7834 | 1108.2457 | 1679.095 | 1581.8934 | 1398.0023 | 2038.9787 | 1915.5464 | 1680.8794 | 2274.3248 | 2134.2427 | 1867.303 | 2523.4684 | 2366.0605 | 2065.5363 | 2968.0711 | 2780.2721 | 2420.8666
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 25.7302 | 24.381 | 21.8471 | 33.1004 | 31.1843 | 27.5592 | 40.1949 | 37.7617 | 33.1356 | 44.8344 | 42.0729 | 36.8106 | 49.7458 | 46.6428 | 40.7185 | 58.5104 | 54.8082 | 47.7232
b) 1:3:6 Concrete | 2.573 | 2.4381 | 2.1847 | 3.31 | 3.1184 | 2.7559 | 4.0195 | 3.7762 | 3.3136 | 4.4834 | 4.2073 | 3.6811 | 4.9746 | 4.6643 | 4.0718 | 5.851 | 5.4808 | 4.7723
c) Reinforcement | 1852.5763 | 1755.4345 | 1572.9939 | 2383.2316 | 2245.268 | 1984.2614 | 2894.0343 | 2718.8401 | 2385.7643 | 3228.074 | 3029.2477 | 2650.3656 | 3581.6971 | 3358.2795 | 2931.729 | 4212.746 | 3946.1926 | 3436.0687
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 13.7539 | 13.104 | 11.8974 | 17.2711 | 16.3417 | 14.5977 | 20.6597 | 19.4806 | 17.2526 | 22.87 | 21.5348 | 19.0037 | 25.2029 | 23.7069 | 20.8637 | 29.3459 | 27.5717 | 24.1883
b) 1:3:6 Concrete | 1.3754 | 1.3104 | 1.1897 | 1.7271 | 1.6342 | 1.4598 | 2.066 | 1.9481 | 1.7253 | 2.287 | 2.1535 | 1.9004 | 2.5203 | 2.3707 | 2.0864 | 2.9346 | 2.7572 | 2.4188
c) Reinforcement | 990.2829 | 943.4876 | 856.6148 | 1243.5226 | 1176.6014 | 1051.0339 | 1487.5006 | 1402.6019 | 1242.1898 | 1646.6421 | 1550.5047 | 1368.2663 | 1814.608 | 1706.9001 | 1502.188 | 2112.9021 | 1985.1604 | 1741.561
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 26.6482 | 25.389 | 23.0513 | 33.4628 | 31.662 | 28.283 | 40.0282 | 37.7436 | 33.427 | 44.3107 | 41.7236 | 36.8197 | 48.8306 | 45.9322 | 40.4235 | 56.8576 | 53.4201 | 46.8649
b) 1:3:6 Concrete | 2.6648 | 2.5389 | 2.3051 | 3.3463 | 3.1662 | 2.8283 | 4.0028 | 3.7744 | 3.3427 | 4.4311 | 4.1724 | 3.682 | 4.8831 | 4.5932 | 4.0423 | 5.6858 | 5.342 | 4.6865
c) Reinforcement | 1918.6731 | 1828.0073 | 1659.6911 | 2409.3251 | 2279.6652 | 2036.3781 | 2882.0324 | 2717.5412 | 2406.7427 | 3190.3691 | 3004.1028 | 2651.016 | 3515.803 | 3307.1189 | 2910.4892 | 4093.7479 | 3846.2483 | 3374.2745
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 37.8233 | 36.036 | 32.7179 | 47.4957 | 44.9396 | 40.1437 | 56.8143 | 53.5716 | 47.4447 | 62.8926 | 59.2207 | 52.2602 | 69.3079 | 65.1941 | 57.3752 | 80.7011 | 75.8221 | 66.518
b) 1:3:6 Concrete | 3.7823 | 3.6036 | 3.2718 | 4.7496 | 4.494 | 4.0144 | 5.6814 | 5.3572 | 4.7445 | 6.2893 | 5.9221 | 5.226 | 6.9308 | 6.5194 | 5.7375 | 8.0701 | 7.5822 | 6.6518
c) Reinforcement | 2723.278 | 2594.5909 | 2355.6906 | 3419.6873 | 3235.6538 | 2890.3431 | 4090.6266 | 3857.1553 | 3416.022 | 4528.2658 | 4263.8878 | 3762.7323 | 4990.172 | 4693.9753 | 4131.0169 | 5810.4809 | 5459.1911 | 4789.2929
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 22.1414 | 21.1785 | 19.4092 | 27.3091 | 25.9238 | 23.343 | 32.2917 | 30.5357 | 27.2356 | 35.5343 | 33.5497 | 29.8048 | 38.9475 | 36.7298 | 32.5313 | 44.9827 | 42.3662 | 37.3923
b) 1:3:6 Concrete | 2.2141 | 2.1178 | 1.9409 | 2.7309 | 2.5924 | 2.3343 | 3.2292 | 3.0536 | 2.7236 | 3.5534 | 3.355 | 2.9805 | 3.8948 | 3.673 | 3.2531 | 4.4983 | 4.2366 | 3.7392
c) Reinforcement | 1594.179 | 1524.8512 | 1397.4629 | 1966.2558 | 1866.5123 | 1680.6966 | 2325.0029 | 2198.5702 | 1960.9664 | 2558.4715 | 2415.5771 | 2145.9486 | 2804.2223 | 2644.5441 | 2342.2556 | 3238.7534 | 3050.363 | 2692.2438
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 42.8989 | 41.0333 | 37.6053 | 52.9114 | 50.2273 | 45.2271 | 62.5652 | 59.1629 | 52.7691 | 68.8478 | 65.0025 | 57.7469 | 75.4608 | 71.1639 | 63.0294 | 87.154 | 82.0844 | 72.4475
b) 1:3:6 Concrete | 4.2899 | 4.1033 | 3.7605 | 5.2911 | 5.0227 | 4.5227 | 6.2565 | 5.9163 | 5.2769 | 6.8848 | 6.5003 | 5.7747 | 7.5461 | 7.1164 | 6.3029 | 8.7154 | 8.2084 | 7.2448
c) Reinforcement | 3088.7218 | 2954.3992 | 2707.5843 | 3809.6207 | 3616.3675 | 3256.3496 | 4504.6932 | 4259.7298 | 3799.3725 | 4957.0385 | 4680.1806 | 4157.7755 | 5433.1808 | 5123.8042 | 4538.1201 | 6275.0847 | 5910.0783 | 5216.2223
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 60.8888 | 58.2408 | 53.3753 | 75.1 | 71.2904 | 64.1933 | 88.8022 | 83.9732 | 74.898 | 97.7194 | 92.2616 | 81.9633 | 107.1057 | 101.0069 | 89.4611 | 123.7024 | 116.5069 | 102.8288
b) 1:3:6 Concrete | 6.0889 | 5.8241 | 5.3375 | 7.51 | 7.129 | 6.4193 | 8.8802 | 8.3973 | 7.4898 | 9.7719 | 9.2262 | 8.1963 | 10.7106 | 10.1007 | 8.9461 | 12.3702 | 11.6507 | 10.2829
c) Reinforcement | 4383.9923 | 4193.3408 | 3843.0229 | 5407.2036 | 5132.9088 | 4621.9156 | 6393.758 | 6046.0681 | 5392.6577 | 7035.7966 | 6642.837 | 5901.3587 | 7711.6114 | 7272.4963 | 6441.2028 | 8906.5719 | 8388.4982 | 7403.6704
TRIPPLE ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 6.6852 | 6.2266 | 5.3691 | 9.1413 | 8.4984 | 7.2944 | 11.5023 | 10.6843 | 9.1505 | 13.0538 | 12.1213 | 10.3722 | 14.7052 | 13.6514 | 11.674 | 17.6782 | 16.4067 | 14.0195
b) 1:3:6 Concrete | 0.66852 | 0.62266 | 0.53691 | 0.91413 | 0.84984 | 0.72944 | 1.1502 | 1.0684 | 0.91505 | 1.3054 | 1.2121 | 1.0372 | 1.4705 | 1.3651 | 1.1674 | 1.7678 | 1.6407 | 1.402
c) Reinforcement | 481.3368 | 448.3171 | 386.5761 | 658.1766 | 611.8855 | 525.1939 | 828.1684 | 769.2667 | 658.8382 | 939.8704 | 872.7335 | 746.801 | 1058.7763 | 982.9035 | 840.5253 | 1272.8316 | 1181.2849 | 1009.4059
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 12.9526 | 12.0641 | 10.4027 | 17.7114 | 16.4657 | 14.1328 | 22.2858 | 20.7008 | 17.7292 | 25.2917 | 23.485 | 20.0962 | 28.4914 | 26.4497 | 22.6183 | 34.2515 | 31.788 | 27.1628
b) 1:3:6 Concrete | 1.2953 | 1.2064 | 1.0403 | 1.7711 | 1.6466 | 1.4133 | 2.2286 | 2.0701 | 1.7729 | 2.5292 | 2.3485 | 2.0096 | 2.8491 | 2.645 | 2.2618 | 3.4252 | 3.1788 | 2.7163
c) Reinforcement | 932.5901 | 868.6143 | 748.9911 | 1275.2172 | 1185.5282 | 1017.5631 | 1604.5762 | 1490.4543 | 1276.499 | 1820.9989 | 1690.9212 | 1446.927 | 2051.3791 | 1904.3755 | 1628.5178 | 2466.1112 | 2288.7395 | 1955.724
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 18.3844 | 17.1232 | 14.7651 | 25.1387 | 23.3706 | 20.0595 | 31.6314 | 29.3817 | 25.164 | 35.8978 | 33.3336 | 28.5237 | 40.4394 | 37.5415 | 32.1034 | 48.6151 | 45.1185 | 38.5537
b) 1:3:6 Concrete | 1.8384 | 1.7123 | 1.4765 | 2.5139 | 2.3371 | 2.0059 | 3.1631 | 2.9382 | 2.5164 | 3.5898 | 3.3334 | 2.8524 | 4.0439 | 3.7541 | 3.2103 | 4.8615 | 4.5119 | 3.8554
c) Reinforcement | 1323.6763 | 1232.872 | 1063.0842 | 1809.9857 | 1682.6852 | 1444.2831 | 2277.463 | 2115.4835 | 1811.805 | 2584.6436 | 2400.0172 | 2053.7028 | 2911.6348 | 2702.9846 | 2311.4447 | 3500.2869 | 3248.5335 | 2775.8663
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 13.0911 | 12.3881 | 11.098 | 16.8223 | 15.8226 | 13.9732 | 20.4182 | 19.1477 | 16.7852 | 22.7709 | 21.3286 | 18.6399 | 25.262 | 23.6409 | 20.6129 | 29.7079 | 27.7733 | 24.1507
b) 1:3:6 Concrete | 1.3091 | 1.2388 | 1.1098 | 1.6822 | 1.5823 | 1.3973 | 2.0418 | 1.9148 | 1.6785 | 2.2771 | 2.1329 | 1.864 | 2.5262 | 2.3641 | 2.0613 | 2.9708 | 2.7773 | 2.4151
c) Reinforcement | 942.5574 | 891.9421 | 799.0565 | 1211.2065 | 1139.2245 | 1006.0709 | 1470.1117 | 1378.6374 | 1208.5314 | 1639.503 | 1535.6571 | 1342.0704 | 1818.861 | 1702.1429 | 1484.1283 | 2138.9696 | 1999.6767 | 1738.8538
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 25.364 | 24.0019 | 21.5024 | 32.5932 | 30.6562 | 27.0731 | 39.5603 | 37.0987 | 32.5212 | 44.1186 | 41.3241 | 36.1147 | 48.945 | 45.8042 | 39.9375 | 57.5591 | 53.8107 | 46.7921
b) 1:3:6 Concrete | 2.5364 | 2.4002 | 2.1502 | 3.2593 | 3.0656 | 2.7073 | 3.956 | 3.7099 | 3.2521 | 4.4119 | 4.1324 | 3.6115 | 4.8945 | 4.5804 | 3.9937 | 5.7559 | 5.3811 | 4.6792
c) Reinforcement | 1826.205 | 1728.1378 | 1548.172 | 2346.7126 | 2207.2474 | 1949.2624 | 2848.3414 | 2671.1099 | 2341.5297 | 3176.5371 | 2975.3356 | 2600.2614 | 3524.0432 | 3297.9019 | 2875.4987 | 4144.2536 | 3874.3736 | 3369.0293
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 36.0005 | 34.0672 | 30.5195 | 46.2614 | 43.512 | 38.4263 | 56.1501 | 52.6563 | 46.1592 | 62.6199 | 58.6536 | 51.2596 | 69.4704 | 65.0124 | 56.6855 | 81.6968 | 76.3765 | 66.4146
b) 1:3:6 Concrete | 3.6 | 3.4067 | 3.052 | 4.6261 | 4.3512 | 3.8426 | 5.615 | 5.2656 | 4.6159 | 6.262 | 5.8654 | 5.126 | 6.947 | 6.5012 | 5.6685 | 8.1697 | 7.6377 | 6.6415
c) Reinforcement | 2592.0329 | 2452.8407 | 2197.4055 | 3330.8178 | 3132.8673 | 2766.695 | 4042.8072 | 3791.2528 | 3323.4615 | 4508.6334 | 4223.057 | 3690.6935 | 5001.8677 | 4680.893 | 4081.3529 | 5882.1664 | 5499.1109 | 4781.848
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 19.3133 | 18.3831 | 16.6931 | 24.227 | 22.8942 | 20.4445 | 28.969 | 27.2763 | 24.142 | 32.0643 | 30.1467 | 26.5836 | 35.3323 | 33.1832 | 29.1787 | 41.1374 | 38.5876 | 33.8198
b) 1:3:6 Concrete | 1.9313 | 1.8383 | 1.6693 | 2.4227 | 2.2894 | 2.0444 | 2.8969 | 2.7276 | 2.4142 | 3.2064 | 3.0147 | 2.6584 | 3.5332 | 3.3183 | 2.9179 | 4.1137 | 3.8588 | 3.382
c) Reinforcement | 1390.5575 | 1323.5814 | 1201.9012 | 1744.3463 | 1648.3805 | 1472.0007 | 2085.7689 | 1963.897 | 1738.2238 | 2308.6296 | 2170.5634 | 1914.0191 | 2543.9251 | 2389.1894 | 2100.8682 | 2961.8953 | 2778.3038 | 2435.0264
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 37.4195 | 35.6172 | 32.3428 | 46.9399 | 44.3575 | 39.6111 | 56.1275 | 52.8479 | 46.7751 | 62.1246 | 58.4093 | 51.5057 | 68.4563 | 64.2924 | 56.5338 | 79.7038 | 74.7634 | 65.5259
b) 1:3:6 Concrete | 3.742 | 3.5617 | 3.2343 | 4.694 | 4.4357 | 3.9611 | 5.6127 | 5.2848 | 4.6775 | 6.2125 | 5.8409 | 5.1506 | 6.8456 | 6.4292 | 5.6534 | 7.9704 | 7.4763 | 6.5526
c) Reinforcement | 2694.2052 | 2564.439 | 2328.6836 | 3379.6709 | 3193.7373 | 2852.0014 | 4041.1773 | 3805.0503 | 3367.8085 | 4472.9699 | 4205.4667 | 3708.4119 | 4928.8549 | 4629.0545 | 4070.4322 | 5738.6721 | 5382.9636 | 4717.8636
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 53.1116 | 50.5535 | 45.9059 | 66.6243 | 62.959 | 56.2223 | 79.6648 | 75.01 | 66.3905 | 88.1768 | 82.9035 | 73.1049 | 97.1638 | 91.2538 | 80.2415 | 113.1279 | 106.1158 | 93.0045
b) 1:3:6 Concrete | 5.3112 | 5.0553 | 4.5906 | 6.6624 | 6.2959 | 5.6222 | 7.9665 | 7.501 | 6.639 | 8.8177 | 8.2903 | 7.3105 | 9.7164 | 9.1254 | 8.0241 | 11.3128 | 10.6116 | 9.3004
c) Reinforcement | 3824.0332 | 3639.849 | 3305.2283 | 4796.9522 | 4533.0464 | 4048.002 | 5735.8646 | 5400.7166 | 4780.1153 | 6348.7315 | 5969.0495 | 5263.5524 | 6995.7941 | 6570.2709 | 5777.3876 | 8145.212 | 7640.3354 | 6696.3225
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 31.1723 | 29.7955 | 27.3164 | 38.4142 | 36.4285 | 32.7995 | 45.4114 | 42.8912 | 38.2417 | 49.9694 | 47.1194 | 41.839 | 54.7693 | 51.5833 | 45.6595 | 63.2599 | 59.4991 | 52.4761
b) 1:3:6 Concrete | 3.1172 | 2.9796 | 2.7316 | 3.8414 | 3.6429 | 3.2799 | 4.5411 | 4.2891 | 3.8242 | 4.9969 | 4.7119 | 4.1839 | 5.4769 | 5.1583 | 4.566 | 6.326 | 5.9499 | 5.2476
c) Reinforcement | 2244.4038 | 2145.2762 | 1966.7822 | 2765.8198 | 2622.8549 | 2361.5633 | 3269.6191 | 3088.1646 | 2753.4009 | 3597.7934 | 3392.6 | 3012.4048 | 3943.3924 | 3713.9997 | 3287.4845 | 4554.7147 | 4283.9351 | 3778.2782
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 60.3963 | 57.7288 | 52.9256 | 74.4274 | 70.5803 | 63.549 | 87.9845 | 83.1017 | 74.0933 | 96.8156 | 91.2939 | 81.063 | 106.1156 | 99.9427 | 88.4653 | 122.5661 | 115.2795 | 101.6724
b) 1:3:6 Concrete | 6.0396 | 5.7729 | 5.2926 | 7.4427 | 7.058 | 6.3549 | 8.7985 | 8.3102 | 7.4093 | 9.6816 | 9.1294 | 8.1063 | 10.6116 | 9.9943 | 8.8465 | 12.2566 | 11.528 | 10.1672
c) Reinforcement | 4348.5323 | 4156.4727 | 3810.6404 | 5358.7759 | 5081.7814 | 4575.5288 | 6334.8871 | 5983.3189 | 5334.7142 | 6970.7247 | 6573.1625 | 5836.5343 | 7640.3227 | 7195.8744 | 6369.5012 | 8824.7598 | 8300.1242 | 7320.4141
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 85.7238 | 81.9376 | 75.1202 | 105.639 | 100.1785 | 90.1986 | 124.8813 | 117.9507 | 105.1646 | 137.4157 | 129.5785 | 115.0571 | 150.6157 | 141.8542 | 125.5636 | 173.9648 | 163.6225 | 144.3092
b) 1:3:6 Concrete | 8.5724 | 8.1938 | 7.512 | 10.5639 | 10.0178 | 9.0199 | 12.4881 | 11.7951 | 10.5165 | 13.7416 | 12.9578 | 11.5057 | 15.0616 | 14.1854 | 12.5564 | 17.3965 | 16.3623 | 14.4309
c) Reinforcement | 6172.1104 | 5899.5096 | 5408.6509 | 7606.0045 | 7212.8511 | 6494.299 | 8991.4526 | 8492.4526 | 7571.8524 | 9893.9318 | 9329.65 | 8284.1133 | 10844.329 | 10213.4991 | 9040.5824 | 12525.4655 | 11780.8215 | 10390.2651
QUAD ACSR MOOSE
'A' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 8.5461 | 7.9483 | 6.8462 | 11.6828 | 10.8445 | 9.2967 | 14.6984 | 13.6317 | 11.6598 | 16.68 | 15.4642 | 13.2153 | 18.7895 | 17.4154 | 14.8728 | 22.5871 | 20.929 | 17.8595
b) 1:3:6 Concrete | 0.85461 | 0.79483 | 0.68462 | 1.1683 | 1.0845 | 0.92967 | 1.4698 | 1.3632 | 1.166 | 1.668 | 1.5464 | 1.3215 | 1.879 | 1.7415 | 1.4873 | 2.2587 | 2.0929 | 1.7859
c) Reinforcement | 615.3211 | 572.2767 | 492.9252 | 841.1599 | 780.8064 | 669.3615 | 1058.2833 | 981.482 | 839.5047 | 1200.9627 | 1113.4205 | 951.5017 | 1352.8463 | 1253.9103 | 1070.8399 | 1626.2695 | 1506.8915 | 1285.8811
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 16.5581 | 15.3998 | 13.2645 | 22.6354 | 21.0113 | 18.0123 | 28.4781 | 26.4114 | 22.5908 | 32.3176 | 29.9618 | 25.6046 | 36.4047 | 33.7424 | 28.816 | 43.7625 | 40.55 | 34.6027
b) 1:3:6 Concrete | 1.6558 | 1.54 | 1.3264 | 2.2635 | 2.1011 | 1.8012 | 2.8478 | 2.6411 | 2.2591 | 3.2318 | 2.9962 | 2.5605 | 3.6405 | 3.3742 | 2.8816 | 4.3762 | 4.055 | 3.4603
c) Reinforcement | 1192.1847 | 1108.7862 | 955.0425 | 1629.7474 | 1512.8124 | 1296.8879 | 2050.4239 | 1901.6213 | 1626.5404 | 2326.8652 | 2157.2522 | 1843.5346 | 2621.1397 | 2429.4512 | 2074.7524 | 3150.8971 | 2919.6022 | 2491.3946
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 23.5018 | 21.8578 | 18.827 | 32.1276 | 29.8225 | 25.5659 | 40.4205 | 37.4872 | 32.0644 | 45.8701 | 42.5265 | 36.3421 | 51.6712 | 47.8924 | 40.9001 | 62.1145 | 57.5549 | 49.1135
b) 1:3:6 Concrete | 2.3502 | 2.1858 | 1.8827 | 3.2128 | 2.9822 | 2.5566 | 4.0421 | 3.7487 | 3.2064 | 4.587 | 4.2526 | 3.6342 | 5.1671 | 4.7892 | 4.09 | 6.2114 | 5.7555 | 4.9114
c) Reinforcement | 1692.1331 | 1573.761 | 1355.5442 | 2313.1899 | 2147.2175 | 1840.7442 | 2910.2791 | 2699.0754 | 2308.638 | 3302.6474 | 3061.9063 | 2616.6298 | 3720.3273 | 3448.2533 | 2944.8098 | 4472.241 | 4143.9515 | 3536.1729
'B' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 16.8257 | 15.9103 | 14.2516 | 21.6081 | 20.3054 | 17.9249 | 26.2201 | 24.564 | 21.521 | 29.2383 | 27.3579 | 23.894 | 32.4345 | 30.3207 | 26.4191 | 38.1393 | 35.6163 | 30.9476
b) 1:3:6 Concrete | 1.6826 | 1.591 | 1.4252 | 2.1608 | 2.0305 | 1.7925 | 2.622 | 2.4564 | 2.1521 | 2.9238 | 2.7358 | 2.3894 | 3.2435 | 3.0321 | 2.6419 | 3.8139 | 3.5616 | 3.0948
c) Reinforcement | 1211.4507 | 1145.5444 | 1026.1153 | 1555.7833 | 1461.9879 | 1290.5922 | 1887.8473 | 1768.6056 | 1549.5122 | 2105.161 | 1969.7696 | 1720.3714 | 2335.2867 | 2183.0933 | 1902.1734 | 2746.0316 | 2564.3743 | 2228.2281
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 32.5998 | 30.8263 | 27.6125 | 41.8657 | 39.3417 | 34.7295 | 50.8014 | 47.5927 | 41.6969 | 56.6493 | 53.006 | 46.2947 | 62.8419 | 58.7464 | 51.187 | 73.8949 | 69.0066 | 59.961
b) 1:3:6 Concrete | 3.26 | 3.0826 | 2.7612 | 4.1866 | 3.9342 | 3.4729 | 5.0801 | 4.7593 | 4.1697 | 5.6649 | 5.3006 | 4.6295 | 6.2842 | 5.8746 | 5.1187 | 7.3895 | 6.9007 | 5.9961
c) Reinforcement | 2347.1857 | 2219.4922 | 1988.0984 | 3014.3301 | 2832.6015 | 2500.5224 | 3657.7041 | 3426.6734 | 3002.18 | 4078.7494 | 3816.4286 | 3333.2197 | 4524.6179 | 4229.7432 | 3685.461 | 5320.4361 | 4968.4751 | 4317.192
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 46.2707 | 43.7534 | 39.1919 | 59.4223 | 55.8398 | 49.2935 | 72.1053 | 67.5509 | 59.1828 | 80.4055 | 75.2343 | 65.7086 | 89.195 | 83.382 | 72.6525 | 104.8831 | 97.9448 | 85.1059
b) 1:3:6 Concrete | 4.6271 | 4.3753 | 3.9192 | 5.9422 | 5.584 | 4.9293 | 7.2105 | 6.7551 | 5.9183 | 8.0405 | 7.5234 | 6.5709 | 8.9195 | 8.3382 | 7.2652 | 10.4883 | 9.7945 | 8.5106
c) Reinforcement | 3331.4894 | 3150.247 | 2821.8171 | 4278.404 | 4020.4666 | 3549.1286 | 5191.58 | 4863.6654 | 4261.1586 | 5789.1928 | 5416.8664 | 4731.0215 | 6422.0384 | 6003.5065 | 5230.9769 | 7551.5868 | 7052.0292 | 6127.6274
'C' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 24.8727 | 23.6622 | 21.4887 | 31.1829 | 29.4467 | 26.2912 | 37.2783 | 35.0721 | 31.0314 | 41.2586 | 38.7586 | 34.1635 | 45.4617 | 42.6594 | 37.4937 | 52.929 | 49.6034 | 43.4513
b) 1:3:6 Concrete | 2.4873 | 2.3662 | 2.1489 | 3.1183 | 2.9447 | 2.6291 | 3.7278 | 3.5072 | 3.1031 | 4.1259 | 3.8759 | 3.4163 | 4.5462 | 4.2659 | 3.7494 | 5.2929 | 4.9603 | 4.3451
c) Reinforcement | 1790.8321 | 1703.6753 | 1547.1876 | 2245.1699 | 2120.1596 | 1892.9676 | 2684.0373 | 2525.192 | 2234.2577 | 2970.6172 | 2790.6222 | 2459.7718 | 3273.2423 | 3071.4787 | 2699.5485 | 3810.8884 | 3571.4471 | 3128.4917
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 48.1908 | 45.8454 | 41.6344 | 60.4169 | 57.0529 | 50.9392 | 72.2267 | 67.9522 | 60.1233 | 79.9385 | 75.0949 | 66.1918 | 88.082 | 82.6526 | 72.6441 | 102.5499 | 96.1067 | 84.1868
b) 1:3:6 Concrete | 4.8191 | 4.5845 | 4.1634 | 6.0417 | 5.7053 | 5.0939 | 7.2227 | 6.7952 | 6.0123 | 7.9938 | 7.5095 | 6.6192 | 8.8082 | 8.2653 | 7.2644 | 10.255 | 9.6107 | 8.4187
c) Reinforcement | 3469.7373 | 3300.8708 | 2997.676 | 4350.0166 | 4107.8093 | 3667.6247 | 5200.3223 | 4892.5594 | 4328.8743 | 5755.5708 | 5406.8306 | 4765.8079 | 6341.9069 | 5950.99 | 5230.3751 | 7383.5963 | 6919.6788 | 6061.4526
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 68.3998 | 65.0709 | 59.094 | 85.753 | 80.9783 | 72.3008 | 102.5153 | 96.4483 | 85.3362 | 113.4611 | 106.5863 | 93.9496 | 125.0197 | 117.3134 | 103.1078 | 145.5548 | 136.4094 | 119.491
b) 1:3:6 Concrete | 6.84 | 6.5071 | 5.9094 | 8.5753 | 8.0978 | 7.2301 | 10.2515 | 9.6448 | 8.5336 | 11.3461 | 10.6586 | 9.395 | 12.502 | 11.7313 | 10.3108 | 14.5555 | 13.6409 | 11.9491
c) Reinforcement | 4924.7884 | 4685.107 | 4254.766 | 6174.2171 | 5830.439 | 5205.6609 | 7381.1026 | 6944.2779 | 6144.2087 | 8169.1973 | 7674.2112 | 6764.3725 | 9001.4162 | 8446.5665 | 7423.7582 | 10479.9431 | 9821.4796 | 8603.3521
'D' TYPE TOWER
1. Normal Dry, DFR
a) M20 Concrete Cu.M | 40.2032 | 38.4125 | 35.2236 | 49.5192 | 46.9333 | 42.256 | 58.531 | 55.2467 | 49.2477 | 64.4044 | 60.6892 | 53.8731 | 70.5911 | 66.4369 | 58.7877 | 81.5372 | 76.632 | 67.5599
b) 1:3:6 Concrete | 4.0203 | 3.8413 | 3.5224 | 4.9519 | 4.6933 | 4.2256 | 5.8531 | 5.5247 | 4.9248 | 6.4404 | 6.0689 | 5.3873 | 7.0591 | 6.6437 | 5.8788 | 8.1537 | 7.6632 | 6.756
c) Reinforcement | 2894.6285 | 2765.7012 | 2536.1014 | 3565.3838 | 3379.1976 | 3042.4299 | 4214.2354 | 3977.759 | 3545.8353 | 4637.1153 | 4369.6229 | 3878.861 | 5082.5624 | 4783.4552 | 4232.7134 | 5870.6761 | 5517.5072 | 4864.3127
2. Wet & PS Foundations
a) M20 Concrete Cu.M | 77.8936 | 74.4243 | 68.2458 | 95.9435 | 90.9333 | 81.8709 | 113.4039 | 107.0404 | 95.4174 | 124.7835 | 117.5853 | 104.3791 | 136.7703 | 128.7215 | 113.9011 | 157.9783 | 148.4746 | 130.8973
b) 1:3:6 Concrete | 7.7894 | 7.4424 | 6.8246 | 9.5943 | 9.0933 | 8.1871 | 11.3404 | 10.704 | 9.5417 | 12.4783 | 11.7585 | 10.4379 | 13.677 | 12.8721 | 11.3901 | 15.7978 | 14.8475 | 13.0897
c) Reinforcement | 5608.3428 | 5358.5461 | 4913.6966 | 6907.9311 | 6547.1953 | 5894.708 | 8165.081 | 7706.908 | 6870.0558 | 8984.4109 | 8466.1445 | 7515.2932 | 9847.4646 | 9267.9445 | 8200.8823 | 11374.4349 | 10690.1702 | 9424.6058
3. FS, SFR, WBC
a) M20 Concrete Cu.M | 110.5587 | 105.6344 | 96.865 | 136.1779 | 129.0666 | 116.2039 | 160.9604 | 151.9283 | 135.4312 | 177.112 | 166.8953 | 148.1509 | 194.1256 | 182.7014 | 161.6661 | 224.2272 | 210.7381 | 185.7897
b) 1:3:6 Concrete | 11.0559 | 10.5634 | 9.6865 | 13.6178 | 12.9067 | 11.6204 | 16.096 | 15.1928 | 13.5431 | 17.7112 | 16.6895 | 14.8151 | 19.4126 | 18.2701 | 16.1666 | 22.4227 | 21.0738 | 18.579
c) Reinforcement | 7960.2284 | 7605.6784 | 6974.279 | 9804.8054 | 9292.7934 | 8366.6824 | 11589.1472 | 10938.8372 | 9751.047 | 12752.0671 | 12016.4631 | 10666.8678 | 13977.0466 | 13154.5018 | 11639.962 | 16144.3592 | 15173.1448 | 13376.8598

## 400 kV DC
CALCULATION OF WIND PRESSURES ON CONDUCTOR & GROUND WIRE.
AS PER THE REVISED CODE IS-802 (Part I / Section I ) :1995
(FOR 400KV D/C TOWERS)
(Reliability Level-1)
DESIGN DATA |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
PARTICULARS
4. Mean height of top conductor above ground in Mtrs. | : | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
5. Mean height of Ground wire above ground in Mtrs. | : | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
6. Height of Insulator above ground in Mtrs. | : | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
7. Basic Wind Speed in M/s [ Vb ] | : | 33 | 33 | 33 | 39 | 39 | 39 | 44 | 44 | 44 | 47 | 47 | 47 | 50 | 50 | 50 | 55 | 55 | 55
8. Reference wind speed in M/s [ Vr = Vb/1.375 ] | : | 24 | 24 | 24 | 28.3636 | 28.3636 | 28.3636 | 32 | 32 | 32 | 34.1818 | 34.1818 | 34.1818 | 36.3636 | 36.3636 | 36.3636 | 40 | 40 | 40
9. Risk Level Co-efficient [ K1 ] | : | bar: Wind Zone-1 1 to Wind Zone-6 3
10. Terrain Roughness Co-efficient | : | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85
11. Design Wind speed in M/s [ Vd = Vr * K1 * K2 ] | : | 25.92 | 24 | 20.4 | 30.6327 | 28.3636 | 24.1091 | 34.56 | 32 | 27.2 | 36.9164 | 34.1818 | 29.0545 | 39.2727 | 36.3636 | 30.9091 | 43.2 | 40 | 34
I. WIND PRESSURE ON CONDUCTOR
1. Gust Response factor [ Gc ] | : | 1.983 | 2.175 | 2.547 | 1.983 | 2.175 | 2.547 | 1.983 | 2.175 | 2.547 | 1.983 | 2.175 | 2.547 | 1.983 | 2.175 | 2.547 | 1.983 | 2.175 | 2.547
2. Drag Co-efficient [ Cdc ] | : | bar: Wind Zone-1 1 to Wind Zone-6 3
3. Design Wind Pressure on Conductor in Kg/sq.m. [ Pc ] | : | 81.4845 | 76.6239 | 64.8293 | 113.8089 | 107.0201 | 90.5467 | 144.8613 | 136.2202 | 115.2521 | 165.2886 | 155.4289 | 131.5041 | 187.0626 | 175.9042 | 148.8277 | 226.3458 | 212.844 | 180.0815
[Pc = 0.6 * Vd * Vd * Gc *Cdc/ 9.81 ]
II. WIND PRESSURE ON GROUND WIRE.
1. Gust Response factor for G wire[ Gc ] | : | 2.036 | 2.251 | 2.637 | 2.036 | 2.251 | 2.637 | 2.036 | 2.251 | 2.637 | 2.036 | 2.251 | 2.637 | 2.036 | 2.251 | 2.637 | 2.036 | 2.251 | 2.637
8. Drag Co-efficient [ Cdc ] | : | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
9. Design Wind Pressure on G. Wire in Kg/sq.m. [ Pgw ] | : | 100.3948 | 95.1615 | 80.5441 | 140.2208 | 132.9116 | 112.4955 | 178.4797 | 169.1761 | 143.1896 | 203.6475 | 193.032 | 163.3811 | 230.4748 | 218.4608 | 184.9039 | 278.8745 | 264.3376 | 223.7337
[Pgw = 0.6 * Vd * Vd * Gc *Cdc/ 9.81 ]
III. WIND PRESSURE ON INSULATORS.
1. Gust Response factor for Insulator [ Gi ] | : | 2.094 | 2.432 | 3.168 | 2.094 | 2.432 | 3.168 | 2.094 | 2.432 | 3.168 | 2.094 | 2.432 | 3.168 | 2.094 | 2.432 | 3.168 | 2.094 | 2.432 | 3.168
2. Drag Co-efficient [ Cdi ] | : | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
3. Design Wind Pressure on Insulators in Kg/sq.m. [ Pi ] | : | 103.2548 | 102.8134 | 96.7629 | 144.2154 | 143.5988 | 135.1482 | 183.5641 | 182.7793 | 172.023 | 209.4489 | 208.5535 | 196.2804 | 237.0404 | 236.027 | 222.1371 | 286.8188 | 285.5927 | 268.7859
[Pi = 0.6 * Vd * Vd * Gc *Cdc/ 9.81 ]
III. WIND PRESSURE ON TOWERS.
1. Gust Response factor for Towers [ GT ] |  | 2.106 | 2.45 | 3.192 | 2.106 | 2.45 | 3.192 | 2.106 | 2.45 | 3.192 | 2.106 | 2.45 | 3.192 | 2.106 | 2.45 | 3.192 | 2.106 | 2.45 | 3.192
2. Drag Co-efficient [ Cdt ] |  | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9
3. Design Wind Pressure on Towers in Kg/sq.m. [ Pi ] |  | 250.9624 | 250.3046 | 235.6153 | 350.5177 | 349.599 | 329.0825 | 446.1553 | 444.9859 | 418.8716 | 509.0688 | 507.7345 | 477.9377 | 576.1303 | 574.6203 | 540.8983 | 697.1177 | 695.2905 | 654.4869
[Pi = 0.6 * Vd * Vd * Gt *Cdt/ 9.81 ]

## 400 kV SC
CALCULATION OF WIND PRESSURES ON CONDUCTOR & GROUND WIRE.
AS PER THE REVISED CODE IS-802 (Part I / Section I ) :1995
(FOR 400KV S/C TOWERS)
(Reliability Level-1)
DESIGN DATA |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
PARTICULARS
4. Mean height of top conductor above ground in Mtrs. | : | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
5. Mean height of Ground wire above ground in Mtrs. | : | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
6. Height of Insulator above ground in Mtrs. | : | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
7. Basic Wind Speed in M/s [ Vb ] | : | 33 | 33 | 33 | 39 | 39 | 39 | 44 | 44 | 44 | 47 | 47 | 47 | 50 | 50 | 50 | 55 | 55 | 55
8. Reference wind speed in M/s [ Vr = Vb/1.375 ] | : | 24 | 24 | 24 | 28.3636 | 28.3636 | 28.3636 | 32 | 32 | 32 | 34.1818 | 34.1818 | 34.1818 | 36.3636 | 36.3636 | 36.3636 | 40 | 40 | 40
9. Risk Level Co-efficient [ K1 ] | : | bar: Wind Zone-1 1 to Wind Zone-6 3
10. Terrain Roughness Co-efficient | : | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85
11. Design Wind speed in M/s [ Vd = Vr * K1 * K2 ] | : | 25.92 | 24 | 20.4 | 30.6327 | 28.3636 | 24.1091 | 34.56 | 32 | 27.2 | 36.9164 | 34.1818 | 29.0545 | 39.2727 | 36.3636 | 30.9091 | 43.2 | 40 | 34
I. WIND PRESSURE ON CONDUCTOR
1. Gust Response factor [ Gc ] | : | 1.847 | 1.975 | 2.282 | 1.847 | 1.975 | 2.282 | 1.847 | 1.975 | 2.282 | 1.847 | 1.975 | 2.282 | 1.847 | 1.975 | 2.282 | 1.847 | 1.975 | 2.282
2. Drag Co-efficient [ Cdc ] | : | bar: Wind Zone-1 1 to Wind Zone-6 3
3. Design Wind Pressure on Conductor in Kg/sq.m. [ Pc ] | : | 75.896 | 69.578 | 58.0842 | 106.0036 | 97.1792 | 81.1259 | 134.9263 | 123.6942 | 103.2608 | 153.9526 | 141.1366 | 117.8219 | 174.2333 | 159.7291 | 133.343 | 210.8223 | 193.2722 | 161.3451
[Pc = 0.6 * Vd * Vd * Gc *Cdc/ 9.81 ]
II. WIND PRESSURE ON GROUND WIRE.
1. Gust Response factor for G wire[ Gc ] | : | 1.932 | 2.1 | 2.442 | 1.932 | 2.1 | 2.442 | 1.932 | 2.1 | 2.442 | 1.932 | 2.1 | 2.442 | 1.932 | 2.1 | 2.442 | 1.932 | 2.1 | 2.442
8. Drag Co-efficient [ Cdc ] | : | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
9. Design Wind Pressure on G. Wire in Kg/sq.m. [ Pgw ] | : | 95.2666 | 88.778 | 74.5881 | 133.0583 | 123.9957 | 104.1768 | 169.3628 | 157.8275 | 132.601 | 193.2451 | 180.0832 | 151.2994 | 218.702 | 203.8062 | 171.2307 | 264.6294 | 246.6055 | 207.1891
[Pgw = 0.6 * Vd * Vd * Gc *Cdc/ 9.81 ]
III. WIND PRESSURE ON INSULATORS.
1. Gust Response factor for Insulator [ Gi ] | : | 1.916 | 2.26 | 2.916 | 1.916 | 2.26 | 2.916 | 1.916 | 2.26 | 2.916 | 1.916 | 2.26 | 2.916 | 1.916 | 2.26 | 2.916 | 1.916 | 2.26 | 2.916
2. Drag Co-efficient [ Cdi ] | : | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
3. Design Wind Pressure on Insulators in Kg/sq.m. [ Pi ] | : | 94.4776 | 95.542 | 89.0659 | 131.9564 | 133.443 | 124.3978 | 167.9602 | 169.8525 | 158.3393 | 191.6447 | 193.8038 | 180.6671 | 216.8908 | 219.3343 | 204.4671 | 262.4379 | 265.3945 | 247.4052
[Pi = 0.6 * Vd * Vd * Gc *Cdc/ 9.81 ]
III. WIND PRESSURE ON TOWERS.
1. Gust Response factor for Towers [ GT ] |  | 1.982 | 2.32 | 3.008 | 1.982 | 2.32 | 3.008 | 1.982 | 2.32 | 3.008 | 1.982 | 2.32 | 3.008 | 1.982 | 2.32 | 3.008 | 1.982 | 2.32 | 3.008
2. Drag Co-efficient [ Cdt ] |  | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9
3. Design Wind Pressure on Towers in Kg/sq.m. [ Pi ] |  | 236.1859 | 237.0231 | 222.0335 | 329.8794 | 331.0488 | 310.1128 | 419.886 | 421.3744 | 394.7261 | 479.0951 | 480.7935 | 450.3874 | 542.2081 | 544.1302 | 509.7187 | 656.0718 | 658.3976 | 616.7596
[Pi = 0.6 * Vd * Vd * Gt *Cdt/ 9.81 ]

## 765 kV SC
CALCULATION OF WIND PRESSURES ON CONDUCTOR & GROUND WIRE.
AS PER THE REVISED CODE IS-802 (Part I / Section I ) :1995
(FOR 765 KV S/C TOWERS)
(Reliability Level-1)
DESIGN DATA |  | Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
Terrain Category |  | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
PARTICULARS
4. Mean height of top conductor above ground in Mtrs. | : | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
5. Mean height of Ground wire above ground in Mtrs. | : | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
6. Height of Insulator above ground in Mtrs. | : | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
7. Basic Wind Speed in M/s [ Vb ] | : | 33 | 33 | 33 | 39 | 39 | 39 | 44 | 44 | 44 | 47 | 47 | 47 | 50 | 50 | 50 | 55 | 55 | 55
8. Reference wind speed in M/s [ Vr = Vb/1.375 ] | : | 24 | 24 | 24 | 28.3636 | 28.3636 | 28.3636 | 32 | 32 | 32 | 34.1818 | 34.1818 | 34.1818 | 36.3636 | 36.3636 | 36.3636 | 40 | 40 | 40
9. Risk Level Co-efficient [ K1 ] | : | bar: Wind Zone-1 1 to Wind Zone-6 3
10. Terrain Roughness Co-efficient | : | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85 | 1.08 | 1 | 0.85
11. Design Wind speed in M/s [ Vd = Vr * K1 * K2 ] | : | 25.92 | 24 | 20.4 | 30.6327 | 28.3636 | 24.1091 | 34.56 | 32 | 27.2 | 36.9164 | 34.1818 | 29.0545 | 39.2727 | 36.3636 | 30.9091 | 43.2 | 40 | 34
I. WIND PRESSURE ON CONDUCTOR
1. Gust Response factor [ Gc ] | : | 1.89 | 2.025 | 2.365 | 1.89 | 2.025 | 2.365 | 1.89 | 2.025 | 2.365 | 1.89 | 2.025 | 2.365 | 1.89 | 2.025 | 2.365 | 1.89 | 2.025 | 2.365
2. Drag Co-efficient [ Cdc ] | : | bar: Wind Zone-1 1 to Wind Zone-6 3
3. Design Wind Pressure on Conductor in Kg/sq.m. [ Pc ] | : | 77.663 | 71.3394 | 60.1968 | 108.4714 | 99.6394 | 84.0766 | 138.0675 | 126.8257 | 107.0166 | 157.5367 | 144.7097 | 122.1073 | 178.2897 | 163.7728 | 138.1929 | 215.7305 | 198.1651 | 167.2135
[Pc = 0.6 * Vd * Vd * Gc *Cdc/ 9.81 ]
II. WIND PRESSURE ON GROUND WIRE.
1. Gust Response factor for G wire[ Gc ] | : | 1.983 | 2.175 | 2.547 | 1.983 | 2.175 | 2.547 | 1.983 | 2.175 | 2.547 | 1.983 | 2.175 | 2.547 | 1.983 | 2.175 | 2.547 | 1.983 | 2.175 | 2.547
8. Drag Co-efficient [ Cdc ] | : | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
9. Design Wind Pressure on G. Wire in Kg/sq.m. [ Pgw ] | : | 97.7814 | 91.9486 | 77.7952 | 136.5707 | 128.4241 | 108.6561 | 173.8336 | 163.4642 | 138.3026 | 198.3463 | 186.5147 | 157.8049 | 224.4752 | 211.085 | 178.5932 | 271.615 | 255.4128 | 216.0978
[Pgw = 0.6 * Vd * Vd * Gc *Cdc/ 9.81 ]
III. WIND PRESSURE ON INSULATORS.
1. Gust Response factor for Insulator [ Gi ] | : | 1.982 | 2.32 | 3.008 | 1.982 | 2.32 | 3.008 | 1.982 | 2.32 | 3.008 | 1.982 | 2.32 | 3.008 | 1.982 | 2.32 | 3.008 | 1.982 | 2.32 | 3.008
2. Drag Co-efficient [ Cdi ] | : | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
3. Design Wind Pressure on Insulators in Kg/sq.m. [ Pi ] | : | 97.7321 | 98.0785 | 91.8759 | 136.5018 | 136.9857 | 128.3226 | 173.7459 | 174.3618 | 163.335 | 198.2462 | 198.949 | 186.3672 | 224.362 | 225.1573 | 210.9181 | 271.478 | 272.4404 | 255.2109
[Pi = 0.6 * Vd * Vd * Gc *Cdc/ 9.81 ]
III. WIND PRESSURE ON TOWERS.
1. Gust Response factor for Towers [ GT ] |  | 2.048 | 2.38 | 3.092 | 2.048 | 2.38 | 3.092 | 2.048 | 2.38 | 3.092 | 2.048 | 2.38 | 3.092 | 2.048 | 2.38 | 3.092 | 2.048 | 2.38 | 3.092
2. Drag Co-efficient [ Cdt ] |  | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9
3. Design Wind Pressure on Towers in Kg/sq.m. [ Pi ] |  | 244.0508 | 243.153 | 228.2339 | 340.8643 | 339.6104 | 318.7729 | 433.868 | 432.272 | 405.7491 | 495.0488 | 493.2278 | 462.9647 | 560.2635 | 558.2025 | 523.9528 | 677.9188 | 675.4251 | 633.9829
[Pi = 0.6 * Vd * Vd * Gt *Cdt/ 9.81 ]

## Loading calculations
TOWER LOADING CALCULATIONS FOR 400 KV DC LINE
TWIN ACSR MOOSE
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
A' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 2
CONDUCTOR
Wind on Conductor | 2071.0098 | 1947.4719 | 1647.7022 | 2892.5674 | 2720.0227 | 2301.3361 | 3681.7952 | 3462.1722 | 2929.2484 | 4200.974 | 3950.3814 | 3342.3087 | 4754.3843 | 4470.7802 | 3782.6038 | 5752.805 | 5409.644 | 4576.9506
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 373.7973 | 362.6649 | 336.4324 | 450.0963 | 433.9035 | 394.891 | 524.0005 | 503.5217 | 453.5415 | 571.9478 | 548.8949 | 492.3072 | 622.1881 | 596.5612 | 533.3651 | 710.3225 | 680.3988 | 606.1849
TOTAL | 2579.2448 | 2443.9998 | 2110.1199 | 3530.432 | 3340.8919 | 2872.1901 | 4444.7961 | 4203.6725 | 3606.7638 | 5045.6241 | 4770.8129 | 4090.1729 | 5685.1989 | 5374.6485 | 4605.1914 | 6836.5656 | 6461.8845 | 5533.0947
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 82.6892 | 80.3636 | 73.8699 | 100.1013 | 96.9571 | 88.0441 | 116.1109 | 112.2879 | 101.3708 | 126.2329 | 122.002 | 109.8839 | 136.6871 | 132.0465 | 118.7247 | 154.7624 | 149.4324 | 134.0913
TOTAL | 523.6232 | 498.3131 | 427.6198 | 715.9513 | 680.7047 | 582.1245 | 899.9935 | 855.3092 | 730.2594 | 1020.6527 | 969.7985 | 827.4536 | 1148.9323 | 1091.5265 | 930.8227 | 1379.579 | 1310.4032 | 1116.7298
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'B' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 15
CONDUCTOR
Wind on Conductor | 2071.0098 | 1947.4719 | 1647.7022 | 2892.5674 | 2720.0227 | 2301.3361 | 3681.7952 | 3462.1722 | 2929.2484 | 4200.974 | 3950.3814 | 3342.3087 | 4754.3843 | 4470.7802 | 3782.6038 | 5752.805 | 5409.644 | 4576.9506
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 2795.6222 | 2712.3637 | 2516.1711 | 3366.2607 | 3245.1556 | 2953.3817 | 3918.9889 | 3765.8284 | 3392.0274 | 4277.5856 | 4105.1737 | 3681.9557 | 4653.332 | 4461.6689 | 3989.0266 | 5312.4874 | 5088.6889 | 4533.6446
TOTAL | 5001.0697 | 4793.6985 | 4289.8586 | 6446.5965 | 6152.1439 | 5430.6808 | 7839.7844 | 7465.9792 | 6545.2497 | 8751.262 | 8327.0916 | 7279.8214 | 9716.3428 | 9239.7563 | 8060.8529 | 11438.7305 | 10870.1745 | 9460.5544
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 618.4308 | 601.0375 | 552.4714 | 748.6559 | 725.1401 | 658.4803 | 868.3908 | 839.7986 | 758.15 | 944.0931 | 912.4503 | 821.8194 | 1022.2804 | 987.5732 | 887.9399 | 1157.4646 | 1117.6022 | 1002.8661
TOTAL | 1059.3648 | 1018.987 | 906.2213 | 1364.5059 | 1308.8877 | 1152.5607 | 1652.2735 | 1582.82 | 1387.0387 | 1838.513 | 1760.2469 | 1539.3891 | 2034.5255 | 1947.0532 | 1700.0379 | 2382.2812 | 2278.573 | 1985.5046
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'C' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 30
CONDUCTOR
Wind on Conductor | 2071.0098 | 1947.4719 | 1647.7022 | 2892.5674 | 2720.0227 | 2301.3361 | 3681.7952 | 3462.1722 | 2929.2484 | 4200.974 | 3950.3814 | 3342.3087 | 4754.3843 | 4470.7802 | 3782.6038 | 5752.805 | 5409.644 | 4576.9506
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 5543.4106 | 5378.3181 | 4989.2898 | 6674.9237 | 6434.7857 | 5856.2302 | 7770.9227 | 7467.2224 | 6726.0162 | 8481.9805 | 8140.1067 | 7300.912 | 9227.0442 | 8846.9975 | 7909.7998 | 10534.0766 | 10090.3089 | 8989.7172
TOTAL | 7748.8581 | 7459.6529 | 6762.9773 | 9755.2595 | 9341.774 | 8333.5293 | 11691.7183 | 11167.3732 | 9879.2385 | 12955.6569 | 12362.0246 | 10898.7778 | 14290.055 | 13625.0848 | 11981.6261 | 16660.3197 | 15871.7945 | 13916.627
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 1226.28 | 1191.7911 | 1095.4899 | 1484.5022 | 1437.8728 | 1305.6939 | 1721.9232 | 1665.2281 | 1503.3279 | 1872.0326 | 1809.2884 | 1629.5771 | 2027.0692 | 1958.2487 | 1760.687 | 2295.1246 | 2216.0819 | 1988.5728
TOTAL | 1667.214 | 1609.7406 | 1449.2398 | 2100.3522 | 2021.6205 | 1799.7743 | 2505.8059 | 2408.2494 | 2132.2165 | 2766.4524 | 2657.0849 | 2347.1469 | 3039.3144 | 2917.7287 | 2572.7849 | 3519.9413 | 3377.0527 | 2971.2113
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'D Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 60
CONDUCTOR
Wind on Conductor | 2071.0098 | 1947.4719 | 1647.7022 | 2892.5674 | 2720.0227 | 2301.3361 | 3681.7952 | 3462.1722 | 2929.2484 | 4200.974 | 3950.3814 | 3342.3087 | 4754.3843 | 4470.7802 | 3782.6038 | 5752.805 | 5409.644 | 4576.9506
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 10709.0469 | 10390.1126 | 9638.5677 | 12894.9625 | 12431.0514 | 11313.3679 | 15012.2699 | 14425.5658 | 12993.6656 | 16385.9281 | 15725.4785 | 14104.279 | 17825.2806 | 17091.0867 | 15280.5598 | 20350.2733 | 19492.9798 | 17366.8
TOTAL | 12914.4944 | 12471.4475 | 11412.2552 | 15975.2983 | 15338.0397 | 13790.6671 | 18933.0655 | 18125.7167 | 16146.8879 | 20859.6045 | 19947.3965 | 17702.1447 | 22888.2914 | 21869.1741 | 19352.3861 | 26476.5164 | 25274.4655 | 22293.7099
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 2368.9911 | 2302.3636 | 2116.324 | 2867.838 | 2777.757 | 2522.4069 | 3326.5002 | 3216.9737 | 2904.2064 | 3616.4892 | 3495.2767 | 3148.1013 | 3915.997 | 3783.046 | 3401.3861 | 4433.8403 | 4281.1415 | 3841.6277
TOTAL | 2809.9251 | 2720.3131 | 2470.0739 | 3483.688 | 3361.5046 | 3016.4873 | 4110.3829 | 3959.995 | 3533.0951 | 4510.9091 | 4343.0733 | 3865.6711 | 4928.2422 | 4742.526 | 4213.484 | 5658.6569 | 5442.1123 | 4824.2662
TRIPPLE ACSR MOOSE
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
A' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 2
CONDUCTOR
Wind on Conductor | 3106.5147 | 2921.2078 | 2471.5533 | 4338.8511 | 4080.034 | 3452.0042 | 5522.6928 | 5193.2583 | 4393.8726 | 6301.4609 | 5925.5721 | 5013.4631 | 7131.5764 | 6706.1703 | 5673.9057 | 8629.2075 | 8114.4661 | 6865.4259
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 560.6959 | 543.9974 | 504.6486 | 675.1444 | 650.8553 | 592.3365 | 786.0007 | 755.2825 | 680.3122 | 857.9216 | 823.3423 | 738.4608 | 933.2821 | 894.8418 | 800.0476 | 1065.4837 | 1020.5982 | 909.2774
TOTAL | 3801.6483 | 3599.0682 | 3102.1873 | 5201.7639 | 4917.855 | 4220.3037 | 6547.6939 | 6186.5194 | 5298.1587 | 7432.085 | 7020.451 | 6007.4809 | 8373.4851 | 7908.3192 | 6763.1758 | 10068.1293 | 9506.9059 | 8124.6625
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 82.6892 | 80.3636 | 73.8699 | 100.1013 | 96.9571 | 88.0441 | 116.1109 | 112.2879 | 101.3708 | 126.2329 | 122.002 | 109.8839 | 136.6871 | 132.0465 | 118.7247 | 154.7624 | 149.4324 | 134.0913
TOTAL | 523.6232 | 498.3131 | 427.6198 | 715.9513 | 680.7047 | 582.1245 | 899.9935 | 855.3092 | 730.2594 | 1020.6527 | 969.7985 | 827.4536 | 1148.9323 | 1091.5265 | 930.8227 | 1379.579 | 1310.4032 | 1116.7298
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'B' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 15
CONDUCTOR
Wind on Conductor | 3106.5147 | 2921.2078 | 2471.5533 | 4338.8511 | 4080.034 | 3452.0042 | 5522.6928 | 5193.2583 | 4393.8726 | 6301.4609 | 5925.5721 | 5013.4631 | 7131.5764 | 6706.1703 | 5673.9057 | 8629.2075 | 8114.4661 | 6865.4259
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 4193.4333 | 4068.5455 | 3774.2566 | 5049.391 | 4867.7334 | 4430.0725 | 5878.4833 | 5648.7425 | 5088.0411 | 6416.3784 | 6157.7605 | 5522.9335 | 6979.998 | 6692.5034 | 5983.5399 | 7968.7311 | 7633.0333 | 6800.4668
TOTAL | 7434.3858 | 7123.6163 | 6371.7953 | 9576.0105 | 9134.7331 | 8058.0397 | 11640.1765 | 11079.9795 | 9705.8876 | 12990.5418 | 12354.8692 | 10791.9536 | 14420.201 | 13705.9809 | 11946.6681 | 16971.3767 | 16119.341 | 14015.852
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 618.4308 | 601.0375 | 552.4714 | 748.6559 | 725.1401 | 658.4803 | 868.3908 | 839.7986 | 758.15 | 944.0931 | 912.4503 | 821.8194 | 1022.2804 | 987.5732 | 887.9399 | 1157.4646 | 1117.6022 | 1002.8661
TOTAL | 1059.3648 | 1018.987 | 906.2213 | 1364.5059 | 1308.8877 | 1152.5607 | 1652.2735 | 1582.82 | 1387.0387 | 1838.513 | 1760.2469 | 1539.3891 | 2034.5255 | 1947.0532 | 1700.0379 | 2382.2812 | 2278.573 | 1985.5046
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'C Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 30
CONDUCTOR
Wind on Conductor | 3106.5147 | 2921.2078 | 2471.5533 | 4338.8511 | 4080.034 | 3452.0042 | 5522.6928 | 5193.2583 | 4393.8726 | 6301.4609 | 5925.5721 | 5013.4631 | 7131.5764 | 6706.1703 | 5673.9057 | 8629.2075 | 8114.4661 | 6865.4259
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 8315.1159 | 8067.4771 | 7483.9347 | 10012.3856 | 9652.1785 | 8784.3453 | 11656.3841 | 11200.8335 | 10089.0243 | 12722.9708 | 12210.16 | 10951.368 | 13840.5663 | 13270.4962 | 11864.6997 | 15801.1149 | 15135.4633 | 13484.5758
TOTAL | 11556.0683 | 11122.5479 | 10081.4733 | 14539.0051 | 13919.1782 | 12412.3125 | 17418.0773 | 16632.0705 | 14706.8708 | 19297.1342 | 18407.2687 | 16220.3881 | 21280.7693 | 20283.9737 | 17827.8279 | 24803.7605 | 23621.771 | 20699.9609
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 1226.28 | 1191.7911 | 1095.4899 | 1484.5022 | 1437.8728 | 1305.6939 | 1721.9232 | 1665.2281 | 1503.3279 | 1872.0326 | 1809.2884 | 1629.5771 | 2027.0692 | 1958.2487 | 1760.687 | 2295.1246 | 2216.0819 | 1988.5728
TOTAL | 1667.214 | 1609.7406 | 1449.2398 | 2100.3522 | 2021.6205 | 1799.7743 | 2505.8059 | 2408.2494 | 2132.2165 | 2766.4524 | 2657.0849 | 2347.1469 | 3039.3144 | 2917.7287 | 2572.7849 | 3519.9413 | 3377.0527 | 2971.2113
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'D'Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 60
CONDUCTOR
Wind on Conductor | 3106.5147 | 2921.2078 | 2471.5533 | 4338.8511 | 4080.034 | 3452.0042 | 5522.6928 | 5193.2583 | 4393.8726 | 6301.4609 | 5925.5721 | 5013.4631 | 7131.5764 | 6706.1703 | 5673.9057 | 8629.2075 | 8114.4661 | 6865.4259
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 16063.5703 | 15585.169 | 14457.8516 | 19342.4437 | 18646.5771 | 16970.0519 | 22518.4049 | 21638.3488 | 19490.4984 | 24578.8922 | 23588.2178 | 21156.4185 | 26737.9208 | 25636.6301 | 22920.8397 | 30525.4099 | 29239.4698 | 26050.2
TOTAL | 19304.5227 | 18640.2397 | 17055.3902 | 23869.0632 | 22913.5767 | 20598.0191 | 28280.0981 | 27069.5857 | 24108.3448 | 31153.0555 | 29785.3264 | 26425.4385 | 34178.1238 | 32650.1075 | 28883.9679 | 39528.0555 | 37725.7775 | 33265.5852
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 2368.9911 | 2302.3636 | 2116.324 | 2867.838 | 2777.757 | 2522.4069 | 3326.5002 | 3216.9737 | 2904.2064 | 3616.4892 | 3495.2767 | 3148.1013 | 3915.997 | 3783.046 | 3401.3861 | 4433.8403 | 4281.1415 | 3841.6277
TOTAL | 2809.9251 | 2720.3131 | 2470.0739 | 3483.688 | 3361.5046 | 3016.4873 | 4110.3829 | 3959.995 | 3533.0951 | 4510.9091 | 4343.0733 | 3865.6711 | 4928.2422 | 4742.526 | 4213.484 | 5658.6569 | 5442.1123 | 4824.2662
QUAD ACSR MOOSE
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
A' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 2
CONDUCTOR
Wind on Conductor | 4142.0196 | 3894.9437 | 3295.4044 | 5785.1348 | 5440.0453 | 4602.6723 | 7363.5904 | 6924.3444 | 5858.4968 | 8401.9479 | 7900.7628 | 6684.6174 | 9508.7686 | 8941.5604 | 7565.2076 | 11505.61 | 10819.2881 | 9153.9012
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 747.5946 | 725.3299 | 672.8648 | 900.1925 | 867.807 | 789.782 | 1048.0009 | 1007.0434 | 907.0829 | 1143.8955 | 1097.7898 | 984.6144 | 1244.3762 | 1193.1224 | 1066.7302 | 1420.645 | 1360.7976 | 1212.3698
TOTAL | 5024.0519 | 4754.1366 | 4094.2546 | 6873.0957 | 6494.8181 | 5568.4173 | 8650.5917 | 8169.3664 | 6989.5536 | 9818.5458 | 9270.0891 | 7924.7889 | 11061.7713 | 10441.9899 | 8921.1603 | 13299.6931 | 12551.9273 | 10716.2302
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 82.6892 | 80.3636 | 73.8699 | 100.1013 | 96.9571 | 88.0441 | 116.1109 | 112.2879 | 101.3708 | 126.2329 | 122.002 | 109.8839 | 136.6871 | 132.0465 | 118.7247 | 154.7624 | 149.4324 | 134.0913
TOTAL | 523.6232 | 498.3131 | 427.6198 | 715.9513 | 680.7047 | 582.1245 | 899.9935 | 855.3092 | 730.2594 | 1020.6527 | 969.7985 | 827.4536 | 1148.9323 | 1091.5265 | 930.8227 | 1379.579 | 1310.4032 | 1116.7298
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
B' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 15
CONDUCTOR
Wind on Conductor | 4142.0196 | 3894.9437 | 3295.4044 | 5785.1348 | 5440.0453 | 4602.6723 | 7363.5904 | 6924.3444 | 5858.4968 | 8401.9479 | 7900.7628 | 6684.6174 | 9508.7686 | 8941.5604 | 7565.2076 | 11505.61 | 10819.2881 | 9153.9012
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 5591.2444 | 5424.7274 | 5032.3422 | 6732.5214 | 6490.3112 | 5906.7633 | 7837.9777 | 7531.6567 | 6784.0548 | 8555.1712 | 8210.3473 | 7363.9113 | 9306.664 | 8923.3379 | 7978.0531 | 10624.9747 | 10177.3777 | 9067.2891
TOTAL | 9867.7018 | 9453.5341 | 8453.7319 | 12705.4246 | 12117.3222 | 10685.3986 | 15440.5685 | 14693.9797 | 12866.5254 | 17229.8215 | 16382.6467 | 14304.0858 | 19124.0591 | 18172.2054 | 15832.4832 | 22504.0228 | 21368.5075 | 18571.1495
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 618.4308 | 601.0375 | 552.4714 | 748.6559 | 725.1401 | 658.4803 | 868.3908 | 839.7986 | 758.15 | 944.0931 | 912.4503 | 821.8194 | 1022.2804 | 987.5732 | 887.9399 | 1157.4646 | 1117.6022 | 1002.8661
TOTAL | 1059.3648 | 1018.987 | 906.2213 | 1364.5059 | 1308.8877 | 1152.5607 | 1652.2735 | 1582.82 | 1387.0387 | 1838.513 | 1760.2469 | 1539.3891 | 2034.5255 | 1947.0532 | 1700.0379 | 2382.2812 | 2278.573 | 1985.5046
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'C' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 30
CONDUCTOR
Wind on Conductor | 4142.0196 | 3894.9437 | 3295.4044 | 5785.1348 | 5440.0453 | 4602.6723 | 7363.5904 | 6924.3444 | 5858.4968 | 8401.9479 | 7900.7628 | 6684.6174 | 9508.7686 | 8941.5604 | 7565.2076 | 11505.61 | 10819.2881 | 9153.9012
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 11086.8211 | 10756.6361 | 9978.5796 | 13349.8475 | 12869.5714 | 11712.4603 | 15541.8455 | 14934.4447 | 13452.0325 | 16963.9611 | 16280.2133 | 14601.8241 | 18454.0884 | 17693.995 | 15819.5996 | 21068.1532 | 20180.6177 | 17979.4344
TOTAL | 15363.2785 | 14785.4428 | 13399.9693 | 19322.7507 | 18496.5824 | 16491.0956 | 23144.4362 | 22096.7677 | 19534.5031 | 25638.6114 | 24452.5127 | 21541.9985 | 28271.4835 | 26942.8625 | 23674.0297 | 32947.2013 | 31371.7474 | 27483.2948
GROUND WIRE
Wind on Ground Wire | 357.8799 | 336.532 | 284.7304 | 499.8488 | 470.0322 | 397.6813 | 636.2309 | 598.279 | 506.1874 | 725.9473 | 682.6438 | 577.5661 | 821.5792 | 772.5711 | 653.6511 | 994.1108 | 934.811 | 790.9178
Deviation Load | 53.4486 | 53.2201 | 50.0882 | 74.6514 | 74.3322 | 69.9579 | 95.0197 | 94.6135 | 89.0456 | 108.4187 | 107.9552 | 101.6022 | 122.7011 | 122.1766 | 114.9866 | 148.4684 | 147.8336 | 139.1338
TOTAL | 411.3285 | 389.7521 | 334.8186 | 574.5001 | 544.3645 | 467.6392 | 731.2506 | 692.8926 | 595.233 | 834.366 | 790.599 | 679.1683 | 944.2803 | 894.7476 | 768.6377 | 1142.5791 | 1082.6446 | 930.0516
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'D' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 60
CONDUCTOR
Wind on Conductor | 4142.0196 | 3894.9437 | 3295.4044 | 5785.1348 | 5440.0453 | 4602.6723 | 7363.5904 | 6924.3444 | 5858.4968 | 8401.9479 | 7900.7628 | 6684.6174 | 9508.7686 | 8941.5604 | 7565.2076 | 11505.61 | 10819.2881 | 9153.9012
Wind on Insulator | 134.4377 | 133.863 | 125.9853 | 187.7684 | 186.9657 | 175.963 | 239.0004 | 237.9787 | 223.9739 | 272.7024 | 271.5366 | 255.557 | 308.6265 | 307.3071 | 289.2225 | 373.4381 | 371.8416 | 349.9593
Deviation Load | 21418.0937 | 20780.2253 | 19277.1354 | 25789.9249 | 24862.1028 | 22626.7359 | 30024.5398 | 28851.1317 | 25987.3311 | 32771.8562 | 31450.957 | 28208.5579 | 35650.5611 | 34182.1734 | 30561.1196 | 40700.5466 | 38985.9597 | 34733.6001
TOTAL | 25694.5511 | 24809.032 | 22698.5252 | 31762.8281 | 30489.1138 | 27405.3711 | 37627.1306 | 36013.4547 | 32069.8018 | 41446.5066 | 39623.2564 | 35148.7324 | 45467.9562 | 43431.041 | 38415.5497 | 52579.5947 | 50177.0894 | 44237.4605
GROUND WIRE
Wind on Ground Wire | 440.934 | 417.9495 | 353.7499 | 615.85 | 583.7476 | 494.0804 | 783.8827 | 743.0213 | 628.8887 | 894.4198 | 847.7965 | 717.5697 | 1012.2452 | 959.48 | 812.0979 | 1224.8167 | 1160.9708 | 982.6385
Deviation Load | 2368.9911 | 2302.3636 | 2116.324 | 2867.838 | 2777.757 | 2522.4069 | 3326.5002 | 3216.9737 | 2904.2064 | 3616.4892 | 3495.2767 | 3148.1013 | 3915.997 | 3783.046 | 3401.3861 | 4433.8403 | 4281.1415 | 3841.6277
TOTAL | 2809.9251 | 2720.3131 | 2470.0739 | 3483.688 | 3361.5046 | 3016.4873 | 4110.3829 | 3959.995 | 3533.0951 | 4510.9091 | 4343.0733 | 3865.6711 | 4928.2422 | 4742.526 | 4213.484 | 5658.6569 | 5442.1123 | 4824.2662
TOWER LOADING CALCULATIONS FOR 400 KV SC LINE
TWIN ACSR MOOSE
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
A' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 2
CONDUCTOR
Wind on Conductor | 1928.9738 | 1768.394 | 1476.2687 | 2694.1866 | 2469.9056 | 2061.896 | 3429.2868 | 3143.8115 | 2624.4777 | 3912.8588 | 3587.1279 | 2994.5616 | 4428.3146 | 4059.674 | 3389.0467 | 5358.2606 | 4912.2055 | 4100.7465
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 361.0117 | 346.8376 | 322.116 | 431.4821 | 410.5253 | 372.971 | 500.4473 | 473.6931 | 424.9548 | 545.4281 | 515.1853 | 459.6766 | 592.702 | 558.9709 | 496.6828 | 675.885 | 636.3369 | 562.7489
TOTAL | 2412.9954 | 2239.6273 | 1914.3485 | 3297.4758 | 3054.1737 | 2596.8329 | 4148.4183 | 3838.6526 | 3255.5904 | 4707.8082 | 4354.6458 | 3689.4669 | 5303.4084 | 4904.2181 | 4151.9456 | 6375.8398 | 5894.086 | 4985.6169
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 80.4103 | 77.5245 | 71.2419 | 97.0205 | 93.087 | 84.367 | 112.365 | 107.5636 | 96.8229 | 122.0875 | 116.7653 | 104.8155 | 132.1403 | 126.2957 | 113.136 | 149.5402 | 142.8181 | 127.6323
TOTAL | 498.8211 | 467.4374 | 398.8328 | 681.4125 | 637.676 | 541.9113 | 856.2066 | 800.7421 | 679.2067 | 970.8198 | 907.6905 | 769.3227 | 1092.6794 | 1021.4126 | 865.1812 | 1311.7926 | 1225.9095 | 1037.607
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'B' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 15
CONDUCTOR
Wind on Conductor | 1928.9738 | 1768.394 | 1476.2687 | 2694.1866 | 2469.9056 | 2061.896 | 3429.2868 | 3143.8115 | 2624.4777 | 3912.8588 | 3587.1279 | 2994.5616 | 4428.3146 | 4059.674 | 3389.0467 | 5358.2606 | 4912.2055 | 4100.7465
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 2699.9989 | 2593.9914 | 2409.099 | 3227.0455 | 3070.3103 | 2789.4426 | 3742.8349 | 3542.7412 | 3178.2286 | 4079.2454 | 3853.0607 | 3437.9122 | 4432.8063 | 4180.532 | 3714.6804 | 5054.9304 | 4759.1504 | 4208.7875
TOTAL | 4751.9826 | 4486.7811 | 4001.3315 | 6093.0393 | 5713.9587 | 5013.3045 | 7390.8059 | 6907.7007 | 6008.8642 | 8241.6256 | 7692.5211 | 6667.7025 | 9143.5127 | 8525.7792 | 7369.9432 | 10754.8851 | 10016.8996 | 8631.6555
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 601.3869 | 579.8043 | 532.817 | 725.614 | 696.1955 | 630.9788 | 840.3759 | 804.4659 | 724.1367 | 913.0896 | 873.2851 | 783.9132 | 988.2747 | 944.5631 | 846.1418 | 1118.4083 | 1068.1338 | 954.5591
TOTAL | 1019.7977 | 969.7172 | 860.4079 | 1310.0061 | 1240.7846 | 1088.5231 | 1584.2174 | 1497.6444 | 1306.5205 | 1761.8219 | 1664.2103 | 1448.4204 | 1948.8138 | 1839.6799 | 1598.187 | 2280.6607 | 2151.2252 | 1864.5338
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'C' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 30
CONDUCTOR
Wind on Conductor | 1928.9738 | 1768.394 | 1476.2687 | 2694.1866 | 2469.9056 | 2061.896 | 3429.2868 | 3143.8115 | 2624.4777 | 3912.8588 | 3587.1279 | 2994.5616 | 4428.3146 | 4059.674 | 3389.0467 | 5358.2606 | 4912.2055 | 4100.7465
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 5353.8001 | 5143.5989 | 4776.9776 | 6398.8754 | 6088.0867 | 5531.157 | 7421.6288 | 7024.8652 | 6302.0768 | 8088.6938 | 7640.1944 | 6817.0008 | 8789.7661 | 8289.534 | 7365.8015 | 10023.3695 | 9436.8705 | 8345.5614
TOTAL | 7405.7838 | 7036.3886 | 6369.2101 | 9264.8691 | 8731.7351 | 7755.019 | 11069.5998 | 10389.8246 | 9132.7124 | 12251.074 | 11479.6548 | 10046.7911 | 13500.4724 | 12634.7812 | 11021.0643 | 15723.3243 | 14694.6196 | 12768.4294
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 1192.4838 | 1149.6881 | 1056.5174 | 1438.8126 | 1380.4788 | 1251.1614 | 1666.3727 | 1595.1672 | 1435.8832 | 1810.5559 | 1731.628 | 1554.4135 | 1959.6397 | 1872.9644 | 1677.8059 | 2217.6804 | 2117.9915 | 1892.7855
TOTAL | 1610.8947 | 1539.601 | 1384.1083 | 2023.2046 | 1925.0679 | 1708.7057 | 2410.2142 | 2288.3457 | 2018.267 | 2659.2883 | 2522.5532 | 2218.9206 | 2920.1788 | 2768.0812 | 2429.8511 | 3379.9327 | 3201.0829 | 2802.7601
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'D' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 60
CONDUCTOR
Wind on Conductor | 1928.9738 | 1768.394 | 1476.2687 | 2694.1866 | 2469.9056 | 2061.896 | 3429.2868 | 3143.8115 | 2624.4777 | 3912.8588 | 3587.1279 | 2994.5616 | 4428.3146 | 4059.674 | 3389.0467 | 5358.2606 | 4912.2055 | 4100.7465
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 10342.7475 | 9936.6701 | 9228.412 | 12361.6779 | 11761.2803 | 10685.3749 | 14337.4858 | 13570.9974 | 12174.6775 | 15626.1565 | 14759.7222 | 13169.4343 | 16980.5241 | 16014.1499 | 14229.6358 | 19363.663 | 18230.6338 | 16122.3866
TOTAL | 12394.7312 | 11829.4598 | 10820.6445 | 15227.6717 | 14404.9287 | 12909.2368 | 17985.4568 | 16935.9568 | 15005.3131 | 19788.5366 | 18599.1826 | 16399.2246 | 21691.2305 | 20359.3972 | 17884.8986 | 25063.6177 | 23488.3829 | 20545.2546
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 2303.7019 | 2221.0268 | 2041.0349 | 2779.5726 | 2666.8803 | 2417.0583 | 3219.1848 | 3081.6264 | 2773.9134 | 3497.7254 | 3345.2483 | 3002.8962 | 3785.7331 | 3618.2894 | 3241.2721 | 4284.2295 | 4091.6455 | 3656.5807
TOTAL | 2722.1127 | 2610.9397 | 2368.6258 | 3363.9646 | 3211.4694 | 2874.6026 | 3963.0263 | 3774.8049 | 3356.2972 | 4346.4578 | 4136.1736 | 3667.4034 | 4746.2722 | 4513.4062 | 3993.3173 | 5446.4819 | 5174.7368 | 4566.5554
TRIPPLE ACSR MOOSE
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
A' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 2
CONDUCTOR
Wind on Conductor | 2893.4607 | 2652.591 | 2214.4031 | 4041.2799 | 3704.8585 | 3092.844 | 5143.9302 | 4715.7173 | 3936.7166 | 5869.2881 | 5380.6919 | 4491.8424 | 6642.4719 | 6089.511 | 5083.57 | 8037.3909 | 7368.3083 | 6151.1197
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 541.5175 | 520.2564 | 483.174 | 647.2231 | 615.7879 | 559.4565 | 750.6709 | 710.5397 | 637.4323 | 818.1421 | 772.778 | 689.515 | 889.053 | 838.4564 | 745.0242 | 1013.8276 | 954.5053 | 844.1233
TOTAL | 3557.9881 | 3297.2431 | 2813.5409 | 4860.3101 | 4494.3892 | 3814.2664 | 6113.2853 | 5647.4049 | 4780.3067 | 6936.9516 | 6405.8024 | 5416.586 | 7813.9167 | 7213.5406 | 6094.8103 | 9392.9126 | 8668.3572 | 7317.3646
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 80.4103 | 77.5245 | 71.2419 | 97.0205 | 93.087 | 84.367 | 112.365 | 107.5636 | 96.8229 | 122.0875 | 116.7653 | 104.8155 | 132.1403 | 126.2957 | 113.136 | 149.5402 | 142.8181 | 127.6323
TOTAL | 498.8211 | 467.4374 | 398.8328 | 681.4125 | 637.676 | 541.9113 | 856.2066 | 800.7421 | 679.2067 | 970.8198 | 907.6905 | 769.3227 | 1092.6794 | 1021.4126 | 865.1812 | 1311.7926 | 1225.9095 | 1037.607
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'B' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 15
CONDUCTOR
Wind on Conductor | 2893.4607 | 2652.591 | 2214.4031 | 4041.2799 | 3704.8585 | 3092.844 | 5143.9302 | 4715.7173 | 3936.7166 | 5869.2881 | 5380.6919 | 4491.8424 | 6642.4719 | 6089.511 | 5083.57 | 8037.3909 | 7368.3083 | 6151.1197
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 4049.9984 | 3890.9871 | 3613.6484 | 4840.5683 | 4605.4654 | 4184.1639 | 5614.2523 | 5314.1118 | 4767.3429 | 6118.8681 | 5779.591 | 5156.8683 | 6649.2095 | 6270.798 | 5572.0205 | 7582.3956 | 7138.7256 | 6313.1812
TOTAL | 7066.469 | 6667.9738 | 5944.0153 | 9053.6553 | 8484.0666 | 7438.9738 | 10976.8667 | 10250.977 | 8910.2173 | 12237.6776 | 11412.6154 | 9883.9394 | 13574.0731 | 12645.8822 | 10921.8067 | 15961.4806 | 14852.5775 | 12786.4225
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 601.3869 | 579.8043 | 532.817 | 725.614 | 696.1955 | 630.9788 | 840.3759 | 804.4659 | 724.1367 | 913.0896 | 873.2851 | 783.9132 | 988.2747 | 944.5631 | 846.1418 | 1118.4083 | 1068.1338 | 954.5591
TOTAL | 1019.7977 | 969.7172 | 860.4079 | 1310.0061 | 1240.7846 | 1088.5231 | 1584.2174 | 1497.6444 | 1306.5205 | 1761.8219 | 1664.2103 | 1448.4204 | 1948.8138 | 1839.6799 | 1598.187 | 2280.6607 | 2151.2252 | 1864.5338
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'C Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 30
CONDUCTOR
Wind on Conductor | 2893.4607 | 2652.591 | 2214.4031 | 4041.2799 | 3704.8585 | 3092.844 | 5143.9302 | 4715.7173 | 3936.7166 | 5869.2881 | 5380.6919 | 4491.8424 | 6642.4719 | 6089.511 | 5083.57 | 8037.3909 | 7368.3083 | 6151.1197
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 8030.7001 | 7715.3984 | 7165.4663 | 9598.313 | 9132.13 | 8296.7356 | 11132.4432 | 10537.2977 | 9453.1152 | 12133.0407 | 11460.2916 | 10225.5012 | 13184.6491 | 12434.301 | 11048.7022 | 15035.0543 | 14155.3057 | 12518.3421
TOTAL | 11047.1707 | 10492.3851 | 9495.8332 | 13811.4001 | 13010.7312 | 11551.5455 | 16495.0576 | 15474.1629 | 13595.9897 | 18251.8502 | 17093.316 | 14952.5723 | 20109.5128 | 18809.3852 | 16398.4884 | 23414.1393 | 21869.1576 | 18991.5834
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 1192.4838 | 1149.6881 | 1056.5174 | 1438.8126 | 1380.4788 | 1251.1614 | 1666.3727 | 1595.1672 | 1435.8832 | 1810.5559 | 1731.628 | 1554.4135 | 1959.6397 | 1872.9644 | 1677.8059 | 2217.6804 | 2117.9915 | 1892.7855
TOTAL | 1610.8947 | 1539.601 | 1384.1083 | 2023.2046 | 1925.0679 | 1708.7057 | 2410.2142 | 2288.3457 | 2018.267 | 2659.2883 | 2522.5532 | 2218.9206 | 2920.1788 | 2768.0812 | 2429.8511 | 3379.9327 | 3201.0829 | 2802.7601
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'D'Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 60
CONDUCTOR
Wind on Conductor | 2893.4607 | 2652.591 | 2214.4031 | 4041.2799 | 3704.8585 | 3092.844 | 5143.9302 | 4715.7173 | 3936.7166 | 5869.2881 | 5380.6919 | 4491.8424 | 6642.4719 | 6089.511 | 5083.57 | 8037.3909 | 7368.3083 | 6151.1197
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 15514.1213 | 14905.0052 | 13842.618 | 18542.5169 | 17641.9204 | 16028.0623 | 21506.2287 | 20356.496 | 18262.0163 | 23439.2347 | 22139.5833 | 19754.1515 | 25470.7861 | 24021.2249 | 21344.4537 | 29045.4945 | 27345.9507 | 24183.5799
TOTAL | 18530.5919 | 17681.9918 | 16172.9849 | 22755.604 | 21520.5217 | 19282.8722 | 26868.8431 | 25293.3613 | 22404.8907 | 29558.0443 | 27772.6077 | 24481.2225 | 32395.6498 | 30396.3091 | 26694.2399 | 37424.5795 | 35059.8026 | 30656.8211
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 2303.7019 | 2221.0268 | 2041.0349 | 2779.5726 | 2666.8803 | 2417.0583 | 3219.1848 | 3081.6264 | 2773.9134 | 3497.7254 | 3345.2483 | 3002.8962 | 3785.7331 | 3618.2894 | 3241.2721 | 4284.2295 | 4091.6455 | 3656.5807
TOTAL | 2722.1127 | 2610.9397 | 2368.6258 | 3363.9646 | 3211.4694 | 2874.6026 | 3963.0263 | 3774.8049 | 3356.2972 | 4346.4578 | 4136.1736 | 3667.4034 | 4746.2722 | 4513.4062 | 3993.3173 | 5446.4819 | 5174.7368 | 4566.5554
QUAD ACSR MOOSE
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
A' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 2
CONDUCTOR
Wind on Conductor | 3857.9477 | 3536.788 | 2952.5375 | 5388.3732 | 4939.8113 | 4123.792 | 6858.5736 | 6287.623 | 5248.9555 | 7825.7175 | 7174.2558 | 5989.1233 | 8856.6291 | 8119.3479 | 6778.0933 | 10716.5213 | 9824.411 | 8201.4929
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 722.0233 | 693.6752 | 644.232 | 862.9641 | 821.0506 | 745.942 | 1000.8945 | 947.3862 | 849.9097 | 1090.8561 | 1030.3707 | 919.3533 | 1185.404 | 1117.9418 | 993.3655 | 1351.7701 | 1272.6737 | 1125.4978
TOTAL | 4702.9809 | 4354.8589 | 3712.7332 | 6423.1445 | 5934.6046 | 5031.6999 | 8078.1523 | 7456.1572 | 6305.023 | 9166.095 | 8456.959 | 7143.7052 | 10324.425 | 9522.863 | 8037.6751 | 12409.9854 | 11442.6284 | 9649.1123
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 80.4103 | 77.5245 | 71.2419 | 97.0205 | 93.087 | 84.367 | 112.365 | 107.5636 | 96.8229 | 122.0875 | 116.7653 | 104.8155 | 132.1403 | 126.2957 | 113.136 | 149.5402 | 142.8181 | 127.6323
TOTAL | 498.8211 | 467.4374 | 398.8328 | 681.4125 | 637.676 | 541.9113 | 856.2066 | 800.7421 | 679.2067 | 970.8198 | 907.6905 | 769.3227 | 1092.6794 | 1021.4126 | 865.1812 | 1311.7926 | 1225.9095 | 1037.607
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
B' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 15
CONDUCTOR
Wind on Conductor | 3857.9477 | 3536.788 | 2952.5375 | 5388.3732 | 4939.8113 | 4123.792 | 6858.5736 | 6287.623 | 5248.9555 | 7825.7175 | 7174.2558 | 5989.1233 | 8856.6291 | 8119.3479 | 6778.0933 | 10716.5213 | 9824.411 | 8201.4929
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 5399.9978 | 5187.9828 | 4818.1979 | 6454.091 | 6140.6205 | 5578.8852 | 7485.6697 | 7085.4824 | 6356.4572 | 8158.4908 | 7706.1213 | 6875.8245 | 8865.6126 | 8361.064 | 7429.3607 | 10109.8608 | 9518.3008 | 8417.5749
TOTAL | 9380.9553 | 8849.1665 | 7886.6991 | 12014.2714 | 11254.1746 | 9864.6431 | 14562.9275 | 13594.2534 | 11811.5705 | 16233.7297 | 15132.7097 | 13100.1763 | 18004.6336 | 16765.9852 | 14473.6702 | 21168.0761 | 19688.2555 | 16941.1894
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 601.3869 | 579.8043 | 532.817 | 725.614 | 696.1955 | 630.9788 | 840.3759 | 804.4659 | 724.1367 | 913.0896 | 873.2851 | 783.9132 | 988.2747 | 944.5631 | 846.1418 | 1118.4083 | 1068.1338 | 954.5591
TOTAL | 1019.7977 | 969.7172 | 860.4079 | 1310.0061 | 1240.7846 | 1088.5231 | 1584.2174 | 1497.6444 | 1306.5205 | 1761.8219 | 1664.2103 | 1448.4204 | 1948.8138 | 1839.6799 | 1598.187 | 2280.6607 | 2151.2252 | 1864.5338
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'C' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 30
CONDUCTOR
Wind on Conductor | 3857.9477 | 3536.788 | 2952.5375 | 5388.3732 | 4939.8113 | 4123.792 | 6858.5736 | 6287.623 | 5248.9555 | 7825.7175 | 7174.2558 | 5989.1233 | 8856.6291 | 8119.3479 | 6778.0933 | 10716.5213 | 9824.411 | 8201.4929
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 10707.6001 | 10287.1979 | 9553.9551 | 12797.7507 | 12176.1733 | 11062.3141 | 14843.2575 | 14049.7303 | 12604.1537 | 16177.3876 | 15280.3888 | 13634.0016 | 17579.5321 | 16579.068 | 14731.603 | 20046.7391 | 18873.7409 | 16691.1228
TOTAL | 14688.5577 | 13948.3815 | 12622.4563 | 18357.9311 | 17289.7274 | 15348.072 | 21920.5154 | 20558.5013 | 18059.2669 | 24252.6265 | 22706.9772 | 19858.3535 | 26718.5531 | 24983.9892 | 21775.9125 | 31104.9544 | 29043.6956 | 25214.7373
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 1192.4838 | 1149.6881 | 1056.5174 | 1438.8126 | 1380.4788 | 1251.1614 | 1666.3727 | 1595.1672 | 1435.8832 | 1810.5559 | 1731.628 | 1554.4135 | 1959.6397 | 1872.9644 | 1677.8059 | 2217.6804 | 2117.9915 | 1892.7855
TOTAL | 1610.8947 | 1539.601 | 1384.1083 | 2023.2046 | 1925.0679 | 1708.7057 | 2410.2142 | 2288.3457 | 2018.267 | 2659.2883 | 2522.5532 | 2218.9206 | 2920.1788 | 2768.0812 | 2429.8511 | 3379.9327 | 3201.0829 | 2802.7601
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'D' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 60
CONDUCTOR
Wind on Conductor | 3857.9477 | 3536.788 | 2952.5375 | 5388.3732 | 4939.8113 | 4123.792 | 6858.5736 | 6287.623 | 5248.9555 | 7825.7175 | 7174.2558 | 5989.1233 | 8856.6291 | 8119.3479 | 6778.0933 | 10716.5213 | 9824.411 | 8201.4929
Wind on Insulator | 123.0099 | 124.3957 | 115.9638 | 171.8072 | 173.7428 | 161.9659 | 218.6842 | 221.1479 | 206.1578 | 249.5214 | 252.3325 | 235.2286 | 282.3918 | 285.5733 | 266.2162 | 341.6941 | 345.5436 | 322.1216
Deviation Load | 20685.495 | 19873.3402 | 18456.824 | 24723.3559 | 23522.5606 | 21370.7497 | 28674.9716 | 27141.9947 | 24349.3551 | 31252.313 | 29519.4443 | 26338.8686 | 33961.0482 | 32028.2999 | 28459.2716 | 38727.326 | 36461.2676 | 32244.7732
TOTAL | 24666.4526 | 23534.5239 | 21525.3252 | 30283.5362 | 28636.1146 | 25656.5077 | 35752.2294 | 33650.7657 | 29804.4684 | 39327.5519 | 36946.0327 | 32563.2205 | 43100.0691 | 40433.2211 | 35503.5811 | 49785.5413 | 46631.2223 | 40768.3877
GROUND WIRE
Wind on Ground Wire | 418.4108 | 389.9129 | 327.5909 | 584.392 | 544.5891 | 457.5443 | 743.8415 | 693.1785 | 582.3838 | 848.7324 | 790.9252 | 664.5071 | 960.5391 | 895.1168 | 752.0452 | 1162.2524 | 1083.0914 | 909.9747
Deviation Load | 2303.7019 | 2221.0268 | 2041.0349 | 2779.5726 | 2666.8803 | 2417.0583 | 3219.1848 | 3081.6264 | 2773.9134 | 3497.7254 | 3345.2483 | 3002.8962 | 3785.7331 | 3618.2894 | 3241.2721 | 4284.2295 | 4091.6455 | 3656.5807
TOTAL | 2722.1127 | 2610.9397 | 2368.6258 | 3363.9646 | 3211.4694 | 2874.6026 | 3963.0263 | 3774.8049 | 3356.2972 | 4346.4578 | 4136.1736 | 3667.4034 | 4746.2722 | 4513.4062 | 3993.3173 | 5446.4819 | 5174.7368 | 4566.5554
TOWER LOADING CALCULATIONS FOR 765 KV SC LINE
TWIN ACSR MOOSE
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
A' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 2
CONDUCTOR
Wind on Conductor | 1973.8823 | 1813.1634 | 1529.963 | 2756.9099 | 2532.4349 | 2136.8905 | 3509.124 | 3223.4017 | 2719.9342 | 4003.954 | 3677.9413 | 3103.4786 | 4531.4101 | 4162.4505 | 3512.3117 | 5483.0063 | 5036.5651 | 4249.8972
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 365.0319 | 350.7548 | 326.5343 | 437.3625 | 416.3539 | 379.7911 | 507.9078 | 481.1618 | 433.8952 | 553.838 | 523.642 | 469.9064 | 602.0613 | 568.4155 | 508.2054 | 686.8283 | 647.4285 | 576.4272
TOTAL | 2552.361 | 2378.1217 | 2057.1542 | 3492.3925 | 3247.9656 | 2796.938 | 4396.4929 | 4085.3698 | 3510.553 | 4990.7618 | 4636.0879 | 3980.411 | 5623.478 | 5222.6097 | 4481.1622 | 6762.7425 | 6279.0034 | 5383.7049
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 81.5282 | 78.9346 | 72.6547 | 98.5345 | 95.0138 | 86.3496 | 114.2073 | 109.9185 | 99.2787 | 124.1269 | 119.3769 | 107.5541 | 134.3778 | 129.1647 | 116.1572 | 152.1108 | 146.1193 | 131.126
TOTAL | 510.9841 | 482.773 | 414.3312 | 698.353 | 659.0525 | 563.5672 | 877.6844 | 827.8534 | 706.7036 | 995.2637 | 938.5494 | 800.6334 | 1120.2728 | 1056.25 | 900.5385 | 1345.0437 | 1267.8925 | 1080.2274
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'B' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 15
CONDUCTOR
Wind on Conductor | 1973.8823 | 1813.1634 | 1529.963 | 2756.9099 | 2532.4349 | 2136.8905 | 3509.124 | 3223.4017 | 2719.9342 | 4003.954 | 3677.9413 | 3103.4786 | 4531.4101 | 4162.4505 | 3512.3117 | 5483.0063 | 5036.5651 | 4249.8972
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 2730.0661 | 2623.2878 | 2442.143 | 3271.0254 | 3113.9022 | 2840.4501 | 3798.632 | 3598.5996 | 3245.0936 | 4142.1433 | 3916.3078 | 3514.4203 | 4502.8041 | 4251.1682 | 3800.8581 | 5136.775 | 4842.1047 | 4311.0874
TOTAL | 4917.3952 | 4650.6548 | 4172.763 | 6326.0554 | 5945.5139 | 5257.597 | 7687.2171 | 7202.8076 | 6321.7513 | 8579.0671 | 8028.7537 | 7024.9249 | 9524.2208 | 8905.3624 | 7773.8148 | 11212.6892 | 10473.6796 | 9118.3651
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 609.7481 | 590.3503 | 543.3827 | 736.9372 | 710.6065 | 645.8068 | 854.1541 | 822.0782 | 742.5035 | 928.3427 | 892.8171 | 804.3951 | 1005.0089 | 966.0202 | 868.7377 | 1137.6335 | 1092.8233 | 980.6886
TOTAL | 1039.204 | 994.1887 | 885.0592 | 1336.7557 | 1274.6452 | 1123.0243 | 1617.6312 | 1540.013 | 1349.9284 | 1799.4795 | 1711.9896 | 1497.4744 | 1990.9039 | 1893.1055 | 1653.119 | 2330.5665 | 2214.5966 | 1929.79
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'C' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 30
CONDUCTOR
Wind on Conductor | 1973.8823 | 1813.1634 | 1529.963 | 2756.9099 | 2532.4349 | 2136.8905 | 3509.124 | 3223.4017 | 2719.9342 | 4003.954 | 3677.9413 | 3103.4786 | 4531.4101 | 4162.4505 | 3512.3117 | 5483.0063 | 5036.5651 | 4249.8972
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 5413.42 | 5201.6905 | 4842.5003 | 6486.0827 | 6174.5247 | 5632.2993 | 7532.2684 | 7135.6262 | 6434.6627 | 8213.4134 | 7765.6065 | 6968.7078 | 8928.564 | 8429.5978 | 7536.6824 | 10185.6584 | 9601.3596 | 8548.4109
TOTAL | 7600.7491 | 7229.0575 | 6573.1202 | 9541.1127 | 9006.1364 | 8049.4462 | 11420.8535 | 10739.8342 | 9511.3204 | 12650.3372 | 11878.0524 | 10479.2124 | 13949.9807 | 13083.7919 | 11509.6392 | 16261.5726 | 15232.9345 | 13355.6886
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 1209.0633 | 1170.5996 | 1077.468 | 1461.2652 | 1409.0543 | 1280.5636 | 1693.6934 | 1630.0904 | 1472.3026 | 1840.8012 | 1770.3578 | 1595.0268 | 1992.8219 | 1915.5116 | 1722.611 | 2255.8018 | 2166.9482 | 1944.5974
TOTAL | 1638.5191 | 1574.438 | 1419.1445 | 2061.0837 | 1973.093 | 1757.7812 | 2457.1705 | 2348.0253 | 2079.7275 | 2711.938 | 2589.5303 | 2288.1061 | 2978.7169 | 2842.5969 | 2506.9923 | 3448.7348 | 3288.7214 | 2893.6988
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'D' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 60
CONDUCTOR
Wind on Conductor | 1973.8823 | 1813.1634 | 1529.963 | 2756.9099 | 2532.4349 | 2136.8905 | 3509.124 | 3223.4017 | 2719.9342 | 4003.954 | 3677.9413 | 3103.4786 | 4531.4101 | 4162.4505 | 3512.3117 | 5483.0063 | 5036.5651 | 4249.8972
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 10457.9243 | 10048.8944 | 9354.9921 | 12530.1496 | 11928.2658 | 10880.7667 | 14551.2251 | 13784.9713 | 12430.8138 | 15867.0962 | 15001.9997 | 13462.5097 | 17248.6611 | 16284.7324 | 14559.7523 | 19677.1811 | 18548.4024 | 16514.2616
TOTAL | 12645.2535 | 12076.2614 | 11085.6121 | 15585.1796 | 14759.8775 | 13297.9136 | 18439.8102 | 17389.1793 | 15507.4715 | 20304.02 | 19114.4457 | 16973.0143 | 22270.0778 | 20938.9265 | 18532.7091 | 25753.0953 | 24179.9773 | 21321.5394
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 2335.7309 | 2261.4248 | 2081.5083 | 2822.9475 | 2722.0839 | 2473.8589 | 3271.9644 | 3149.0928 | 2844.2703 | 3556.1548 | 3420.0686 | 3081.3552 | 3849.8362 | 3700.4843 | 3327.8288 | 4357.8745 | 4186.2224 | 3756.6737
TOTAL | 2765.1867 | 2665.2632 | 2423.1848 | 3422.766 | 3286.1226 | 2951.0765 | 4035.4415 | 3867.0277 | 3451.6952 | 4427.2916 | 4239.2411 | 3774.4345 | 4835.7312 | 4627.5696 | 4112.2101 | 5550.8074 | 5307.9956 | 4705.775
TRIPPLE ACSR MOOSE
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
A' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 2
CONDUCTOR
Wind on Conductor | 2960.8234 | 2719.7452 | 2294.9445 | 4135.3649 | 3798.6524 | 3205.3357 | 5263.686 | 4835.1025 | 4079.9013 | 6005.931 | 5516.9119 | 4655.218 | 6797.1152 | 6243.6758 | 5268.4676 | 8224.5094 | 7554.8477 | 6374.8458
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 547.5478 | 526.1322 | 489.8014 | 656.0438 | 624.5308 | 569.6867 | 761.8617 | 721.7428 | 650.8428 | 830.757 | 785.463 | 704.8596 | 903.0919 | 852.6233 | 762.3081 | 1030.2425 | 971.1428 | 864.6408
TOTAL | 3721.8181 | 3460.0809 | 2985.4028 | 5089.5287 | 4722.36 | 4055.2788 | 6405.0088 | 5937.6515 | 5087.4677 | 7269.6578 | 6736.8796 | 5767.1035 | 8190.2137 | 7588.0427 | 6491.4208 | 9847.6598 | 9121.0002 | 7796.8671
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 81.5282 | 78.9346 | 72.6547 | 98.5345 | 95.0138 | 86.3496 | 114.2073 | 109.9185 | 99.2787 | 124.1269 | 119.3769 | 107.5541 | 134.3778 | 129.1647 | 116.1572 | 152.1108 | 146.1193 | 131.126
TOTAL | 510.9841 | 482.773 | 414.3312 | 698.353 | 659.0525 | 563.5672 | 877.6844 | 827.8534 | 706.7036 | 995.2637 | 938.5494 | 800.6334 | 1120.2728 | 1056.25 | 900.5385 | 1345.0437 | 1267.8925 | 1080.2274
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'B' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 15
CONDUCTOR
Wind on Conductor | 2960.8234 | 2719.7452 | 2294.9445 | 4135.3649 | 3798.6524 | 3205.3357 | 5263.686 | 4835.1025 | 4079.9013 | 6005.931 | 5516.9119 | 4655.218 | 6797.1152 | 6243.6758 | 5268.4676 | 8224.5094 | 7554.8477 | 6374.8458
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 4095.0991 | 3934.9318 | 3663.2145 | 4906.5382 | 4670.8533 | 4260.6752 | 5697.948 | 5397.8995 | 4867.6404 | 6213.2149 | 5874.4617 | 5271.6304 | 6754.2062 | 6376.7523 | 5701.2871 | 7705.1626 | 7263.157 | 6466.6311
TOTAL | 7269.3694 | 6868.8805 | 6158.816 | 9340.0231 | 8768.6825 | 7746.2673 | 11341.0951 | 10613.8082 | 9304.2652 | 12652.1157 | 11825.8783 | 10333.8743 | 14041.3279 | 13112.1717 | 11430.3997 | 16522.5799 | 15413.0145 | 13398.8574
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 609.7481 | 590.3503 | 543.3827 | 736.9372 | 710.6065 | 645.8068 | 854.1541 | 822.0782 | 742.5035 | 928.3427 | 892.8171 | 804.3951 | 1005.0089 | 966.0202 | 868.7377 | 1137.6335 | 1092.8233 | 980.6886
TOTAL | 1039.204 | 994.1887 | 885.0592 | 1336.7557 | 1274.6452 | 1123.0243 | 1617.6312 | 1540.013 | 1349.9284 | 1799.4795 | 1711.9896 | 1497.4744 | 1990.9039 | 1893.1055 | 1653.119 | 2330.5665 | 2214.5966 | 1929.79
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'C Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 30
CONDUCTOR
Wind on Conductor | 2960.8234 | 2719.7452 | 2294.9445 | 4135.3649 | 3798.6524 | 3205.3357 | 5263.686 | 4835.1025 | 4079.9013 | 6005.931 | 5516.9119 | 4655.218 | 6797.1152 | 6243.6758 | 5268.4676 | 8224.5094 | 7554.8477 | 6374.8458
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 8120.13 | 7802.5358 | 7263.7504 | 9729.1241 | 9261.7871 | 8448.449 | 11298.4026 | 10703.4394 | 9651.9941 | 12320.12 | 11648.4097 | 10453.0617 | 13392.846 | 12644.3967 | 11305.0236 | 15278.4876 | 14402.0394 | 12822.6163
TOTAL | 11294.4002 | 10736.4845 | 9759.3519 | 14162.609 | 13359.6162 | 11934.0411 | 16941.5497 | 15919.3481 | 14088.6189 | 18759.0208 | 17599.8263 | 15515.3057 | 20679.9678 | 19379.8161 | 17034.1362 | 24095.905 | 22551.8969 | 19754.8426
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 1209.0633 | 1170.5996 | 1077.468 | 1461.2652 | 1409.0543 | 1280.5636 | 1693.6934 | 1630.0904 | 1472.3026 | 1840.8012 | 1770.3578 | 1595.0268 | 1992.8219 | 1915.5116 | 1722.611 | 2255.8018 | 2166.9482 | 1944.5974
TOTAL | 1638.5191 | 1574.438 | 1419.1445 | 2061.0837 | 1973.093 | 1757.7812 | 2457.1705 | 2348.0253 | 2079.7275 | 2711.938 | 2589.5303 | 2288.1061 | 2978.7169 | 2842.5969 | 2506.9923 | 3448.7348 | 3288.7214 | 2893.6988
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'D'Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 60
CONDUCTOR
Wind on Conductor | 2960.8234 | 2719.7452 | 2294.9445 | 4135.3649 | 3798.6524 | 3205.3357 | 5263.686 | 4835.1025 | 4079.9013 | 6005.931 | 5516.9119 | 4655.218 | 6797.1152 | 6243.6758 | 5268.4676 | 8224.5094 | 7554.8477 | 6374.8458
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 15686.8865 | 15073.3416 | 14032.4882 | 18795.2245 | 17892.3986 | 16321.1501 | 21826.8377 | 20677.457 | 18646.2207 | 23800.6443 | 22502.9996 | 20193.7646 | 25872.9917 | 24427.0986 | 21839.6285 | 29515.7716 | 27822.6036 | 24771.3925
TOTAL | 18861.1568 | 18007.2903 | 16528.0897 | 23228.7094 | 21990.2278 | 19806.7422 | 27469.9848 | 25893.3658 | 23082.8455 | 30239.5451 | 28454.4162 | 25256.0085 | 33160.1135 | 31162.518 | 27568.7411 | 38333.1889 | 35972.4611 | 31703.6188
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 2335.7309 | 2261.4248 | 2081.5083 | 2822.9475 | 2722.0839 | 2473.8589 | 3271.9644 | 3149.0928 | 2844.2703 | 3556.1548 | 3420.0686 | 3081.3552 | 3849.8362 | 3700.4843 | 3327.8288 | 4357.8745 | 4186.2224 | 3756.6737
TOTAL | 2765.1867 | 2665.2632 | 2423.1848 | 3422.766 | 3286.1226 | 2951.0765 | 4035.4415 | 3867.0277 | 3451.6952 | 4427.2916 | 4239.2411 | 3774.4345 | 4835.7312 | 4627.5696 | 4112.2101 | 5550.8074 | 5307.9956 | 4705.775
QUAD ACSR MOOSE
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
A' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 2
CONDUCTOR
Wind on Conductor | 3947.7645 | 3626.3269 | 3059.926 | 5513.8199 | 5064.8698 | 4273.7809 | 7018.248 | 6446.8034 | 5439.8684 | 8007.908 | 7355.8826 | 6206.9573 | 9062.8203 | 8324.9011 | 7024.6235 | 10966.0125 | 10073.1303 | 8499.7944
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 730.0638 | 701.5096 | 653.0685 | 874.7251 | 832.7078 | 759.5823 | 1015.8156 | 962.3237 | 867.7905 | 1107.676 | 1047.284 | 939.8128 | 1204.1226 | 1136.8311 | 1016.4109 | 1373.6566 | 1294.857 | 1152.8544
TOTAL | 4891.2752 | 4542.04 | 3913.6515 | 6686.6649 | 6196.7544 | 5313.6196 | 8413.5247 | 7789.9333 | 6664.3824 | 9548.5538 | 8837.6712 | 7553.796 | 10756.9494 | 9953.4757 | 8501.6794 | 12932.5771 | 11962.9971 | 10210.0293
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 81.5282 | 78.9346 | 72.6547 | 98.5345 | 95.0138 | 86.3496 | 114.2073 | 109.9185 | 99.2787 | 124.1269 | 119.3769 | 107.5541 | 134.3778 | 129.1647 | 116.1572 | 152.1108 | 146.1193 | 131.126
TOTAL | 510.9841 | 482.773 | 414.3312 | 698.353 | 659.0525 | 563.5672 | 877.6844 | 827.8534 | 706.7036 | 995.2637 | 938.5494 | 800.6334 | 1120.2728 | 1056.25 | 900.5385 | 1345.0437 | 1267.8925 | 1080.2274
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
B' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 15
CONDUCTOR
Wind on Conductor | 3947.7645 | 3626.3269 | 3059.926 | 5513.8199 | 5064.8698 | 4273.7809 | 7018.248 | 6446.8034 | 5439.8684 | 8007.908 | 7355.8826 | 6206.9573 | 9062.8203 | 8324.9011 | 7024.6235 | 10966.0125 | 10073.1303 | 8499.7944
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 5460.1322 | 5246.5757 | 4884.286 | 6542.0509 | 6227.8044 | 5680.9002 | 7597.264 | 7197.1993 | 6490.1872 | 8284.2866 | 7832.6156 | 7028.8405 | 9005.6082 | 8502.3365 | 7601.7161 | 10273.5501 | 9684.2093 | 8622.1748
TOTAL | 9621.3435 | 9087.1061 | 8144.869 | 12353.9907 | 11591.8511 | 10234.9376 | 14994.9732 | 14024.8089 | 12286.7791 | 16725.1644 | 15623.0028 | 13642.8238 | 18558.4351 | 17318.9811 | 15086.9846 | 21832.4706 | 20352.3494 | 17679.3497
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 609.7481 | 590.3503 | 543.3827 | 736.9372 | 710.6065 | 645.8068 | 854.1541 | 822.0782 | 742.5035 | 928.3427 | 892.8171 | 804.3951 | 1005.0089 | 966.0202 | 868.7377 | 1137.6335 | 1092.8233 | 980.6886
TOTAL | 1039.204 | 994.1887 | 885.0592 | 1336.7557 | 1274.6452 | 1123.0243 | 1617.6312 | 1540.013 | 1349.9284 | 1799.4795 | 1711.9896 | 1497.4744 | 1990.9039 | 1893.1055 | 1653.119 | 2330.5665 | 2214.5966 | 1929.79
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'C' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 30
CONDUCTOR
Wind on Conductor | 3947.7645 | 3626.3269 | 3059.926 | 5513.8199 | 5064.8698 | 4273.7809 | 7018.248 | 6446.8034 | 5439.8684 | 8007.908 | 7355.8826 | 6206.9573 | 9062.8203 | 8324.9011 | 7024.6235 | 10966.0125 | 10073.1303 | 8499.7944
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 10826.84 | 10403.381 | 9685.0005 | 12972.1655 | 12349.0494 | 11264.5986 | 15064.5368 | 14271.2525 | 12869.3254 | 16426.8267 | 15531.213 | 13937.4157 | 17857.128 | 16859.1956 | 15073.3648 | 20371.3168 | 19202.7192 | 17096.8217
TOTAL | 14988.0513 | 14243.9114 | 12945.5835 | 18784.1053 | 17713.096 | 15818.636 | 22462.2459 | 21098.8621 | 18665.9173 | 24867.7045 | 23321.6002 | 20551.3989 | 27409.9548 | 25675.8402 | 22558.6333 | 31930.2373 | 29870.8592 | 26153.9966
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 1209.0633 | 1170.5996 | 1077.468 | 1461.2652 | 1409.0543 | 1280.5636 | 1693.6934 | 1630.0904 | 1472.3026 | 1840.8012 | 1770.3578 | 1595.0268 | 1992.8219 | 1915.5116 | 1722.611 | 2255.8018 | 2166.9482 | 1944.5974
TOTAL | 1638.5191 | 1574.438 | 1419.1445 | 2061.0837 | 1973.093 | 1757.7812 | 2457.1705 | 2348.0253 | 2079.7275 | 2711.938 | 2589.5303 | 2288.1061 | 2978.7169 | 2842.5969 | 2506.9923 | 3448.7348 | 3288.7214 | 2893.6988
TRANSVERSE LOAD FOR RELIABILITY CONDITIONS 32O FULL WIND
| WIND ZONE-1 |  |  | WIND ZONE-2 |  |  | WIND ZONE-3 |  |  | WIND ZONE-4 |  |  | WIND ZONE-5 |  |  | WIND ZONE-6
Terrain Category | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
'D' Type | WIND ZONE-1 2: Angle; WIND ZONE-1 3: 60
CONDUCTOR
Wind on Conductor | 3947.7645 | 3626.3269 | 3059.926 | 5513.8199 | 5064.8698 | 4273.7809 | 7018.248 | 6446.8034 | 5439.8684 | 8007.908 | 7355.8826 | 6206.9573 | 9062.8203 | 8324.9011 | 7024.6235 | 10966.0125 | 10073.1303 | 8499.7944
Wind on Insulator | 213.4469 | 214.2035 | 200.657 | 298.12 | 299.1768 | 280.2565 | 379.4611 | 380.8062 | 356.7235 | 432.9698 | 434.5046 | 407.026 | 490.0066 | 491.7436 | 460.6451 | 592.9079 | 595.0098 | 557.3805
Deviation Load | 20915.8487 | 20097.7888 | 18709.9843 | 25060.2993 | 23856.5315 | 21761.5335 | 29102.4503 | 27569.9427 | 24861.6275 | 31734.1924 | 30003.9995 | 26925.0195 | 34497.3222 | 32569.4648 | 29119.5046 | 39354.3621 | 37096.8048 | 33028.5233
TOTAL | 25077.0601 | 23938.3192 | 21970.5673 | 30872.2391 | 29220.5781 | 26315.5708 | 36500.1594 | 34397.5523 | 30658.2195 | 40175.0702 | 37794.3867 | 33539.0027 | 44050.1491 | 41386.1095 | 36604.7731 | 50913.2826 | 47764.9448 | 42085.6982
GROUND WIRE
Wind on Ground Wire | 429.4559 | 403.8384 | 341.6765 | 599.8185 | 564.0387 | 477.2176 | 763.4771 | 717.9349 | 607.4249 | 871.1368 | 819.1726 | 693.0793 | 985.895 | 927.0853 | 784.3813 | 1192.9329 | 1121.7732 | 949.1014
Deviation Load | 2335.7309 | 2261.4248 | 2081.5083 | 2822.9475 | 2722.0839 | 2473.8589 | 3271.9644 | 3149.0928 | 2844.2703 | 3556.1548 | 3420.0686 | 3081.3552 | 3849.8362 | 3700.4843 | 3327.8288 | 4357.8745 | 4186.2224 | 3756.6737
TOTAL | 2765.1867 | 2665.2632 | 2423.1848 | 3422.766 | 3286.1226 | 2951.0765 | 4035.4415 | 3867.0277 | 3451.6952 | 4427.2916 | 4239.2411 | 3774.4345 | 4835.7312 | 4627.5696 | 4112.2101 | 5550.8074 | 5307.9956 | 4705.775

## Sagten
BASIC DATA | [5 empty] | BASIC DATA
Sl.No. | Particulars | Unit | Size | code |  | Sl.No. | Particulars | Unit | Size | code
1 | Name of Conductor |  | ACSR MOOSE |  |  | 1 | Name of Conductor |  | 7/3.66MM GSS
2 | Diameter of Conductor | Cm | 3.177 | dia |  | 2 | Diameter of Conductor | Cm | 1.098 | dia
3 | Area of Conductor | Sq.Cm | 5.975 | a |  | 3 | Area of Conductor | Sq.Cm | 0.73646 | a
4 | Ultimate Tensile Strgth | kG | 16274 | uts |  | 4 | Ultimate Tensile Strgth | kG | 6975 | uts
5 | Unit Weight | kG/Meter | 2.004 | w |  | 5 | Unit Weight | kG/Meter | 0.583 | w
6 | Modulus of Elasticity | kG/Sq.Cm | 736000 | e |  | 6 | Modulus of Elasticity | kG/Sq.Cm | 1936800 | e
7 | Coeff. Of Linear Expn. | per Deg.C | 1.9e-05 | alph |  | 7 | Coeff. Of Linear Expn. | per Deg.C | 1.15e-05 | alph
8 | Initial Conditions |  |  |  |  | 8 | Initial Conditions
| a) Temperature | o C | 32 | ti |  |  | a) Temperature | o C | 32 | ti
| b) Tension not exceed | [5 empty] | b) Tension not exceed
| %age of UTS | %age | 22 |  |  |  | %age of UTS | %age | 20
| c) Tension as per © | kG | 3580.28 | ten1 |  |  | c) Tension as per © | kG | 1395 | ten1
| d) Wind | kG/Meter | 0 | wi |  |  | d) Wind | kG/Meter | 0 | wi
9 | Ruling Span | Meter | 400 | s |  | 9 | Ruling Span | Meter | 400 | s
10 | Wind span | Meter | 400 | ws |  | 10 | Wind span | Meter | 400 | ws
11 | Weight span | Meter | 600 | wts |  | 11 | Weight span | Meter | 600 | wts
SAG-TENSION CALCULATIONS AT 32 DEG FW
(FOR 400KV D/C TOWERS)
| Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
| 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
Pressure | 81.4845 | 76.6239 | 64.8293 | 113.8089 | 107.0201 | 90.5467 | 144.8613 | 136.2202 | 115.2521 | 165.2886 | 155.4289 | 131.5041 | 187.0626 | 175.9042 | 148.8277 | 226.3458 | 212.844 | 180.0815
Tension Cond | 5354.5234 | 5195.0563 | 4819.2839 | 6447.4812 | 6215.5257 | 5656.684 | 7506.135 | 7212.7829 | 6496.8328 | 8192.9641 | 7862.7393 | 7052.1395 | 8912.6403 | 8545.5434 | 7640.2799 | 10175.1366 | 9746.4899 | 8683.4
Pressure | 100.3948 | 95.1615 | 80.5441 | 140.2208 | 132.9116 | 112.4955 | 178.4797 | 169.1761 | 143.1896 | 203.6475 | 193.032 | 163.3811 | 230.4748 | 218.4608 | 184.9039 | 278.8745 | 264.3376 | 223.7337
Tension GW | 2368.9911 | 2302.3636 | 2116.324 | 2867.838 | 2777.757 | 2522.4069 | 3326.5002 | 3216.9737 | 2904.2064 | 3616.4892 | 3495.2767 | 3148.1013 | 3915.997 | 3783.046 | 3401.3861 | 4433.8403 | 4281.1415 | 3841.6277
Pressure | 103.2548 | 102.8134 | 96.7629 | 144.2154 | 143.5988 | 135.1482 | 183.5641 | 182.7793 | 172.023 | 209.4489 | 208.5535 | 196.2804 | 237.0404 | 236.027 | 222.1371 | 286.8188 | 285.5927 | 268.7859
Pressure | 250.9624 | 250.3046 | 235.6153 | 350.5177 | 349.599 | 329.0825 | 446.1553 | 444.9859 | 418.8716 | 509.0688 | 507.7345 | 477.9377 | 576.1303 | 574.6203 | 540.8983 | 697.1177 | 695.2905 | 654.4869
(FOR 400KV S/C TOWERS)
| Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
| 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
Pressure | 75.896 | 69.578 | 58.0842 | 106.0036 | 97.1792 | 81.1259 | 134.9263 | 123.6942 | 103.2608 | 153.9526 | 141.1366 | 117.8219 | 174.2333 | 159.7291 | 133.343 | 210.8223 | 193.2722 | 161.3451
Tension Cond | 5171.3738 | 4968.3351 | 4614.206 | 6180.839 | 5880.6401 | 5342.6874 | 7168.7429 | 6785.4987 | 6087.3388 | 7813.0782 | 7379.8611 | 6584.7172 | 8490.262 | 8007.075 | 7114.8179 | 9681.8315 | 9115.3169 | 8061.1933
Pressure | 95.2666 | 88.778 | 74.5881 | 133.0583 | 123.9957 | 104.1768 | 169.3628 | 157.8275 | 132.601 | 193.2451 | 180.0832 | 151.2994 | 218.702 | 203.8062 | 171.2307 | 264.6294 | 246.6055 | 207.1891
Tension GW | 2303.7019 | 2221.0268 | 2041.0349 | 2779.5726 | 2666.8803 | 2417.0583 | 3219.1848 | 3081.6264 | 2773.9134 | 3497.7254 | 3345.2483 | 3002.8962 | 3785.7331 | 3618.2894 | 3241.2721 | 4284.2295 | 4091.6455 | 3656.5807
Pressure | 94.4776 | 95.542 | 89.0659 | 131.9564 | 133.443 | 124.3978 | 167.9602 | 169.8525 | 158.3393 | 191.6447 | 193.8038 | 180.6671 | 216.8908 | 219.3343 | 204.4671 | 262.4379 | 265.3945 | 247.4052
Pressure | 236.1859 | 237.0231 | 222.0335 | 329.8794 | 331.0488 | 310.1128 | 419.886 | 421.3744 | 394.7261 | 479.0951 | 480.7935 | 450.3874 | 542.2081 | 544.1302 | 509.7187 | 656.0718 | 658.3976 | 616.7596
(FOR 765 KV S/C TOWERS)
| Wind Zone-1 |  |  | Wind Zone-2 |  |  | Wind Zone-3 |  |  | Wind Zone-4 |  |  | Wind Zone-5 |  |  | Wind Zone-6
| 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3
Pressure | 77.663 | 71.3394 | 60.1968 | 108.4714 | 99.6394 | 84.0766 | 138.0675 | 126.8257 | 107.0166 | 157.5367 | 144.7097 | 122.1073 | 178.2897 | 163.7728 | 138.1929 | 215.7305 | 198.1651 | 167.2135
Tension Cond | 5228.9622 | 5024.4472 | 4677.4961 | 6265.0748 | 5964.1329 | 5440.3834 | 7275.6126 | 6892.4857 | 6215.4069 | 7933.5481 | 7500.9999 | 6731.2549 | 8624.3306 | 8142.3662 | 7279.8762 | 9838.5905 | 9274.2012 | 8257.1308
Pressure | 97.7814 | 91.9486 | 77.7952 | 136.5707 | 128.4241 | 108.6561 | 173.8336 | 163.4642 | 138.3026 | 198.3463 | 186.5147 | 157.8049 | 224.4752 | 211.085 | 178.5932 | 271.615 | 255.4128 | 216.0978
Tension GW | 2335.7309 | 2261.4248 | 2081.5083 | 2822.9475 | 2722.0839 | 2473.8589 | 3271.9644 | 3149.0928 | 2844.2703 | 3556.1548 | 3420.0686 | 3081.3552 | 3849.8362 | 3700.4843 | 3327.8288 | 4357.8745 | 4186.2224 | 3756.6737
Pressure | 97.7321 | 98.0785 | 91.8759 | 136.5018 | 136.9857 | 128.3226 | 173.7459 | 174.3618 | 163.335 | 198.2462 | 198.949 | 186.3672 | 224.362 | 225.1573 | 210.9181 | 271.478 | 272.4404 | 255.2109
Pressure | 244.0508 | 243.153 | 228.2339 | 340.8643 | 339.6104 | 318.7729 | 433.868 | 432.272 | 405.7491 | 495.0488 | 493.2278 | 462.9647 | 560.2635 | 558.2025 | 523.9528 | 677.9188 | 675.4251 | 633.9829
SAG - TENSION CALCULATIONS
FOR ACSR MOOSE
SAG - TENSION CALCULATIONS
FOR 7/3.66 GROUND WIRE

## Sagten calculations
SAG-TENSION CALCULATIONS
SUPPORTING SHEET
ACSR MOOSE CONDUCTOR
ACSR MOOSE FOR 400 KV DC LINE
Temp | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
wind | 0.81484 | 0.76624 | 0.64829 | 1.1381 | 1.0702 | 0.90547 | 1.4486 | 1.3622 | 1.1525 | 1.6529 | 1.5543 | 1.315 | 1.8706 | 1.759 | 1.4883 | 2.2635 | 2.1284 | 1.8008
(ke-alph *e*t) | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524
RHS | 1473033332.7853 | 1366424516.4534 | 1134984563.2453 | 2348749895.1174 | 2140782242.4123 | 1689299659.011 | 3463010524.4033 | 3126074018.4655 | 2394609474.9928 | 4341884270.4889 | 3903223503.4672 | 2950923019.4462 | 5406176738.896 | 4844330627.6674 | 3624603759.2242 | 7659019574.1578 | 6836420682.708 | 5050618574.6204
LHS-RHS | 7.8337e-08 | -6.0098e-05 | -2.9712e-07 | 2.1869e-07 | -7.5399e-07 | 1.9397e-06 | 4.648e-06 | -7.474e-07 | -4.0141e-07 | 2.5535e-08 | 0.00079521 | 1.7364e-06 | 1.7539e-05 | -2.1714e-05 | 1.267e-05 | 4.9659e-05 | 1.6096e-07 | -2.4753e-06
Tens2 | 5354.5234 | 5195.0563 | 4819.2839 | 6447.4812 | 6215.5257 | 5656.684 | 7506.135 | 7212.7829 | 6496.8328 | 8192.9641 | 7862.7393 | 7052.1395 | 8912.6403 | 8545.5434 | 7640.2799 | 10175.1366 | 9746.4899 | 8683.4
ACSR MOOSE FOR 400 KV SC LINE
Temp | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
wind | 0.75896 | 0.69578 | 0.58084 | 1.06 | 0.97179 | 0.81126 | 1.3493 | 1.2369 | 1.0326 | 1.5395 | 1.4114 | 1.1782 | 1.7423 | 1.5973 | 1.3334 | 2.1082 | 1.9327 | 1.6135
(ke-alph *e*t) | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524
RHS | 1351025609.5698 | 1223524357.812 | 1019975146.5649 | 2110742751.9743 | 1862019082.0436 | 1464944495.4424 | 3077405868.3149 | 2674438949.1791 | 2031122923.5092 | 3839861986.6877 | 3315235611.34 | 2477696501.4942 | 4763175839.0918 | 4091223134.4121 | 3018485093.4344 | 6717601956.7544 | 5733796001.833 | 4163200236.0375
LHS-RHS | -5.7431e-07 | -7.2177e-06 | -0.00032006 | -6.1516e-05 | 4.1915e-07 | -7.617e-08 | 5.9938e-07 | -7.1776e-07 | -0.00018209 | -5.8369e-05 | -8.5989e-07 | 1.2534e-07 | 1.4945e-07 | -7.6749e-06 | -1.059e-06 | 7.9549e-07 | -0.00010837 | -5.428e-06
Tens2 | 5171.3738 | 4968.3351 | 4614.206 | 6180.839 | 5880.6401 | 5342.6874 | 7168.7429 | 6785.4987 | 6087.3388 | 7813.0782 | 7379.8611 | 6584.7172 | 8490.262 | 8007.075 | 7114.8179 | 9681.8315 | 9115.3169 | 8061.1933
ACSR MOOSE FOR 765 KV SC LINE
Temp | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
wind | 0.77663 | 0.71339 | 0.60197 | 1.0847 | 0.99639 | 0.84077 | 1.3807 | 1.2683 | 1.0702 | 1.5754 | 1.4471 | 1.2211 | 1.7829 | 1.6377 | 1.3819 | 2.1573 | 1.9817 | 1.6721
(ke-alph *e*t) | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524 | -938.0524
RHS | 1388664879.7496 | 1257958130.9786 | 1054639338.9428 | 2184167736.3062 | 1929190927.9156 | 1532565832.6806 | 3196364549.3767 | 2783266676.7179 | 2140678889.5429 | 3994735398.6181 | 3456919440.7682 | 2620328431.3836 | 4961541024.1448 | 4272694819.5339 | 3201171125.9454 | 7008028424.1906 | 5999488696.0197 | 4430670856.2368
LHS-RHS | -1.7435e-05 | -3.2394e-05 | -5.3905e-06 | 0.0003326 | -6.9748e-08 | 2.9844e-07 | 0.00047099 | 3.0494e-07 | 0.0001205 | 1.1757e-06 | 6.7154e-07 | 7.4528e-05 | 2.4008e-07 | 2.4207e-05 | 0.00051048 | -3.491e-07 | 0.00021259 | 9.236e-05
Tens2 | 5228.9622 | 5024.4472 | 4677.4961 | 6265.0748 | 5964.1329 | 5440.3834 | 7275.6126 | 6892.4857 | 6215.4069 | 7933.5481 | 7500.9999 | 6731.2549 | 8624.3306 | 8142.3662 | 7279.8762 | 9838.5905 | 9274.2012 | 8257.1308
7/3.66MM GSS GROUND WIRE
7/3.66MM GSS WIRE FOR 400 KV DC LINE
Temp | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
wind | 1.0039 | 0.95162 | 0.80544 | 1.4022 | 1.3291 | 1.125 | 1.7848 | 1.6918 | 1.4319 | 2.0365 | 1.9303 | 1.6338 | 2.3047 | 2.1846 | 1.849 | 2.7887 | 2.6434 | 2.2373
(ke-alph *e*t) | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886
RHS | 37019825589.7482 | 34082549756.4677 | 26711050615.5792 | 64523510202.1872 | 58793605477.4877 | 44413618662.1803 | 99519163181.8759 | 90235921042.1252 | 66938343510.4282 | 127122005661.093 | 115036066483.51 | 84704733874.2471 | 160548305500.061 | 145068375590.73 | 106219354761.726 | 231303480733.277 | 208639315353.026 | 151760463957.281
LHS-RHS | 0.000842 | 2.6706e-05 | -6.2534e-06 | 1.821e-05 | 3.2265e-06 | -5.4025e-06 | -2.8981e-05 | 1.1456e-05 | 1.7168e-05 | 4.7595e-05 | 4.4573e-06 | 1.482e-05 | 0.00052281 | 6.8978e-06 | -1.8521e-05 | 0.00034342 | 1.5243e-05 | 2.9136e-05
Tens2 | 2368.9911 | 2302.3636 | 2116.324 | 2867.838 | 2777.757 | 2522.4069 | 3326.5002 | 3216.9737 | 2904.2064 | 3616.4892 | 3495.2767 | 3148.1013 | 3915.997 | 3783.046 | 3401.3861 | 4433.8403 | 4281.1415 | 3841.6277
7/3.66MM GSS WIRE FOR 400 KV SC LINE
Temp | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
wind | 0.95267 | 0.88778 | 0.74588 | 1.3306 | 1.24 | 1.0418 | 1.6936 | 1.5783 | 1.326 | 1.9325 | 1.8008 | 1.513 | 2.187 | 2.0381 | 1.7123 | 2.6463 | 2.4661 | 2.0719
(ke-alph *e*t) | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886
RHS | 34139962510.4295 | 30712488104.4661 | 24059131081.146 | 58905603678.8335 | 52219441769.8983 | 39240374087.1549 | 90417373696.6218 | 79584861993.8238 | 58556968191.7257 | 115272301379.987 | 101169353766.474 | 73792943488.7975 | 145370950308.828 | 127307592768.763 | 92243299788.2433 | 209082314997.793 | 182635753223.384 | 131298121870.605
LHS-RHS | -3.685e-06 | -6.266e-06 | -1.2156e-05 | 2.1984e-05 | 2.9808e-05 | -2.1616e-05 | -3.274e-05 | 4.3673e-05 | 2.9769e-05 | 0.00043797 | 6.4071e-05 | -1.5545e-05 | 8.9871e-06 | 1.2302e-06 | -2.5562e-05 | 0.00012708 | -1.9298e-05 | 3.7357e-05
Tens2 | 2303.7019 | 2221.0268 | 2041.0349 | 2779.5726 | 2666.8803 | 2417.0583 | 3219.1848 | 3081.6264 | 2773.9134 | 3497.7254 | 3345.2483 | 3002.8962 | 3785.7331 | 3618.2894 | 3241.2721 | 4284.2295 | 4091.6455 | 3656.5807
7/3.66MM GSS WIRE FOR 765 KV SC LINE
Temp | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
wind | 0.97781 | 0.91949 | 0.77795 | 1.3657 | 1.2842 | 1.0866 | 1.7383 | 1.6346 | 1.383 | 1.9835 | 1.8651 | 1.578 | 2.2448 | 2.1108 | 1.7859 | 2.7161 | 2.5541 | 2.161
(ke-alph *e*t) | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886 | -360.9886
RHS | 35533339966.9378 | 32357121852.6233 | 25461784327.5605 | 61623741342.6086 | 55427718833.0167 | 41976606541.963 | 94821134546.8206 | 84782716802.8144 | 62990045118.6654 | 121005598539.201 | 107936489227.302 | 79564407520.649 | 152714280179.179 | 135975084891.748 | 99635514607.0136 | 219833684260.974 | 195325828440.646 | 142121063586.767
LHS-RHS | -1.272e-05 | -5.6861e-06 | 2.8782e-06 | 6.6048e-06 | 0.00025807 | 2.9577e-06 | -2.2148e-05 | 7.9991e-05 | -1.5125e-05 | 0.0006857 | 1.2987e-05 | 1.2846e-05 | 0.00079238 | 4.7956e-05 | 2.1049e-05 | -2.8358e-05 | -3.4177e-05 | 2.6631e-06
Tens2 | 2335.7309 | 2261.4248 | 2081.5083 | 2822.9475 | 2722.0839 | 2473.8589 | 3271.9644 | 3149.0928 | 2844.2703 | 3556.1548 | 3420.0686 | 3081.3552 | 3849.8362 | 3700.4843 | 3327.8288 | 4357.8745 | 4186.2224 | 3756.6737