## Cover
Central Electricity Regulatory Commission
Capital Cost Benchmarking for Transmission Sub-Station

## L
CERC
Capital Cost Benchmarking
Formatting of Headers / Dividers
| Sheet Header 1 | CERC | SheetHeader1
| Sheet Header 2 | Capital Cost Benchmarking | SheetHeader2
| Sheet Header 3 | Transmission Substations | SheetHeader3
| Header 1 | Header 1 | Header1
| Header 2 | Header 2 | Header2
| Header 3 | Header 3 | Header3
| Inputs Divider | Operational Assumptions | Inputs_Divider
| Table Heading 2 | Table Heading 2 | Table_Heading2
| Table Heading 3 | Table Heading 3
| Table Heading 4 | Table Heading 4
Individual Cell Assumptions
| Standard Assumption | 100 | Assumptions
| Offsheet Reference | 100 | Offsheet
| Flex Cell | 100 | Assumption_Flex
| Name Inputs | Cost Type | Technical_Input
| Technical Input | 1000 | Input
| Empy Cell |  | Empty_Cell
| Background for Flag | 0 | Flag
Infrastructure
| Sub-Total | Sub-Total | Sub-Total
| Line Total | 100 | Line_Summary
| Units | USD | Unit
| Operation Line (Non-Addition) | 100 | Line_Operation
| Operation (Addition / Total) | 100 | Line_Total
| Closing Balance | 100 | Line_ClosingBal
| Key Line | 100 | Line_Key
Development Styles
| WIP | W | WIP

## Computation_Sheet
CERC
Capital Cost Benchmarking
Transmission Substations
| Choose the Type of Compensation | Series Compensation -2- For S/C Line
|  |  | Add | 1
| Total Cost of Sub-Station (INR Crore) | 15.0168 | Substract | -1
Series Compensation -1 - For D/C Line
Series Compensation -2- For S/C Line

## User Guide
CERC
Capital Cost Benchmarking
Transmission Substations
| 1 | Please Select Computation_Sheet
| 2 | Select the type of compensation to be provided from drop down list in cell D8.
| 3 | Final Output shall be available in cell D11

## Actual Cost
CERC
Capital Cost Benchmarking
Transmission Substations
|  | Ref No. |  | C-14405-S162-3/P-154 & 155/LOA-I/2571 DT: 10-07-2008 | C-14405-S162-3/P-154 & 155/LOA-I/2571 DT: 10-07-2008 | C-13603-S162-3(R1)/LOA-I/2821DT: 03/02/2009 | C-46205-S162-1/CA-I/2905 DT: 01-12-2008 | C-33020-S162-1/CA-I/3004 Dated 27.03.2009
|  | Name of Sub-Station |  | Ballabhgarh | Lucknow | Meerut | Raipur | Wardha
|  | Name of Transmission line |  | Ballabhgarh - Kanpur D/C T/L | Lucknow - Gorakhpur D/C T/L | Tehri - Meerath 765 S/C kV | Raipur-Raigrah D/C T/L | Wadra -Raipur D/C line with Quad conductor
|  | % of Compensation |  | 40% | 30% | 50% | 40% | 40%
| S.No. | Name of Equipment | Unit
| 1 | SF6 Bypass Circuit Breaker -3-Ph | INR Lakh | 101.0085 | 86.2483 | 142.2429 | 87.0371 | 51.77
| 2 | Protective Spark Gap - forced triggered | INR Lakh | 172.8517 | 104.7275 | 203.7021 | 129.8414 | 159.8756
| 3 | Damping Cirucit | INR Lakh | 70.3346 | 87.6299 | 72.749 | 20.3353 | 53.6455
| 4 | Series Capacitor Bank | INR Lakh | 366.3899 | 393.1729 | 328.6681 |  | 678.6681
| 5 | Disconnecting and Bypass Isolators (Individual Pole operated) Double Break. | INR Lakh
| a) | 3-Ph, with one earth switch | INR Lakh | 8.27 | 8.9564 | 8.8951 | 31.8908 | 3.0901
| b) | 3-Ph, Without earth switch | INR Lakh | 6.7735 | 7.2098 | 7.2468 | 26.0097 | 2.4839
| 6 | Insulated platforms -3-Ph - Including Plot form & BPS Etc | INR Lakh | 83.3621 | 77.4944 | 207.9761 | 154.0645 | 141.1579
| 7 | Metal Oxide Varistor, (MOV) including 10% Spare | INR Lakh | 83.5148 | 109.1088 | 88.2152 | 156.5371 | 90.7424
| 8 | Control & Protection Equipment excluding signal column | INR Lakh | 172.193 | 172.193 | 161.135 | 175.1515 | 234.6582
| 9 | Current Transformer | INR Lakh | 3.5753 | 3.5753 | 2.6876 | 18.873 | 4.0582
| 10 | Platform to ground signal transmission system | INR Lakh | 21.2642 | 21.2642 | 25.988 | 36.3744
| 11 | Power supply Cubicles including ACDB & DCDB | INR Lakh | 2.7682 | 2.7682 | 20.5095 | 3.919
| 12 | Power and Control cables including cables including cable accessories for both the banks | INR Lakh | 38.2266 | 37.3837 | 52.1834 | 43.0809 | 62.0676
| 13 | Bus bar material including post insulators, disc insulator strings, Hardwares, Conductor, Aluminium Tube, GI wire, clamps and connectors, Earthig materials etc. for 3 phases for both the banks | INR Lakh | 70.143 | 74.7708 | 195.8698 | 191.7195 | 105.647
| 14 | Galvanised Steel Structures for 3 phases for both the banks | INR Lakh | 12.6409 | 12.6409 | 52.9425 | 57.1937 | 45.2187
| 15 | Surge Arrrestor (390kV) for 400kV system | INR Lakh | 1.4184 | 1.4184 | 1.4029
| 16 | Air conditioned kiosks for two banks | INR Lakh | 10.2774 | 10.2774 |  | 14.2508
| 17 | Fire Protection System | INR Lakh | 11.9603 | 11.9603 | 17.5847 | 14.4827 | 6.12
| 18 | Mandatory Spares | INR Lakh | 117.3613 | 139.9333 | 172.7474 | 143.6647 | 178.9666
| 19 | Civil Engineering Works | INR Lakh | 170.5472 | 146.8849 | 459.1125 |  | 240.5517
| 20 | Erection Charges | INR Lakh
| a) | SF6 Bypass Circuit Breaker (3-Ph) | INR Lakh | 5.3022 | 5.3022 | 5.2673 | 9.1779 | 0.7003
| b) | Protective Spark Gap (forced triggered) | INR Lakh | 0.39767 | 0.39767 | 0.39505 | 20.1393 | 0.47619
| c) | Damping Cirucit | INR Lakh | 0.19883 | 0.19883 | 0.2 | 3.1542 | 0.8532
| e) | Series Capacitor Bank | INR Lakh | 7.2906 | 7.2906 | 7.2426 |  | 10.2049
| f) | Disconnecting and Bypass Isolators (Individual Pole operated) Double Break. | INR Lakh
| i | 3-Ph, with one earth switch | INR Lakh | 0.38445 | 0.38445 | 0.26337 | 4.9465 | 0.04914
| ii | 3-Ph, Without earth switch | INR Lakh | 0.38445 | 0.38445 | 0.26337 | 4.9453 | 0.0395
| g) | Insulated platforms -3-Ph - Including Plot form & BPS Etc | INR Lakh | 6.3627 | 6.3627 | 207.9761 |  | 4.4116
| h) | Metal Oxide Varistor, (MOV) including 10% Spare | INR Lakh | 1.9883 | 1.9883 | 1.99 | 9.7178 | 0.19048
| i) | Control & Protection Equipment excluding signal column | INR Lakh | 2.6511 | 2.6511 | 2.6337 | 8.0981 | 6.6667
| j) | Current Transformer | INR Lakh | 0.37557 | 0.37557 | 0.3731 | 2.9273 | 0.070093
| k) | Platform to ground signal transmission system | INR Lakh | 1.0604 | 1.0604 | 1.0535 | 5.6419
| l) | Power supply Cubictes including ACDB & DCDB | INR Lakh | 0.26511 | 0.26511 | 1.8435 | 1.0797
| m) | Power and Control cables including cables including cable accessories for both the banks | INR Lakh | 5.965 | 5.965 | 5.9257 |  | 4.9018
| n) | Bus bar material including post insulators, disc insulator strings, Hardwares, Conductor, Aluminium Tube, GI wire, clamps and connectors, Earthig materials etc. for 3 phases for both the banks | INR Lakh | 4.6395 | 4.6395 | 4.6089 |  | 3.4256
| o) | Galvanised Steel Structures for 3 phases for both the banks | INR Lakh | 3.2476 | 3.2476 | 3.2262 |  | 3.785
| p) | Surge Arrrestor (390kV) for 400kV system | INR Lakh | 0.29162 | 0.29162 | 0.28971
| q) | Air conditioned kiosks for two banks | INR Lakh | 0.53022 | 0.53022
| r) | Fire Protection System | INR Lakh | 5.3022 | 5.3022 | 5.2673 |  | 0.19272
| s) | Dismantling and re-erection of overhead stringing including insulator string along with necessary hardware etc. over the proposed installation of the series capacitor | INR Lakh | 0.33139 | 0.33139 | 0.32921

## Average Cost
CERC
Capital Cost Benchmarking
Transmission Substations
S.No. | Name of Equipment | Unit | Average Rates
1 | SF6 Bypass Circuit Breaker -3-Ph | INR Lakh | 81.52
2 | Protective Spark Gap - forced triggered | INR Lakh | 141.82
3 | Damping Cirucit | INR Lakh | 71.09
4 | Series Capacitor Bank | INR Lakh | 441.7247
5 | Disconnecting and Bypass Isolators (Individual Pole operated) Double Break. | INR Lakh
a) | 3-Ph, with one earth switch | INR Lakh | 7.3
b) | 3-Ph, Without earth switch | INR Lakh | 5.93
6 | Insulated platforms -3-Ph - Including Plot form & BPS Etc | INR Lakh | 132.811
7 | Metal Oxide Varistor, (MOV) including 10% Spare | INR Lakh | 74.3162
8 | Control & Protection Equipment excluding signal column | INR Lakh | 185.0448
9 | Current Transformer | INR Lakh | 3.4741
10 | Platform to ground signal transmission system | INR Lakh | 26.2227
11 | Power supply Cubicles including ACDB & DCDB | INR Lakh | 3.1518
12 | Power and Control cables including cables including cable accessories for both the banks | INR Lakh | 46.5884
13 | Bus bar material including post insulators, disc insulator strings, Hardwares, Conductor, Aluminium Tube, GI wire, clamps and connectors, Earthig materials etc. for 3 phases for both the banks | INR Lakh | 127.63
14 | Galvanised Steel Structures for 3 phases for both the banks | INR Lakh | 36.1274
15 | Surge Arrrestor (390kV) for 400kV system | INR Lakh | 1.4132
16 | Air conditioned kiosks for two banks | INR Lakh | 11.6018
17 | Fire Protection System | INR Lakh | 11.9063
18 | Mandatory Spares | INR Lakh | 150.5347
19 | Civil Engineering Works | INR Lakh | 185.9946
20 | Erection Charges
a) | SF6 Bypass Circuit Breaker (3-Ph) | INR Lakh | 5.15
b) | Protective Spark Gap (forced triggered) | INR Lakh | 4.3612
c) | Damping Cirucit | INR Lakh | 0.92101
e) | Series Capacitor Bank | INR Lakh | 8.0071
f) | Disconnecting and Bypass Isolators (Individual Pole operated) Double Break. | INR Lakh
i | 3-Ph, with one earth switch | INR Lakh | 1.2056
ii | 3-Ph, Without earth switch | INR Lakh | 1.2034
g) | Insulated platforms -3-Ph - Including Plot form & BPS Etc | INR Lakh | 5.7123
h) | Metal Oxide Varistor, (MOV) including 10% Spare | INR Lakh | 3.175
i) | Control & Protection Equipment excluding signal column | INR Lakh | 4.5401
j) | Current Transformer | INR Lakh | 0.82434
k) | Platform to ground signal transmission system | INR Lakh | 2.2041
l) | Power supply Cubictes including ACDB & DCDB | INR Lakh | 0.86336
m) | Power and Control cables including cables including cable accessories for both the banks | INR Lakh | 5.6894
n) | Bus bar material including post insulators, disc insulator strings, Hardwares, Conductor, Aluminium Tube, GI wire, clamps and connectors, Earthig materials etc. for 3 phases for both the banks | INR Lakh | 4.3283
o) | Galvanised Steel Structures for 3 phases for both the banks | INR Lakh | 3.3766
p) | Surge Arrrestor (390kV) for 400kV system | INR Lakh | 0.29098
q) | Air conditioned kiosks for two banks | INR Lakh
r) | Fire Protection System | INR Lakh | 5.2906
s) | Dismantling and re-erection of overhead stringing including insulator string along with necessary hardware etc. over the proposed installation of the series capacitor | INR Lakh | 0.33066

## Alternates
CERC
Capital Cost Benchmarking
Transmission Substations
BOQ & Cost for Series Compensation
[5 empty] | Series Compensation -1 - For D/C Line |  | Series Compensation -2- For S/C Line
| S.No. | Name of Material & Equipment | Unit | Rate (INR Lakhs) | Quantity | Amount - INR | Quantity | Amount - INR
| 1 | SF6 Bypass Circuit Breaker (3-Ph) | Nos | 81.52 | 2 | 163.04 | 1 | 81.52
| 2 | Protective Spark Gap (forced triggered) | Set | 141.82 | 2 | 283.64 | 1 | 141.82
| 3 | Damping Cirucit | Set | 71.09 | 2 | 142.18 | 1 | 71.09
| 4 | Series Capacitor Bank (as per Tech Specification) | Set | 441.7247 | 2 | 883.4495 | 1 | 441.7247
| 5 | Disconnecting and Bypass Isolators (Individual Pole operated) Double Break.
| a) | 3-Ph, with one earth switch | No | 7.3 | 4 | 29.2 | 2 | 14.6
| b) | 3-Ph, Without eatth switch | No | 5.93 | 2 | 11.86 | 1 | 5.93
| 6 | Insulated platforms (3-Ph) | Set | 132.811 | 2 | 265.622 | 1 | 132.811
| a) | Structures
| b) | Platform Insulators including BPIs & String Insulators
| 7 | Metal Oxide Varistor, (MOV) including 10% Spare | Set | 74.3162 | 2 | 148.6325 | 1 | 74.3162
| 8 | Control & Protection Equipment excluding signal column | Set | 185.0448 | 2 | 370.0896 | 1 | 185.0448
| 9 | Current Transformers | Set | 3.4741 | 2 | 6.9482 | 1 | 3.4741
| 10 | Platform to ground signal transmission system | Set | 26.2227 | 2 | 52.4454 | 1 | 26.2227
| 11 | Power supply Cubictes including ACDB & DCDB | Set | 3.1518 | 2 | 6.3035 | 1 | 3.1518
| 12 | Power and Control cables including cables including cable accessories for both the banks | L/S | 46.5884 | 1 | 46.5884 | 0.5 | 23.2942
| 13 | Bus bar material including post insulators, disc insulator strings, Hardwares, Conductor, Aluminium Tube, GI wire, clamps and connectors, Earthig materials etc. for 3 phases for both the banks | L/S | 127.63 | 1 | 127.63 | 0.5 | 63.815
| 14 | Galvanised Steel Structures for 3 phases for both the banks | L/S | 36.1274 | 1 | 36.1274 | 0.5 | 18.0637
| 15 | Surge Arrrestor (390kV) for 400kV system | No | 1.4132 | 6 | 8.4794 | 3 | 4.2397
| 16 | Air conditioned kiosks for two banks | No | 11.6018 | 1 | 11.6018 | 1 | 11.6018
| 17 | Fire Protection System | L/S | 11.9063 | 1 | 11.9063 | 0.5 | 5.9532
| 18 | Civil Works | L/S | 185.9946 | 1 | 185.9946 | 0.75 | 139.496
| 19 | Erection Chargers
| a) | SF6 Bypass Circuit Breaker (3-Ph) | Nos | 5.15 | 2 | 10.3 | 1 | 5.15
| b) | Protective Spark Gap (forced triggered) | Nos | 4.3612 | 2 | 8.7224 | 1 | 4.3612
| c) | Damping Cirucit | Nos | 0.92101 | 2 | 1.842 | 1 | 0.92101
| e) | Series Capacitor Bank | Nos | 8.0071 | 2 | 16.0143 | 1 | 8.0071
| f) | Disconnecting and Bypass Isolators (Individual Pole operated) Double Break. |  | 0
| i | 3-Ph, with one earth switch | Nos | 1.2056 | 4 | 4.8223 | 2 | 2.4112
| ii | 3-Ph, Without earth switch | Nos | 1.2034 | 2 | 2.4068 | 1 | 1.2034
| g) | Insulated platforms -3-Ph - Including Plot form & BPS Etc | Sets | 5.7123 | 2 | 11.4246 | 1 | 5.7123
| h) | Metal Oxide Varistor, (MOV) including 10% Spare | Sets | 3.175 | 2 | 6.35 | 1 | 3.175
| i) | Control & Protection Equipment excluding signal column | Sets | 4.5401 | 2 | 9.0803 | 1 | 4.5401
| j) | Current Transformer | Set | 0.82434 | 2 | 1.6487 | 1 | 0.82434
| k) | Platform to ground signal transmission system | Sets | 2.2041 | 2 | 4.4082 | 1 | 2.2041
| l) | Power supply Cubictes including ACDB & DCDB | Set | 0.86336 | 2 | 1.7267 | 1 | 0.86336
| m) | Power and Control cables including cables including cable accessories for both the banks | L/S | 5.6894 | 1 | 5.6894 | 0.75 | 4.267
| n) | Bus bar material including post insulators, disc insulator strings, Hardwares, Conductor, Aluminium Tube, GI wire, clamps and connectors, Earthig materials etc. for 3 phases for both the banks | L/S | 4.3283 | 1 | 4.3283 | 0.5 | 2.1642
| o) | Galvanised Steel Structures for 3 phases for both the banks | L/S | 3.3766 | 1 | 3.3766 | 0.75 | 2.5325
| p) | Surge Arrrestor (390kV) for 400kV system | Nos | 0.29098 | 6 | 1.7459 | 3 | 0.87295
| q) | Air conditioned kiosks for two banks | Nos | 0 | 1 | 0
| r) | Fire Protection System | L/S | 5.2906 | 1 | 5.2906 | 0.75 | 3.9679
| s) | Dismantling and re-erection of overhead stringing including insulator string along with necessary hardware etc. over the proposed installation of the series capacitor | L/S | 0.33066 | 1 | 0.33066 | 1 | 0.33066
| 20 | Hard Cost |  |  |  | 2891.2464 |  | 1501.6772
| 21 | Material Portion in Rs lakhs |  |  | 2324.69 |  | 1308.673
| 22 | Interest on Materials / equipments at 10.4048 % |  |  |  | 241.8793 |  | 136.1648
| 23 | Total cost of Series compensation in Rs Lakhs |  |  |  | 3133.1257 |  | 1637.842

## Summary
CERC
Capital Cost Benchmarking
Transmission Substations
Alternates
| S.No. | Unit | Series Compensation -1 - For D/C Line | Series Compensation -2- For S/C Line
| 1 | INR Crore | 28.9125 | 15.0168