## Cover
Central Electricity Regulatory Commission
Capital Cost Benchmarking for Transmission Sub-Station 765/400 kV

## L
CERC
Capital Cost Benchmarking
Formatting of Headers / Dividers
| Sheet Header 1 | CERC | SheetHeader1
| Sheet Header 2 | Capital Cost Benchmarking | SheetHeader2
| Sheet Header 3 | Transmission Substations | SheetHeader3
| Header 1 | Header 1 | Header1
| Header 2 | Header 2 | Header2
| Header 3 | Header 3 | Header3
| Inputs Divider | Operational Assumptions | Inputs_Divider
| Table Heading 2 | Table Heading 2 | Table_Heading2
| Table Heading 3 | Table Heading 3
| Table Heading 4 | Table Heading 4
Individual Cell Assumptions
| Standard Assumption | 100 | Assumptions
| Offsheet Reference | 100 | Offsheet
| Flex Cell | 100 | Assumption_Flex
| Name Inputs | Cost Type | Technical_Input
| Technical Input | 1000 | Input
| Empy Cell |  | Empty_Cell
| Background for Flag | 0 | Flag
Infrastructure
| Sub-Total | Sub-Total | Sub-Total
| Line Total | 100 | Line_Summary
| Units | USD | Unit
| Operation Line (Non-Addition) | 100 | Line_Operation
| Operation (Addition / Total) | 100 | Line_Total
| Closing Balance | 100 | Line_ClosingBal
| Key Line | 100 | Line_Key
Development Styles
| WIP | W | WIP

## User Guide
CERC
Capital Cost Benchmarking
| S.No. | Description
| 1 | The model for Transmission sub-station is meant to provide benchmark cost for selected configuration in terms of number of ICTs, reactors, bays etc.
| 2 | There are 3 standard configurations (called alternates here) provided in the model. The cost has been computed for each of the alternates.For example alternate-1 has configuration given below:-
|  | 765KV Lines | 2
|  | 765/400KV Transformer: 3X500 MVAR | 3
|  | 765KV Shunt Reactor: 3X80 MVAR | 2
|  | 765KV Bus Reactor: 3X80 MVAR | 1
|  | No. of diameter | 3
|  | 400KV Lines | 4
|  | 400/220KV Transformer : 315 MVA | 2
|  | 400KV Shunt Reactor : 80 MVAR | 2
|  | 400KV Bus Reactor : 125 MVAR | 0
|  | 400KV Bus Reactor : 80 MVAR | 0
|  | No. of diameter | 5
|  | 220KV Lines | 4
|  | 220KV TBC | 1
|  | 220KV BC | 1
|  | No. of diameter | 8
| 3 | The user has to select the alternate that matches the configuration as given by petitioner using drop down list given in cell C8 of Computation_sheet
| 4 | In case none of the alternates matches the configuration given by petitioner, user has to select the closest alternate that matches the configuration. The user may then add/substract components as given in cells C34 to C44 of "Computation_Sheet" to match the required configuration.
| 5 | The benchmark cost shall get computed in the cell C63 of "Computation_Sheet"
| 6 | The month and the year of escalation can be chosen from drop down list provided in cell D6
| 7 | The model can be updated by entering the value of indices in sheet named "Indices" for corresponding month and year. The user to refer to IEEMA publications for the same.

## Computation_Sheet
CERC
Capital Cost Benchmarking
Transmission Substations
 | time axis 2002-01-01 to 2014-03-02
| Choose Month and Year of Escalation |  | 2009-12-01
| Choose from Alternates given below |  | Alt-1
Configurations for 765/400 kV Sub-Station
| S.No | Partculars | CONFIGURATION
|  |  | Alt-1 | Alt-2 | Alt-3
| 1 | 765KV Lines | 2 | 2 | 4
| 2 | 765/400KV Transformer: 3X500 MVAR | 3 | 2 | 2
| 3 | 765KV Shunt Reactor: 3X80 MVAR | 2 | 1 | 2
| 4 | 765KV Bus Reactor: 3X80 MVAR | 1 | 1 | 1
| 5 | No. of diameter | 3 | 2.5 | 3.5
| 6 | 400KV Lines | 4 | 2 | 8
| 7 | 400/220KV Transformer : 315 MVA | 2 | 0 | 2
| 8 | 400KV Shunt Reactor : 80 MVAR | 2 | 1 | 1
| 9 | 400KV Bus Reactor : 125 MVAR | 0 | 0 | 2
| 10 | 400KV Bus Reactor : 80 MVAR | 0 | 1 | 0
| 11 | No. of diameter | 5 | 3 | 7
| 12 | 220KV Lines | 4 | 0 | 4
| 13 | 220KV TBC | 1 | 0 | 1
| 14 | 220KV BC | 1 | 0 | 1
| 15 | No. of diameter | 8 | 0 | 8
| Chooose Combination to added/substracted (in case the none of the configuration matches the given configuration) | [5 empty] | Not Required | 0
[7 empty] | Add | 1
| Base Cost of Sub-Station (INR Crore) |  | 410.1592 |  |  |  | Substract | -1
| S.No. | Combination | Particulars
| 1 | Combination-1 | 765KV Line Ter. Bay with Shunt Reactor
| 2 | Combination-2 | 765KV Line Ter. Bay without Sh. Reactor
| 3 | Combination-3 | 765/400KV Transformer. Bay
| 4 | Combination-4 | 765KV Bus Reactor bay
| 5 | Combination-5 | 765KV Shunt Reactor (Add or Delete)
| 6 | Combination-6 | 400KV Line Ter. Bay with Shunt Reactor
| 7 | Combination-7 | 400KV Line Ter. Bay without Sh. Reactor
| 8 | Combination-8 | 400KV Bus Reactor bay
| 9 | Combination-9 | 400KV Shunt Reactor (Add or Delete)
| 10 | Combination-10 | 220KV Line Ter. bay
| 11 | Combination-11 | 400/220 kV ICT
Possible Combinations
| S.No. | Combination Name | Add/Substract | Values (INR Crore)
|  | None |  |  |  | Combination-1
| 1 | Combination-1 | Not Required | 0 |  | Combination-2
| 2 | Combination-1 | Not Required | 0 |  | Combination-3
| 3 | Combination-3 | Not Required | 0 |  | Combination-4
| 4 | Combination-1 | Not Required | 0 |  | Combination-5
| 5 | Combination-1 | Not Required | 0 |  | Combination-6
| 6 | Combination-1 | Not Required | 0 |  | Combination-7
| 7 | Combination-1 | Not Required | 0 |  | Combination-8
| 8 | Combination-3 | Not Required | 0 |  | Combination-9
| 9 | Combination-1 | Not Required | 0 |  | Combination-10
| 10 | Combination-10 | Not Required | 0
| 11 | Combination-10 | Not Required | 0
| Total Cost of Sub-Station (INR Crores) |  | 410.1592

## Actual Cost
CERC | e
Capital Cost Benchmarking
Transmission Substations
| Name of sub-station |  | Auto Transformer Package T4 for Fatehpur and Agra Sub-Station | 765 KV Auto Transformer Package T3 for Balia Sub-Station | 765 KV Auto Transformer T3 for Lucknow Sub-Station | 765/400/220KV S/S, Seoni | 765KV/400KV Lucknow (New) Sub-Station and Extension of 400 kV Lucknow Sub- Station | Upgradation of 400KV Balia Sub-Station to 765 kV Sub-Station | 765/400 KV S/S-Fatehpur | 765/400 KV S/S-Agra | 765KV Seoni Sub-Station & 765 kV Sipat Transmission System | Up Gradation of 400/220KV Wardha Sub-Station to 765/400/220 kV Voltage Level
| Reference Numbers |  | LOA NO.:C-14807-S016-3/LOA-I/2790 DT:29-12-08 | LOA NO.:C-14803-S016-3/LOA-I/2787 DT: 29-12-2008 | LOA NO.:C-14803-S016-3/LOA-I/2787 DT: 29-12-2008 | Ref : C-32209-S016-7/LOA -1/ 1636 Dated 31-03-2005, | REF.:C-14804-S019A-3/LOA-I 2981 Dated 06/03/2009 | REF.:C-14803-S019 A-3/LOA-I/2963 Dated 05/03/09 | Ref No.C-14807-S019A-3/LOA-I/3020 DATED 26/03/2009 | Ref No.C-14808-S019A-3/LOA-I/3022 DATED 26/03/2009 | Ref. : C-32209-S019A-7/LOA-III/1653 Dated 04/04/2005 | Ref.: RN/JKN/3006-07
| Base Date of Indices |  | 2008-05-01 | 2008-05-01 | 2008-05-01 | 2004-09-01 | 2008-08-01 | 2008-08-01 | 2008-11-01 | 2008-11-01 | 2004-09-01 | 2008-11-01 | 2009-01-01
| SUPPLY | Unit
1 | POWER TRANSFORMER (Single Phase Units)
i | I.C.T 500 MVA, Single Phase, 765/Root3 / 400/Root3 / 33 KV class including insulating Oil | No | 2052.4168 | 2211.2594 | 2171.2994 | 1321.2491
ii | I.C.T 167 MVA, Single Phase, 400/Root3 / 220/Root3 / 33 KV class including insulating Oil | No | 414.69
iii | I.C.T 315 MVA, 3 Phase, 400/220/33 KV including Insulating Oil | No | 807.06
2 | REACTOR & NGR
i | 110 MVAR, 765/Root3KV, Single Phase with oil | No
ii | 80 MVAR, 765/Root3KV, Single Phase with oil | No |  |  |  | 311.8125
iii | 50 MVAR, 765/Root3KV, Single Phase with oil | No | 320.17
iv | NGR (Dry Core Type) for 765KV Reactor | No |  |  |  | 54.09
v | Surge Arrestor for NGR - 765KV System | No |  |  |  | 1.19
vi | 125MVAR, 400KV, 3Ph. Reactor with insulating Oil | No | 366.83
vii | 80MVAR, 400KV, 3Ph. Reactor with insulating Oil | No | 360.39
ix | 63MVAR, 400KV, 3Ph. Reactor with insulating Oil | No | 320.17
x | 50MVAR, 400KV, 3Ph. Reactor with insulating Oil | No | 320.17
xi | NGR for 400KV Reactor with insulating oil | No | 19.42
xii | Surge Arrestor for NGR - 400KV System | No | 1.28
3 | 765 KV EQUIPMENTS
i | 765 kV,3150KA,40KA Circuit Breaker with CR | No |  |  |  |  | 209.1017 | 208.0244 | 189.8928 | 174.9417 | 251.1011 | 178.0664
ii | 765 kV,3150KA,40KA Circuit Breaker without CR | No |  |  |  |  | 169.811 | 166.6479 | 142.6161 | 142.1748 | 186.2885 | 148.1988
iii | 765 kV CTs 3000A, 40KA, 5-Core, | No |  |  |  |  | 31.7487 | 31.7281 | 47.1196 | 27.4461 | 25.4322 | 27.1508
iv | 765 kV CVT 8800 PF | No |  |  |  |  | 22.0435 | 22.0289 | 20.04 | 14.4993 | 11.7868 | 15.1055
v | 765 kV,3150 A,40 kA Isolator 3-Phase with 1 E/S | No |  |  |  |  | 33.762 | 33.0411 | 35.6097 | 32.8901 | 20.2583 | 33.2741
vi | 765 KV,3150 A,40 kA Isolator 3-Phase with 2 E/S | No |  |  |  |  | 41.0183 | 40.2093 | 40.8245 | 38.0519 |  | 0
vii | 765 kV, 2000A, 40KA, S-Phase Isolator with 1 E/S | No | [8 empty] | 7.0434 | 11.5041
viii | 765 kV 3 Phase E/S | No | [9 empty] | 0
ix | 624 kV Surge Arrestor | No |  |  |  |  | 10.8074 | 10.7901 | 10.4002 | 10.3373 | 6.6578 | 9.5824
4 | 765KV C & R Panels
| Circuit Breaker panel with Auto Reclose | [5 empty] | 4.7903 | 4.8042 | 6.7193 | 5.6273 |  | 5.9496
| Circuit Breaker panel without Auto Reclose | [7 empty] | 5.4805 | 5.2473 |  | 5.6821
| Line protection panel | [5 empty] | 28.1958 | 28.2777 | 16.6593 | 23.5314 | 34.5112 | 26.7778
| 765/400KV Transf. protn. panel(both HV and MV) | [5 empty] | 14.041 | 14.0818 | 11.3918 | 16.3416 | 22.9377 | 12.9202
| Reactor Protection Panel | [5 empty] | 11.8563 | 11.8908 | 7.6727 | 10.8057 | 18.7636 | 11.9914
| Bus Bar Protection Panel | [5 empty] | 39.8245 | 44.2082 | 65.1235 |  | 176.6737 | 0
5 | 420KV EQUIPMENTS
| 420KV, 3150A, 40KA Breaker with CR | [5 empty] | 43.099 | 38.5814 | 31.5414 | 40.5309 | 34.2907 | 0
| 420KV, 3150A, 40KA Breaker without CR | [5 empty] | 32.2548 | 28.8969 | 27.7992 | 26.5044 | 32.0958 | 27.36
| 420KV, 3000A, 40KA CT, 5 Core Current Transformer with 120% current rating, | [5 empty] | 7.7783 | 7.3197 | 27.8 | 10.8722 | 6.1438 | 6.8
| 420 kV CVT 4400 PF | [7 empty] | 3.8491 | 3.4082 | 5.4304 | 0
| 420 kV CVT 8800 PF | [5 empty] | 5.7211 | 5.65 |  |  | 4.8268 | 0
| 420 kV,3150 A,40 kA DB Isolator 3 Ph. with 1 E/S | [7 empty] | 4.3623 | 9.6248 | 8.0813 | 10.1
| 420 kV,2000 A,40 kA Isolator 3 Ph. with 1 E/S | [5 empty] | 8.3777 | 7.6412 | 4.1571 | 9.6248 | 7.3421 | 0
| 420 kV,2000A,40 kA Isolator 3 Ph. with 2 E/S | [5 empty] | 9.6064 | 8.1352 | 5.6454 | 11.174 | 9.3983 | 6.21
| 420 kV,2000 A,40 kA DB Isolator S Ph. with 1 E/S | [9 empty] | 2.9816 | 0
| 390 kV Surge Arrestor | [5 empty] | 1.2144 | 1.5969 | 1.0692 | 1.8173 | 1.6452 | 1.4
6 | 400KV C & P Panels
| Circuit Breaker Panel with Auto Reclose | [5 empty] | 4.7903 | 4.8042 | 6.7193 | 5.8823 |  | 5.6821
| Circuit Breaker Panel without Auto Reclose | [5 empty] | 4.7346 | 4.8042 | 5.4619 |  |  | 4.3708
| Line Protection Panel | [5 empty] | 15.8957 |  | 13.4451 |  | 34.5112 | 0
| Transf. Protn. Panel | [7 empty] | 11.3918 |  | 32.1708 | 12.9202
| Reactor Protection Panel | [6 empty] | 12.3929 | 7.6727 | 10.8049 |  | 11.9914
| Bus Bar Protection Panel | [5 empty] | 43.5566 |  | 90.4924 | 77.8815 | 164.8596 | 37.5967
7 | 245KV EQUIPMENTS
i | 245 KV, 1600A, 40KA Class Circuit Breaker | [7 empty] | 12.8304 |  | 15.2691 | 0
ii | 245 KV, 2500A 40KA Class Circuit Breaker | [7 empty] | 12.8304 |  | 15.2692 | 0
iii | 245 KV,1600 A,40 kA ,5 core, CT with 120% extended current | [7 empty] | 3.7422 |  | 2.8107 | 0
iv | 245 KV,1600 A,40 kA ,5 core, CT with 150% extended current | [7 empty] | 3.7422 |  | 3.2576 | 0
v | 245 KV, CVT 4400 pf with 3 secondaries | [7 empty] | 2.9938 |  | 2.918 | 0
vi | 245 KV,1600A, 40 kA, 3Ph.Isolator DB Type - 1 E/S | [7 empty] | 1.7214 |  | 3.5549 | 0
vii | 245KV,1600A, 40 kA, 3-Ph.Isolator DB Type - 2 E/S | [7 empty] | 2.2881 |  | 4.2068 | 0
viii | 245KV,2500A, 40 kA, 3-Ph. Isolator DB Type 2 E/S | [7 empty] | 2.6516 |  | 4.5387 | 0
ix | 245KV, 1600A, 40 KA, 3 Ph.DB Tandem Type without E/S | [7 empty] | 1.1547 |  | 3.2296 | 0
xii | 216 kV Surge Arrestors | [7 empty] | 0.43302 |  |  | 0
8 | 220KV C & P Panels
i | Circuit Breaker panel with Auto Reclose
ii | Circuit Breaker panel without Auto Reclose
iii | Line Protection Panel | [9 empty] | 34.5112
iv | Bus Bar Protection Panel | [9 empty] | 63.3948
9 | COMMON EQUIPMENTS
i | C & P Panel.
Time Synchronisation Equipment
Special Relay Test Kit
Video Projection System(VPS) 67" size
| Complete Substation automation system for 765/400/230kV S/S including hardware and software for remote control station alongthwith associated equipments and Kiosks for the following bays ( bays as defined in the teechnical specification, Sec-Substaion Aut | [5 empty] | 169.9977 | 159.8709 | 48.7099 | 76.2786 | 410.6565
ii | LT Switchgear
| 415V Main Switch Board | [5 empty] | 15.2745 | 15.0164 | 13.0413 | 12.817 | 21.8044
| 415V ACDB | [5 empty] | 16.1029 | 15.2753 | 11.6811 | 13.2157 | 20.707 | 12.3407
| 415V MLDB | [5 empty] | 14.2544 | 14.1273 | 10.3624 | 9.7271 | 7.4028 | 9.1428
| 415V Emergency LDB | [5 empty] | 7.0073 | 5.9946 | 4.7243 | 4.4337 | 1.3977 | 4.2345
| 220V DCDB | [5 empty] | 3.8638 | 3.7102 | 3.359 | 2.4977 | 5.2109 | 4.6582
| 50V DCDB | [5 empty] | 2.5152 | 2.3738 | 2.3206 | 2.2841 | 4.1135 | 4.2351
iii | Battery & Battery Charger
| 220V Battery | [5 empty] | 14.0338 | 8.3448 | 8.04 | 18.5796 | 10.6972 | 8.7852
| 50V Battery | [5 empty] | 3.7708 | 1.435 | 1.931 | 1.9969 | 3.428 | 1.1267
| Battery Charger for 220V Battery | [5 empty] | 6.233 | 4.5679 | 3.3533 | 4.1996 | 2.2486 | 3.1496
| Battery Charger for 50V Battery | [5 empty] | 3.3431 | 2.4511 | 1.5379 | 3.3597 | 1.6998 | 2.9093
iv | DG Set-250KVA with control panel | [5 empty] | 28.5018 | 29.8178 | 44.1668 | 52.0472 | 17.692 | 52.04
v | High Wall Type Split AC unit of 2TR Capacity | [5 empty] | 0.37775 | 0.37138 | 0.33037 | 0.48527 | 0.82125 | 0.43943
vi | Illumination | [5 empty] | 76.9518 | 40.2795 | 143.9835 | 28.713 | 24.4326 | 0
vii | 72.5KV & 36 KV Equipments
| 800KVA 33/.440 KV Distribution Transformer | [5 empty] | 15.053
| 72.5KV circuit breakers(3ph.) | [7 empty] | 5.346
| 72.5KV Isolator without Earthswitch | [7 empty] | 0.5346 |  | 1.422
| 72.5KV Horn gap Fuse | [9 empty] | 0.29893
| 630KVA, 33/.440 KV Distribution Transformer | [7 empty] | 6.9498 | 12.2911
| 33KV Horn gap Fuse | [5 empty] | 0.18 |  |  | 0.48926 | 0.2591
| 33KV Isolator without ES | [5 empty] | 1.7362 |  |  | 0.50939 | 1.1494
| 33KV Surge Arrestor. | [5 empty] | 0.03 |  |  | 0.03 | 0.35925
viii | PLCC Equipments | [5 empty] | 142.6298 | 65.4887 | 107.23 | 54.1046 | 239.7407
3150A, 40KA,Line Trap(For 765KV)
3150A, 40KA, 1 mH Line Trap(for 400KV)
2000A, 40KA, 1 mH Line Trap(for 400KV)
1600, 40KA, 0.5 mH Line Trap(for 220KV)
Coupling device for 765KV
Coupling device for 400KV
Carr Eqpt (for speech+protection and speech+Data)-765KV
Carr Eqpt (for speech+protection and speech+Data)-400KV
Protection coupler-765KV
Protection coupler-400KV
HF Cable
EPAX(24/8) with 24 Telephones,Cables etc.,
Testing and Mainetance equipment
10 | Mandatory Spares | [5 empty] | 369.0534 | 405.0926 | 486.522 | 241.8542 | 222.8598
11 | ERECTION HARDWARE
i | 765 KV
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary | [5 empty] | 450.8194 | 635.9414 | 721.2705 | 360.4526 | 300.3446
765KV I Type Layout
Line bay
Transformer bay
Bus Reactor bay
Line Reactors
Bus(for one diameter)
ii | 400 KV
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary | [5 empty] | 264.0093 | 221.5582 | 506.8767 | 389.1007 | 205.3737
400 KV I Type Layout
Line bay
Transformer bay
Re-oriented Line bay
Spare bay of half dia
Line Reactor
Bus for two diameters
iii | 220 KV
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary | [7 empty] | 135.0367 |  | 100.8077
220 KV DMT Type Layout
Line bay
Transformer bay
Main & Transfer Bus
Transfer bus coupler bay
Bus coupler bay
12 | Visual Monitoring system for watch & ward
13 | Fire Protection System | [5 empty] | 180.4204 | 195.4258 | 303.05 | 458.9451 | 132.1394
i | Pumping arrangement forHVW system and Hydrant System, complete with all piping, valves, fittings etc., inside pump House (Set)
ii | Hydrant system, complete U/G and O/G piping and accessories etc., outside the the pump House for(Set)
iii | HVW Sprray system complete with U/G and O/G pipeing and accessories etc out side the pump house along with one hydrant point for each of the following
765KV S-Phase Transformer
400KV 3-Phase Transformer
765KV S-Phase Shunt Reactor
765KV S-Phase Bus Reactor
400KV 3-Phase Shunt Reactor
400KV 3-Phase Bus Reactor
iv | Portable extinguishers (Set)
v | Smoke detection system(Set)
14 | Illumination -- Indoor + Outdoor | [7 empty] | 143.9835
i | Switchyard Lighting | [9 empty] | 24.4326
ii | Street Lighting | [8 empty] | 28.713 | 60.3799
15 | Power & Control Cables : Per Km Rate | Lump-Sum
i | Power Cable - | [11 empty] | 1.47
ii | Control Cable | [11 empty] | 1.1
Cables with associated accessories likeclamps, glands, lugs and straight joints etc.,(LS)
i | 1.1KV Power Cables
a | 1C 630Sq.mm(XLPE)
b | 1C 300Sq.mm(XLPE)
c | 3.5C 300Sq.mm(XLPE)
d | 1C 150Sq. Mm(PVC)
e | 3.5C 70 Sq.mm(PVC)
ii | 1.1KV Power Cables(PVC) for 765KV S/S
a | 3.5C 35Sq.mm
b | 4C 16Sq.mm
c | 4C 6Sq.mm
d | 2C 6Sq.mm
ii | 1.1KV grade control cables(PVC) 765KV S/S
a | 5C 2.5Sq.mm
b | 7C 2.5Sq.mm
c | 10C 2.5Sq.mm
d | 14C 2.5Sq.mm
e | 19C 2.5Sq.mm
f | 27C 2.5Sq.mm
iv | 1.1KV Power Cables(PVC) for 400KV S/S
a | 3.5C 35Sq.mm
b | 4C 16Sq.mm
c | 4C 6Sq.mm
d | 2C 6Sq.mm
v | 1.1KV grade control cables(PVC) 400KV S/S
a | 5C 2.5Sq.mm
b | 7C 2.5Sq.mm
c | 10C 2.5Sq.mm
d | 14C 2.5Sq.mm
e | 19C 2.5Sq.mm
f | 27C 2.5Sq.mm
vi | 1.1KV Power Cables(PVC) for 220KV S/S
a | 3.5C 35Sq.mm
b | 4C 16Sq.mm
c | 4C 6Sq.mm
vii | 1.1KV grade control cables(PVC) 220KV S/S
a | 5C 2.5Sq.mm
b | 7C 2.5Sq.mm
c | 10C 2.5Sq.mm
d | 14C 2.5Sq.mm
e | 19C 2.5Sq.mm
f | 27C 2.5Sq.mm
| Power & Control Cables : Total Price | [5 empty] | 252.1241 | 333.1599 |  | 212.4166
| Power Cable - | [5 empty] | 102.9601
viii | Control Cable
| Control Cable | [5 empty] | 149.164 |  |  |  | 155.3201
16 | Main Earthmat - 40 mm MS Rod Rate Per Km | [5 empty] | 5.3 | 5.2081 | 4.3002 | 5.6397 | 3.3088
40mm MS Rods - 46Km
| Main Earthmat - 40 mm MS Rod : Total Price | [5 empty] | 204.4081 |  | 101.4157 | 217.7465 | 155.3201
17 | Steel Structures (Rate Per MT)
i | MS | [5 empty] | 0.73091 | 0.71545 | 0.61936 |  | 0.72 |  | 0.6
ii | HT | [5 empty] | 0.78 |  | 0.60115 |  | 0.83 |  | 0.8
| Steel Structures Total price | [8 empty] | 1128.0265
| Lattice Type - : Total Price | [5 empty] | 923.5144 | 0.71545 | 295.6012 |  | 413.8642
| H.T steel - Total Price | [5 empty] | 75.2111 |  | 38.002 |  | 123.4303
ERECTION
1 | POWER TRANSFORMER (Single Phase Units)
i | I.C.T 500 MVA, Single Phase, 765/Root3 / 400/Root3 / 33 KV class including insulating Oil | No
ii | I.C.T 167 MVA, Single Phase, 400/Root3 / 220/Root3 / 33 KV class including insulating Oil | No
iii | I.C.T 315 MVA, 3 Phase, 400/220/33 KV including i Insulating Oil | No
2 | REACTOR & NGR
i | 110 MVAR, 765/Root3KV, Single Phase with oil | No
ii | 80 MVAR, 765/Root3KV, Single Phase with oil | No
iii | 50 MVAR, 765/Root3KV, Single Phase with oil | No
iv | NGR (Dry Core Type) for 765KV Reactor | No
v | Surge Arrestor for NGR - 765KV System | No
vi | 125MVAR, 400KV, 3Ph. Reactor with insulating Oil | No
vii | 80MVAR, 400KV, 3Ph. Reactor with insulating Oil | No
ix | 63MVAR, 400KV, 3Ph. Reactor with insulating Oil | No
x | 50MVAR, 400KV, 3Ph. Reactor with insulating Oil | No
xi | NGR for 400KV Reactor with insulating oil | No
xii | Surge Arrestor for NGR - 400KV System | No
3 | 765 KV EQUIPMENTS
i | 765 Kv,3150KA,40KA Circuit Breaker with CR | No
ii | 765 Kv,3150KA,40KA Circuit Breaker without CR | No
iii | 765 kV CTs 3000A, 40KA, 5-Core, | No
iv | 765 kv CVT 4400 PF | No
v | 765 KV,3150 A,40 kA Isolator 3-Phase with 1 E/S | No
vi | 765 KV,3150 A,40 kA Isolator 3-Phase with 2 E/S | No
vii | 765KV, 2000A, 40KA, S-Phase Isolator with 1 E/S | No
viii | 765 KV 3 Phase E/S | No
ix | 624KV Surge Arrestor | No
4 | 765KV C & R Panels
Circuit Breaker panel with Auto Reclose
Circuit Breaker panel without Auto Reclose
Line protection panel
765/400KV Transf. protn. panel(both HV and MV)
Reactor protection panel
Bus Bar Protection Panel
5 | 420KV EQUIPMENTS
420KV, 3150A, 40KA Breaker with CR
420KV, 3150A, 40KA Breaker without CR
420KV, 3000A, 40KA CT, 5 Core Current Transformer with 120% current rating,
420 kv CVT 4400 PF
420 kv CVT 8800 PF
420 KV,2000 A,40 kA DB Isolator 3 Ph. with 1 E/S
420 KV,3150A,40 kA Isolator 3 Ph. with 1 E/S
420 KV,3150A,40 kA Isolator 3 Ph. with 2 E/S
420 KV,2000 A,40 kA DB Isolator S Ph. with 1 E/S
390KV Surge Arrestor
6 | 400KV C & P Panels
Circuit Breaker panel without Auto Reclose
Circuit Breaker panel without Auto Reclose
Line protection panel
400/220KV Transf. protn. panel(both HV and MV)
Reactor protection panel
Bus Bar Protection Panel
7 | 245KV EQUIPMENTS
i | 245 KV, 1600A, 40KA Class Circuit Breaker
ii | 245 KV, 2500A 40KA Class Circuit Breaker
iii | 245KV,1600 A,40 kA ,5 core, CT with 120% extended current
iv | 245KV,1600 A,40 kA ,5 core, CT with 150% extended current
v | 245KV, CVT 4400 pf with 3 secondaries
vi | 245KV,1600A, 40 kA, 3Ph.Isolator DB Type - 1 E/S
vii | 245KV,1600A, 40 kA, 3-Ph.Isolator DB Type - 2 E/S
viii | 245KV,2500A, 40 kA, 3-Ph. Isolator DB Type 2 E/S
ix | 245KV, 1600A, 40 KA, 3 Ph.DB Tandem Type without E/S
x | 245KV,1600A, 40kA S Ph. Isolator DB Type - 1E/S
xi | 245KV,1600A, 40kA S Ph. Isolator DB Type w/o E/S
xii | 216 kV Surge Arrestors
8 | 220KV C & P Panels
i | Circuit Breaker panel with Auto Reclose
ii | Circuit Breaker panel without Auto Reclose
iii | Line protection panel
iv | Bus Bar Protection panel
9 | COMMON EQUIPMENTS
i | C & P Panel.
Time Synchronisation Equipment
Special Relay Test Kit
Video Projection System(VPS) 67" size
Complete Substation automation system for 400/230kV S/S including hardware and software for remote control station alongthwith associated equipments and Kiosks for the following bays ( bays as defined in the teechnical specification, Sec-Substaion Automat
ii | LT Switchgear
415V Main Switch Board
415V ACDB
415V MLDB
415V Emergency LDB
220V DCDB
50V DCDB
iii | Battery & Battery Charger
220V Battery
50V Battery
Battery Charger for 220V Battery
Battery Charger for 50V Battery
iv | DG Set-250KVA with control panel
v | High Wall Type Split AC unit of 2TR Capacity
vi | Illumination (Indoor)
vii | 72.5KV & 36 KV Equipments
800KVA 33/.440 KV Distribution Transformer
72.5KV Isolator without Earthswitch
72.5KV Horn gap Fuse
630KVA, 33/.440 KV Distribution Transformer
33KV Horn gap Fuse
33KV Isolator without ES
33KV Surge Arrestor.
viii | PLCC Equipments
3150A, 40KA,Line Trap(For 765KV)
3150A, 40KA, 1 mH Line Trap(for 400KV)
2000A, 40KA, 1 mH Line Trap(for 400KV)
1600, 40KA, 0.5 mH Line Trap(for 220KV)
Coupling device for 765KV
Coupling device for 400KV
Carr Eqpt (for speech+protection and speech+Data)-765KV
Carr Eqpt (for speech+protection and speech+Data)-400KV
Protection coupler-765KV
Protection coupler-400KV
HF Cable
EPAX(24/8) with 24 Telephones,Cables etc.,
Testing and Mainetance equipment
10 | Mandatory Spares
11 | ERECTION HARDWARE
i | 765 KV
Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary
765KV I Type Layout
Line bay
Transformer bay
Bus Reactor bay
Line Reactors
Bus(for one diameter)
ii | 400 KV
Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary
400 KV I Type Layout
Line bay
Transformer bay
Re-oriented Line bay
Spare bay of half dia
Line Reactor
Bus for two diameters
iii | 220 KV
Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary
220 KV DMT Type Layout
Line bay
Transformer bay
Main & Transfer Bus
Transfer bus coupler bay
Bus coupler bay
12 | Visual Monitoring system for watch & ward
13 | Fire Protection System
i | Pumping arrangement forHVW system and Hydrant System, complete with all piping, valves, fittings etc., inside pump House (Set)
ii | Hydrant system, complete U/G and O/G piping and accessories etc., outside the the pump House for(Set)
ii | HVW Sprray system complete with U/G and O/G pipeing and accessories etc out side the pump house along with one hydrant point for each of the following
765KV S-Phase Transformer
400KV 3-Phase Transformer
765KV S-Phase Shunt Reactor
765KV S-Phase Bus Reactor
400KV 3-Phase Shunt Reactor
400KV 3-Phase Bus Reactor
iii | Portable extinguishers (Set)
iv | Smoke detection system(Set)
14 | Illumination(Outdoor)
i | Switchyard Lighting
ii | Street Lighting
15 | Power & Control Cables - Total
Cables with associated accessories likeclamps, glands, lugs and straight joints etc.,(LS)
i | 1.1KV Power Cables
1C 630Sq.mm(XLPE)
1C 300Sq.mm(XLPE)
3.5C 300Sq.mm(XLPE)
1C 150Sq. Mm(PVC)
3.5C 70 Sq.mm(PVC)
ii | 1.1KV Power Cables(PVC) for 765KV S/S
3.5C 35Sq.mm
4C 16Sq.mm
4C 6Sq.mm
2C 6Sq.mm
iii | 1.1KV grade control cables(PVC) 765KV S/S
5C 2.5Sq.mm
7C 2.5Sq.mm
10C 2.5Sq.mm
14C 2.5Sq.mm
19C 2.5Sq.mm
27C 2.5Sq.mm
iv | 1.1KV Power Cables(PVC) for 400KV S/S
3.5C 35Sq.mm
4C 16Sq.mm
4C 6Sq.mm
2C 6Sq.mm
v | 1.1KV grade control cables(PVC) 400KV S/S
5C 2.5Sq.mm
7C 2.5Sq.mm
10C 2.5Sq.mm
14C 2.5Sq.mm
19C 2.5Sq.mm
27C 2.5Sq.mm
vi | 1.1KV Power Cables(PVC) for 220KV S/S
3.5C 35Sq.mm
4C 16Sq.mm
4C 6Sq.mm
vii | 1.1KV grade control cables(PVC) 220KV S/S
5C 2.5Sq.mm
7C 2.5Sq.mm
10C 2.5Sq.mm
14C 2.5Sq.mm
19C 2.5Sq.mm
27C 2.5Sq.mm
viii | HT Cable - 33KV Cable(Single Core)
Erection Rate Per Km
16 | Main Earthmat - 40 mm MS Rod 46Km- Total
Erection Rate Per Km
17 | Steel Structures (MT)
i | Lattice Type - Rate Per MT
ii | Pipe Type - Rate Per MT
Lattice Type - Total Price
Pipe Type - Total Price
CIVIL WORKS
1 | Control room cum Administrative Building | [11 empty] | 70
2 | DG & FFPH Building | [11 empty] | 120
3 | Water supply & Sanitary System | [11 empty] | 30
4 | Foundation
765KV I.C.T 500 MVA, Single Phase(Complete)
765KV Shunt Reactor with NGR & SA(Complete)
765KV Bus Reactor (Complete)
Gantry structures(RCC Portion)
Equipment support structures(RCC Portion)
5 | Roads/Tracks | [11 empty] | 0.018942
Road cum Rail Track (from edge of road to edge of Tr. Foundn)
Road cum Rail Track (from edge of road to edge of Rtr.Foundn)
Roads inside Switchyard (3.75M & 7.0M) with crossings
6 | Cable Trenches (including Buried) | [11 empty] | 0.03
7 | Site Surfacing & Antiweed Treatment | [11 empty] | 0.00052196
8 | Storm water Drains with culverts | [11 empty] | 0.015599
9 | Switchyard Fencing | [11 empty] | 0.00072
10 | Rain water Harvesting
11 | Land Scaping
12 | Parking Shed | [11 empty] | 35
Total
Foundations
| Foundation - 765KV S Phase Transformer | [11 empty] | 20
| Foundation - 400/220 KV 3 Phase Transformer | [11 empty] | 15
| Foundation - 400/220 KV S Phase Transformer | [11 empty] | 15
| Fire wall between the Transformers | [11 empty] | 2
| Foundation for 765KV Shunt Reactor | [11 empty] | 10
| Foundation for NGR & SA of 765KV System | [11 empty] | 3
| Foundation for 400KV Reactor with NGR & SA | [11 empty] | 10
| Fire wall between the Shunt Reactors | [11 empty] | 1
| Foundation for 765KV S Phase Bus Reactor | [11 empty] | 10
| Foundation for 400KV 3 Phase Bus Reactor | [11 empty] | 10
| Fire wall between the Bus Reactors | [11 empty] | 1
| Foundations for Gantries, Equipments (Other than ICTs 7 Reactors) and Equipment Support Structures (Lumpsum) | [11 empty] | 1000
Erection,Testing & Commissioning of Common Equipments
| Auxiliary Transformers, LT Switchgear, AC & DC Panels. 72.5 kV, 33kV, 11 kV equipments etc | [11 empty] | 3
| Station D.C Batteries 220 V System | [11 empty] | 0.2496
| Station D.C Batteries 48 / 50 V System | [11 empty] | 0.104
| Battery Charger for 220 V DC Battery System | [11 empty] | 0.2
| Battery Charger for 48 / 50 V DC Battery System | [11 empty] | 0.15
| Sub-Station Automation including Hardware, software, Remote Control Station, DMT scheme, Time Synchronising equipment, A/C kiosks etc., | [11 empty] | 10
| Visual Monitoring System | [11 empty] | 3
| Power cables | [11 empty] | 0.2
| Control cables | [11 empty] | 0.2
| Earth mat formation | [11 empty] | 15
| Diesel Generator set with AMF panel 250 kVA | [11 empty] | 1
| Air Conditioning and Ventilation | [11 empty] | 1
| Fire Fighting System | [11 empty] | 24
| Illumination System - Indoor & outdoor | [11 empty] | 10
| PLCC Equipments (Total for the Sub - Station) | [11 empty] | 2
| Erection,Testing & Commng -765KV S Phase Transformer | [11 empty] | 10
| Erection,Testing & Commng-400/220KV 3 Phase Transf | [11 empty] | 6
| Erection, Testng & Commng-400/220KV S Ph. Transformer | [11 empty] | 6
| Erection, Testng & Commng - 765KV Shunt Reactor | [11 empty] | 4
| Erection, Testng & Commng - NGR & SA of 765KV Shunt Reactor | [11 empty] | 4
| Erection, Testng & Commng - 400KV Reactor with NGR & SA | [11 empty] | 1
| Erection, Testng & Commng - 765KV, S Phase Bus Reactor | [11 empty] | 4
| Erection, Testng & Commng - 400KV 3 Phase Bus Reactor | [11 empty] | 4
Erection Testing & commisioning of 765KV Equipments
| 765KV Circuit breakers | [11 empty] | 0.93
| 765KV Isolators | [11 empty] | 0.87
| 765KV Current Transformers | [11 empty] | 0.5
| 765KV CVT | [11 empty] | 0.5
| 624KV Surge Arrestor | [11 empty] | 0.25
| Bus Bars formation etc. | [11 empty] | 60
Control & Protection panels
| 765KV CB relay Panel with Auto Reclosure | [11 empty] | 0.2
| 765KV CB relay Panel without Auto Reclosure | [11 empty] | 0.2
| 765KV Line Protection Panel | [11 empty] | 0.2
| 765-400/33KV Transformer Protection Panel | [11 empty] | 0.2
| 765KV Reactor Protection Panel | [11 empty] | 0.2
| Duplicate Bus Bar Protection Panel - 765KV | [11 empty] | 0.8
Erection Testing & commisioning of 400 kV Equipments
| 420 KV Circuit breakers | [11 empty] | 0.3
| 420KV Isolators | [11 empty] | 0.2
| 420 KV Current Transformers | [11 empty] | 0.06
| 420KV CVT | [11 empty] | 0.06
| 390KV surge Arrestors | [11 empty] | 0.03
| Bus Bars formation etc | [11 empty] | 30
C & P panels
| 400KV CB relay Panel with Reclosure | [11 empty] | 0.3
| 400KV CB relay Panel without Auto Reclosure | [11 empty] | 0.9
| 400KV Line Protection Panel | [11 empty] | 0.54652
| 400-220/33KV Transformer Protection Panel | [11 empty] | 0.095568
| 400KV Reactor Protection Panel | [11 empty] | 1.5984
| 400KV Bus Bar Protection panelPanel | [11 empty] | 1.25
| 245 KV Circuit breakers | [11 empty] | 0.2
| 245 KV Isolators | [11 empty] | 0.15
| 245 KV Current Transformers | [11 empty] | 0.05
| 245 KV CVT | [11 empty] | 0.05
| 216 KV surge Arrestors | [11 empty] | 0.03
| 220 kV Bus Bars formation etc | [11 empty] | 15
220KV C & P Panels
| Circuit breaker relay panel | [11 empty] | 0.25
| Line protection panel | [11 empty] | 0.66
| Single Bus Bar protection panel | [11 empty] | 2
| Lattice Type | [11 empty] | 0.0199
| Tubular Type | [11 empty] | 0.023

## Indices
CERC
Capital Cost Benchmarking
| S.No. | Particulars | Units | 2002-01-01 | 2002-02-01 | 2002-03-01 | 2002-04-01 | 2002-05-01 | 2002-06-01 | 2002-07-01 | 2002-08-01 | 2002-09-01 | 2002-10-01 | 2002-11-01 | 2002-12-01 | 2003-01-01 | 2003-02-01 | 2003-03-01 | 2003-04-01 | 2003-05-01 | 2003-06-01 | 2003-07-01 | 2003-08-01 | 2003-09-01 | 2003-10-01 | 2003-11-01 | 2003-12-01 | 2004-01-01 | 2004-02-01 | 2004-03-01 | 2004-04-01 | 2004-05-01 | 2004-06-01 | 2004-07-01 | 2004-08-01 | 2004-09-01 | 2004-10-01 | 2004-11-01 | 2004-12-01 | 2005-01-01 | 2005-02-01 | 2005-03-01 | 2005-04-01 | 2005-05-01 | 2005-06-01 | 2005-07-01 | 2005-08-01 | 2005-09-01 | 2005-10-01 | 2005-11-01 | 2005-12-01 | 2006-01-01 | 2006-02-01 | 2006-03-01 | 2006-04-01 | 2006-05-01 | 2006-06-01 | 2006-07-01 | 2006-08-01 | 2006-09-01 | 2006-10-01 | 2006-11-01 | 2006-12-01 | 2007-01-01 | 2007-02-01 | 2007-03-01 | 2007-04-01 | 2007-05-01 | 2007-06-01 | 2007-07-01 | 2007-08-01 | 2007-09-01 | 2007-10-01 | 2007-11-01 | 2007-12-01 | 2008-01-01 | 2008-02-01 | 2008-03-01 | 2008-04-01 | 2008-05-01 | 2008-06-01 | 2008-07-01 | 2008-08-01 | 2008-09-01 | 2008-10-01 | 2008-11-01 | 2008-12-01 | 2009-01-01 | 2009-02-01 | 2009-03-01 | 2009-04-01 | 2009-05-01 | 2009-06-01 | 2009-07-01 | 2009-08-01 | 2009-09-01 | 2009-10-01 | 2009-11-01 | 2009-12-01 | 2010-01-01 | 2010-02-01 | 2010-03-01 | 2010-04-01 | 2010-05-01 | 2010-06-01 | 2010-07-01 | 2010-08-01 | 2010-09-01 | 2010-10-01 | 2010-11-01 | 2010-12-01 | 2011-01-01 | 2011-02-01 | 2011-03-01 | 2011-04-01 | 2011-05-01 | 2011-06-01 | 2011-07-01 | 2011-08-01 | 2011-09-01 | 2011-10-01 | 2011-11-01 | 2011-12-01 | 2012-01-01 | 2012-02-01 | 2012-03-01 | 2012-04-01 | 2012-05-01 | 2012-06-01 | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-02 | 2014-02-02 | 2014-03-02
| 1 | LT Transformer
| i | Copper |  | 117662 | [19 empty] | 105116 | [5 empty] | 161583 |  |  |  | 150346 | 151962 | 156101 | 156101 | 162132 |  | 161959 |  |  |  | 155105 |  |  | 169400 | 183947 |  |  |  | 234065 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 343064 | 310398 | 327855 | 350128 | 340897 | 291788 | 271169 | 298979 | 384365 | 3,56,028 | 374688 | 3,78,574 | 3,78,065 | 3,79,097 | 3,42,410 | 3,49,353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258059 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| ii | Electrical Steel sheet -CRGO |  | 125048 | [19 empty] | 82245 | [5 empty] | 84522 |  |  |  | 96618 | 82864 | 101482 | 84681 | 86634 |  | 101372 |  |  |  | 161048 |  |  | 174600 | 212825 |  |  |  | 200074 | 195894 | 194855 | 221331 | 204827 | 203822 | 212009 | 210100 | 209593 | 200334 | 203675 | 198712 | 200218 | 195011 | 196183 | 191168 | 182565 | 185109 | 219073 | 198404 | 209701 | 215120 | 192092 | 195575 | 188296 | 194326 | 231172 | 1,95,118 | 203869 | 2,12,968 | 2,15,227 | 2,25,373 | 2,29,721 | 2,43,082 | 238764 | 230946 | 250205 | 228507 | 237253 | 222515 | 219799 | 186754 | 187491 | 182536 | 170393 | 164804 | 162203 | 157341 | 152995
| iii | Iron & Steel |  | 137.6 | [19 empty] | 166.1 | [5 empty] | 198.7 |  |  |  | 239.8 | 242.9 | 237.2 | 237.2 | 237.2 |  | 239.9 |  |  |  | 258.8 |  |  | 256.3 | 259.7 |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 268.3 | 276.7 | 276.7 | 217.22 | 276.7 | 277.3 | 277.9 | 280.1 | 280.6 | 280.6 | 287 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| iv | Insulating Materials |  | 185.45 | [19 empty] | 185.45 | [5 empty] | 310.82 |  |  |  | 309.36 | 287.76 | 313.74 | 286.59 | 290.5 |  | 346.69 |  |  |  | 289.25 |  |  | 229.85 | 301.15 |  |  |  | 286.83 | 288.92 | 300.68 | 309.05 | 308.45 | 307,52 | 306.86 | 303.78 | 302.1 | 290.46 | 287.38 | 286.94 | 286.94 | 286.94 | 286.94 | 282.48 | 282.48 | 282.48 | 331.53 | 275.4 | 305.11 | 281.76 | 281.17 | 286.55 | 302.69 | 311.55 | 375.31 | 365.31 | 373.3 | 374.56 | 389.66 | 411.88 | 406.98 | 399.71 | 392.28 | 390.17 | 387.81 | 363.11 | 359.59 | 384.24 | 373.24 | 381.53 | 392.25 | 407.77 | 408.76 | 408.76 | 403.14 | 403.35 | 405.91
| v | Transformer Oil |  | 35513 | [19 empty] | 21014 | [5 empty] | 40560 |  |  |  | 43210 | 43210 | 43210 | 43435 | 44335 |  | 44335 |  |  |  | 39160 |  |  | 39923 | 39923 |  |  |  | 34017 | 34017 | 36127 | 38018 | 38018 | 40350 | 40655 | 42602 | 42241 | 43946 | 41113 | 38995 | 38779 | 38562 | 38661 | 38183 | 36487 | 35573 | 35704 | 35269 | 37131 | 49950 | 35827 | 35827 | 36319 | 38599 | 39304 | 39304 | 40182 | 45215 | 49538 | 56272 | 59080 | 56642 | 54287 | 53145 | 52986 | 49375 | 46625 | 46250 | 45500 | 44125 | 44125 | 47300 | 47250 | 50950 | 50375 | 49625 | 50625
| vi | Labour |  | 111.9552 | [19 empty] | 117.3648 | [5 empty] | 118.5408 |  |  |  | 121.5984 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.4784 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.19 | 150.2787 | 151.3677 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 2 | Power Transformers
| i | Copper |  | 117662 | [19 empty] | 105116 | [5 empty] | 161583 |  |  |  | 150346 | 151962 | 156101 | 156101 | 162132 |  | 161959 |  |  |  | 155105 |  |  | 169400 | 183947 |  |  |  | 234065 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 343064 | 310398 | 327855 | 350128 | 340897 | 291788 | 271169 | 298979 | 384365 | 356028 | 374688 | 378574 | 3,78,065 | 379097 | 342410 | 3,49,353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258059 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| ii | Electrical Steel sheet -CRGO |  | 125048 | [19 empty] | 82245 | [5 empty] | 84522 |  |  |  | 96618 | 95664 | 101482 | 84681 | 86634 |  | 101372 |  |  |  | 186476 |  |  | 188786 | 212825 |  |  |  | 200074 | 195894 | 194855 | 221331 | 204827 | 203822 | 212009 | 210100 | 209593 | 200334 | 203675 | 198712 | 200218 | 195011 | 196183 | 191168 | 182565 | 185109 | 219073 | 198404 | 209701 | 191920 | 192092 | 195575 | 188296 | 194326 | 231172 | 195118 | 203869 | 212968 | 2,15,227 | 225373 | 229721 | 2,43,082 | 238764 | 230946 | 250205 | 228507 | 237253 | 222515 | 219799 | 186754 | 187491 | 182536 | 170393 | 164804 | 162203 | 157341 | 152995
| iii | Iron & Steel |  | 137.6 | [19 empty] | 166.1 | [5 empty] | 198.7 |  |  |  | 239.8 | 242.9 | 237.2 | 237.2 | 237.2 |  | 239.9 |  |  |  | 258.8 |  |  | 256.3 | 259.7 |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 268.3 | 276.7 | 276.7 | 217.22 | 276.7 | 277.3 | 277.9 | 280.1 | 280.6 | 280.6 | 287.4 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| iv | Insulating Material |  | 185.45 | [19 empty] | 185.45 | [5 empty] | 310.82 |  |  |  | 309.36 | 315.02 | 313.74 | 286.59 | 290.5 |  | 346.69 |  |  |  | 316.65 |  |  | 251.56 | 301.15 |  |  |  | 286.83 | 288.92 | 300.68 | 309.05 | 308.45 | 307.52 | 306.86 | 303.78 | 302.1 | 290.46 | 287.38 | 286.94 | 286.94 | 286.94 | 286.94 | 282.48 | 282.48 | 282.48 | 331.53 | 275.4 | 305.11 | 281.76 | 281.17 | 286.55 | 302.69 | 311.55 | 365.31 | 365.31 | 373.71 | 374.56 | 389.66 | 411.88 | 406.98 | 399.71 | 392.28 | 390.17 | 387.81 | 363.11 | 359.59 | 384.24 | 373.24 | 381.53 | 392.25 | 407.77 | 408.76 | 408.76 | 403.14 | 403.35 | 405.91
| v | Transformer Oil |  | 35513 | [19 empty] | 21014 | [5 empty] | 40560 |  |  |  | 43210 | 43210 | 43210 | 43435 | 44335 |  | 44335 |  |  |  | 39160 |  |  | 39923 | 39923 |  |  |  | 34017 | 34017 | 36127 | 38018 | 38018 | 40350 | 40655 | 42602 | 42241 | 43946 | 41113 | 38995 | 38779 | 38562 | 38661 | 38183 | 36487 | 35573 | 35269 | 32484 | 36007 | 49950 | 35827 | 35827 | 36319 | 38599 | 39304 | 39304 | 40182 | 45215 | 49538 | 56272 | 59080 | 56642 | 54287 | 53145 | 52986 | 49375 | 46625 | 46250 | 45500 | 44125 | 44125 | 47300 | 47250 | 50950 | 50375 | 49625 | 50625
| vi | Labour |  | 111.9552 | [19 empty] | 117.3648 | [5 empty] | 118.5408 |  |  |  | 121.5984 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.4784 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.1897 | 150.2787 | 151.3677 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 3-A | Circuit Breaker(From India)
| i | Iron & Steel |  | 137.6 | [19 empty] | 166.1 | [5 empty] | 198.7 |  |  |  | 242.9 | 242.9 | 237.2 | 237.2 | 237.2 |  | 237.2 |  |  |  | 258.8 |  |  | 256.3 | 256.3 |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 267.2 | 268.7 | 268.3 | 217.22 | 276.7 | 277.3 | 277.9 | 280.13 | 280.6 | 280.6 | 287.4 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| ii | Copper |  | 117662 | [19 empty] | 121706 | [5 empty] | 180263 |  |  |  | 170202 | 170202 | 171962 | 171962 | 177245 |  | 177245 |  |  |  | 174024 |  |  | 196067 | 196067 |  |  |  | 245956 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 327276 | 343064 | 328486 | 350128 | 299451 | 283695 | 302578 | 340650 | 384365 | 356028 | 374688 | 378574 | 3,78,065 | 379097 | 342410 | 3,49,353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258059 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| iii | Alluminium |  | 104050 | [19 empty] | 107950 | [5 empty] | 109025 |  |  |  | 114325 | 114325 | 117325 | 117325 | 117325 |  | 117325 |  |  |  | 124650 |  |  | 117050 | 117050 |  |  |  | 140300 | 146300 | 147800 | 148800 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 166300 | 162900 | 162900 | 160400 | 159400 | 155900 | 152900 | 155900 | 148900 | 145900 | 147400 | 144900 | 141400 | 143400 | 141317 | 163400 | 167400 | 175400 | 1,74,400 | 178400 | 167400 | 159465 | 151836 | 141398 | 131900 | 128400 | 128400 | 128400 | 131400 | 126900 | 132400 | 144650 | 150650 | 146650 | 148150 | 151150 | 162650
| iv | Epoxy Resin |  | 168 | [19 empty] | 168 | [5 empty] | 168 |  |  |  | 168 | 168 | 168 | 168 | 168 |  | 168 |  |  |  | 168 |  |  | 168 | 168 |  |  |  | 168 | 168 | 168 | 168 | 168 | 168 | 180 | 180 | 180 | 180 | 180 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188
| v | Labour |  | 111.9552 | [19 empty] | 117.3648 | [5 empty] | 118.5408 |  |  |  | 122.7744 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.008 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.19 | 150.2787 | 151.3677 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 3-B | Circuit Breaker(From Abroad)
| i | Steel | [77 empty] | 258.8 |  |  | 258.8 |  |  | 0 |  | 0
| ii | Copper | [77 empty] | 213 |  |  | 213 |  |  | 0 |  | 0
| iii | Alluminium | [77 empty] | 116.8 |  |  | 116.8 |  |  | 0 |  | 0
| iv | Labour | [77 empty] | 142.5 |  |  | 142.5 |  |  | 0 |  | 0
| 4-A | Current Transformer (From India)
| i | Copper |  | 117662 | [19 empty] | 121706 | 0 | 0 |  |  |  | 161583 |  |  |  | 170202 | 170202 | 170202 | 171962 | 177245 |  | 177245 |  |  |  | 174024 |  |  | 196067 | 196067 |  |  |  | 234065 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 343064 | 310398 | 327855 | 350128 | 340897 | 291788 | 271169 | 298979 | 384365 | 356028 | 374688 | 378574 | 3,78,065 | 379097 | 342410 | 3,49,353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258090 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| ii | Electrical Steel sheet -CRGO |  | 125048 | [19 empty] | 82245 | 0 | 0 |  |  |  | 84522 |  |  |  | 82864 | 82864 | 82864 | 84681 | 86634 |  | 86634 |  |  |  | 161048 |  |  | 188786 | 188786 |  |  |  | 200074 | 195894 | 194855 | 221331 | 204827 | 203822 | 212009 | 210100 | 209593 | 200334 | 203675 | 198712 | 200218 | 195011 | 196183 | 191168 | 182565 | 185109 | 219073 | 198404 | 209701 | 215120 | 192092 | 195575 | 188296 | 194326 | 231172 | 195118 | 203869 | 212968 | 2,15,227 | 225373 | 229721 | 2,43,082 | 238764 | 230946 | 250205 | 228507 | 237253 | 222515 | 219799 | 186754 | 187491 | 182536 | 170393 | 164804 | 162203 | 157341 | 152995
| iii | Iron & Steel |  | 137.6 | [19 empty] | 166.1 | 0 | 0 |  |  |  | 198.7 |  |  |  | 242.9 | 242.9 | 242.9 | 237.2 | 237.2 |  | 237.2 |  |  |  | 258.8 |  |  | 256.3 | 256.3 |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 268.3 | 276.7 | 276.7 | 217.22 | 276.7 | 277.3 | 277.9 | 280.1 | 280.6 | 280.6 | 287 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| iv | Aluminium |  | 104050 | [19 empty] | 107950 | 0 | 0 |  |  |  | 109025 |  |  |  | 114325 | 114325 | 114325 | 117325 | 117325 |  | 117325 |  |  |  | 124650 |  |  | 117050 | 117050 |  |  |  | 140300 | 146300 | 147800 | 148800 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 166300 | 162900 | 162900 | 160400 | 159400 | 155900 | 152900 | 155900 | 148900 | 145900 | 147400 | 144900 | 141400 | 143400 | 141317 | 163400 | 167400 | 175400 | 1,74,400 | 178400 | 167400 | 159465 | 151836 | 141398 | 131900 | 128400 | 128400 | 128400 | 131400 | 126900 | 132400 | 144650 | 150650 | 146650 | 148150 | 151150 | 162650
| v | Index No of Insulator |  | 116.16 | [19 empty] | 122.14 | 0 | 0 |  |  |  | 131.81 |  |  |  | 138.48 | 138.48 | 138.48 | 142.91 | 145.26 |  | 145.26 |  |  |  | 173.25 |  |  | 181.11 | 181.11 |  |  |  | 136.69 | 136.24 | 134.1 | 133.93 | 134.42 | 137.6 | 138.99 | 139.25 | 141.91 | 142.76 | 143.83 | 144.08 | 143.74 | 142.89 | 144.33 | 143.95 | 143.74 | 144.43 | 144.78 | 144.88 | 144.72 | 144.79 | 145.71 | 146.4 | 148.13 | 148.18 | 148.21 | 148.21 | 150.71 | 159.36 | 160.11 | 167.71 | 170.33 | 171.24 | 168.45 | 164.89 | 161.94 | 157.02 | 159.87 | 150.87 | 150.64 | 150.7 | 153.18 | 153.63 | 156.06 | 157.95 | 157.56 | 158.03 | 159.31
| vi | Transformer Oil |  | 35513 | [19 empty] | 39098 | 0 | 0 |  |  |  | 40560 |  |  |  | 43210 | 43210 | 43210 | 43435 | 44335 |  | 44335 |  |  |  | 39160 |  |  | 39923 | 39923 |  |  |  | 34017 | 34017 | 36127 | 38018 | 38018 | 40350 | 40655 | 42602 | 42241 | 43946 | 41113 | 38995 | 38779 | 38562 | 38661 | 38183 | 36487 | 35573 | 35704 | 35269 | 37131 | 49950 | 35827 | 35827 | 36319 | 38599 | 39304 | 39304 | 40182 | 45215 | 49538 | 56272 | 59080 | 56642 | 54287 | 53145 | 52986 | 49375 | 46625 | 46250 | 45500 | 44125 | 44125 | 47300 | 47250 | 50950 | 50375 | 49625 | 50625
| vii | Labour |  | 111.9552 | [19 empty] | 117.3648 | 0 | 0 |  |  |  | 118.5408 |  |  |  | 122.7744 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.008 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.19 | 150.2787 | 151.3677 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 4-B | Current Transformer (From Abroad)
| i | Alluminium | [77 empty] | US$2719 |  |  | US$2719 |  |  | 0
| ii | Electric Energy | [77 empty] | 0.0959 |  |  | 0.0959 |  |  | 0
| iii | Copper | [77 empty] | US$7669 |  |  | US$7669 |  |  | 0
| iv | Vacuum Gas Oil | [77 empty] | Euro 1009.25 |  |  | Euro 1009.25 |  |  | 0
| v | Labour | [77 empty] | 2313(Weekly) |  |  | 2313(Weekly) |  |  | 0
| 5-A | Capacitive Voltage Transformer (From India)
| i | Copper |  | 117662 | [19 empty] | 121706 | 0 | 0 |  |  |  | 161583 |  |  |  | 170202 | 170202 | 170202 | 171962 | 177245 |  | 177245 |  |  |  | 174024 |  |  | 196067 | 196067 |  |  |  | 234065 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 343064 | 310398 | 327855 | 350128 | 340897 | 291788 | 271169 | 298979 | 384365 | 356028 | 374688 | 378574 | 3,78,065 | 379097 | 342410 | 3,49,353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258090 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| ii | Electrical Steel sheet -CRGO |  | 125048 | [19 empty] | 82245 | 0 | 0 |  |  |  | 84522 |  |  |  | 82864 | 82864 | 82864 | 84681 | 86634 |  | 86634 |  |  |  | 161048 |  |  | 188786 | 188786 |  |  |  | 200074 | 195894 | 194855 | 221331 | 204827 | 203822 | 212009 | 210100 | 209593 | 200334 | 203675 | 198712 | 200218 | 195011 | 196183 | 191168 | 182565 | 185109 | 219073 | 198404 | 209701 | 215120 | 192092 | 195575 | 188296 | 194326 | 231172 | 195118 | 203869 | 21968 | 2,15,227 | 225373 | 2,29,721 | 2,43,082 | 238764 | 230946 | 250205 | 228507 | 237253 | 222515 | 219799 | 186754 | 187491 | 182536 | 170393 | 164804 | 162203 | 157341 | 152995
| iii | Iron & Steel |  | 137.6 | [19 empty] | 166.1 | 0 | 0 |  |  |  | 198.7 |  |  |  | 242.9 | 242.9 | 242.9 | 237.2 | 237.2 |  | 237.2 |  |  |  | 258.8 |  |  | 256.3 | 256.3 |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 268.3 | 276.7 | 276.7 | 217.22 | 276.7 | 277.3 | 277.9 | 280.1 | 280.6 | 280.6 | 287 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| iv | Aluminium | [27 empty] | 109025 |  |  |  | 114325 | 114325 | 114325 | 117325 | 117325 |  | 117325 |  |  |  | 124650 |  |  | 117050 | 117050 |  |  |  | 140300 | 146300 | 147800 | 148800 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 166300 | 162900 | 162900 | 160400 | 159400 | 155900 | 152900 | 155900 | 148900 | 145900 | 147400 | 144900 | 141400 | 143400 | 141317 | 163400 | 167400 | 175400 | 1,74,400 | 178400 | 167400 | 159465 | 151836 | 141398 | 131900 | 128400 | 128400 | 128400 | 131400 | 126900 | 132400 | 144650 | 150650 | 146650 | 148150 | 151150 | 162650
| v | Index No of Insulator |  | 116.16 | [19 empty] | 122.14 | 0 | 0 |  |  |  | 131.81 |  |  |  | 138.48 | 138.48 | 138.48 | 142.91 | 145.26 |  | 145.26 |  |  |  | 173.25 |  |  | 181.11 | 181.11 |  |  |  | 136.69 | 136.24 | 134.1 | 133.93 | 134.42 | 137.6 | 138.99 | 139.25 | 141.91 | 142.76 | 143.83 | 144.08 | 143.74 | 142.89 | 144.33 | 143.95 | 143.74 | 144.43 | 144.78 | 144.88 | 144.72 | 144.79 | 145.71 | 146.4 | 148.13 | 148.18 | 148.21 | 148.21 | 150.71 | 159.36 | 160.11 | 167.71 | 170.33 | 171.24 | 168.45 | 164.89 | 161.94 | 157.02 | 159.87 | 150.87 | 150.64 | 150.7 | 153.18 | 153.63 | 156.06 | 157.95 | 157.56 | 158.03 | 159.31
| vi | Transformer Oil |  | 35513 | [19 empty] | 39098 | 0 | 0 |  |  |  | 40560 |  |  |  | 43210 | 43210 | 43210 | 43435 | 44335 |  | 44335 |  |  |  | 39160 |  |  | 39923 | 39923 |  |  |  | 34017 | 34017 | 36127 | 38018 | 38018 | 40350 | 40655 | 42602 | 42241 | 43946 | 41113 | 38995 | 38779 | 38562 | 38661 | 38183 | 36487 | 35573 | 35704 | 35269 | 37131 | 49950 | 35827 | 35827 | 36319 | 38599 | 39304 | 39304 | 40182 | 45215 | 49538 | 56272 | 59080 | 56642 | 54287 | 53145 | 52986 | 49375 | 46625 | 46250 | 45500 | 44125 | 44125 | 47300 | 47250 | 50950 | 50375 | 49625 | 50625
| vii | Labour |  | 111.9552 | [19 empty] | 117.3648 | 0 | 0 |  |  |  | 118.5408 |  |  |  | 122.7744 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.008 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.19 | 150.2787 | 151.3677 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 5-B | Capacitive Voltage Transformer (From Abroad)
| i | Alluminium | [77 empty] | US$2719 |  |  | US$2719 |  |  | 0 |  | 0
| ii | Insulator | [77 empty] | 197.1 |  |  | 197.1 |  |  | 0 |  | 0
| iii | Copper | [77 empty] | US$7669 |  |  | US$7669 |  |  | 0 |  | 0
| iv | Crude Oil | [77 empty] | US$116.64 |  |  | US$116.64 |  |  | 0 |  | 0
| v | Labour | [77 empty] | 15.94(per hour) |  |  | 15.94(per hour) |  |  | 0 |  | 0
| 6-A | Isolators (From India)
| i | Iron & Steel |  | 137.6 | [19 empty] | 166.1 | 0 | 0 |  |  |  | 198.7 |  |  |  | 242.9 | 242.9 | 237.2 | 237.2 | 237.2 |  | 237.2 |  |  |  | 258.8 |  |  | 256.3 | 256.3 |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 268.3 | 276.7 | 276.7 | 217.22 | 276.7 | 277.3 | 277.9 | 280.1 | 280.6 | 280.6 | 287 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| ii | Copper |  | 117662 | [19 empty] | 121706 | 0 | 0 |  |  |  | 180263 |  |  |  | 170202 | 170202 | 171962 | 171962 | 177245 |  | 177245 |  |  |  | 174024 |  |  | 196067 | 196067 |  |  |  | 234065 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 343064 | 310398 | 327855 | 350128 | 340897 | 291788 | 271169 | 298979 | 384365 | 356028 | 374688 | 378574 | 3,78,065 | 379097 | 342410 | 3,49,353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258090 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| iii | Alluminium |  | 104050 | [19 empty] | 107950 | 0 | 0 |  |  |  | 109025 |  |  |  | 114325 | 114325 | 117325 | 117325 | 117325 |  | 117325 |  |  |  | 124650 |  |  | 117050 | 117050 |  |  |  | 140300 | 146300 | 147800 | 148800 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 166300 | 162900 | 162900 | 160400 | 159400 | 155900 | 152900 | 155900 | 148900 | 145900 | 147400 | 144900 | 141400 | 143400 | 141317 | 163400 | 167400 | 175400 | 1,74,400 | 178400 | 167400 | 159465 | 151836 | 141398 | 131900 | 128400 | 128400 | 128400 | 131400 | 126900 | 132400 | 144650 | 150650 | 146650 | 148150 | 151150 | 162650
| iv | Index No of Insulator |  | 168 | [19 empty] | 168 | 0 | 0 |  |  |  | 131.81 |  |  |  | 138.48 | 138.48 | 138.48 | 142.91 | 145.26 |  | 145.26 |  |  |  | 173.25 |  |  | 181.11 | 168 |  |  |  | 136.69 | 136.24 | 134.1 | 133.93 | 134.42 | 137.6 | 138.99 | 139.25 | 141.91 | 142.76 | 143.83 | 144.08 | 143.74 | 142.89 | 144.33 | 143.95 | 143.74 | 144.43 | 144.78 | 144.88 | 144.72 | 144.79 | 145.71 | 146.4 | 148.13 | 148.18 | 148.21 | 148.21 | 150.71 | 159.36 | 160.11 | 167.71 | 170.33 | 171.24 | 168.45 | 164.89 | 161.94 | 157.02 | 159.87 | 150.87 | 150.64 | 150.7 | 153.18 | 153.63 | 156.06 | 157.95 | 157.56 | 158.03 | 159.31
| v | Labour |  | 111.9552 | [19 empty] | 117.3648 | 0 | 0 |  |  |  | 118.5408 |  |  |  | 122.7744 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.008 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.19 | 150.2787 | 151.3677 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 6-B | Isolators (From Abroad)
| i | Electrolytic Copper Wire / bars | [80 empty] | 0 |  |  | 0 |  | 0
| ii | Bus Bar Grade Aluminium | [80 empty] | 0 |  |  | 0 |  | 0
| iii | Structural Steel | [80 empty] | 0 |  |  | 0 |  | 0
| iv | Procelian | [80 empty] | 0 |  |  | 0 |  | 0
| v | Labour | [80 empty] | 0 |  |  | 0 |  | 0
| 7-A | Surge Arrester (FROM INDIA)
| i | Zinc |  | 52800 | [19 empty] | 55900 | 0 | 0 |  |  |  | 66000 |  |  |  | 58600 | 58600 | 57900 | 57900 | 59000 |  | 59000 |  |  |  | 69900 |  |  | 66300 | 66300 |  |  |  | 107100 | 124500 | 121500 | 140200 | 171900 | 197900 | 166200 | 175300 | 181600 | 180500 | 212300 | 228800 | 221500 | 176500 | 178000 | 160400 | 174000 | 166300 | 157800 | 163500 | 144500 | 136700 | 131100 | 111100 | 109800 | 104200 | 107300 | 107300 | 98000 | 97700 | 90300 | 88700 | 83657 | 76145 | 72134 | 68926 | 63400 | 68900 | 67900 | 80700 | 88400 | 88200 | 91000 | 98900 | 106900 | 108300 | 125900 | 123700 | 139800
| ii | Cobalt |  | 1268.82 | [19 empty] | 1425.14 | 0 | 0 |  |  |  | 3317.41 |  |  |  | 3102.75 | 3102.75 | 2993.64 | 2993.64 | 2891.41 |  | 2891.41 |  |  |  | 1938.31 |  |  | 1516.42 | 1516.42 |  |  |  | 1756.49 | 1566.66 | 1436.71 | 1545.07 | 1716.5 | 1794.76 | 1698.04 | 1655.52 | 1985.91 | 2203.03 | 1996.81 | 2024.6 | 2889.92 | 2725.73 | 2762.56 | 3064.45 | 2954.22 | 2806.47 | 2665.83 | 2550.15 | 2443.39 | 2662.27 | 2764.57 | 3038.87 | 3632.43 | 4203.7 | 4570.15 | 4784.31 | 4726.05 | 4772.21 | 4495.37 | 4035.76 | 3827.61 | 33143.28 | 2892.46 | 22637.34 | 1677.63 | 2003.71 | 1748.72 | 1602.87 | 1850.25 | 1721.26 | 1642.2 | 2023.92 | 2210.95 | 2149.1 | 1946.99 | 2336.41 | 2190.66
| iii | Alluminum |  | 104050 | [19 empty] | 107950 | 0 | 0 |  |  |  | 109025 |  |  |  | 114325 | 114325 | 93967 | 117325 | 117325 |  | 117325 |  |  |  | 124650 |  |  | 117050 | 117050 |  |  |  | 140300 | 146300 | 147800 | 148800 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 166300 | 162900 | 162900 | 160400 | 159400 | 155900 | 152900 | 155900 | 148900 | 145900 | 147400 | 144900 | 141400 | 143400 | 141317 | 1,63,400 | 1,67,400 | 1,75,400 | 1,74,400 | 178400 | 1,67,400 | 159465 | 151836 | 141398 | 131900 | 128400 | 128400 | 128400 | 131400 | 126900 | 132400 | 144650 | 150650 | 146650 | 148150 | 151150 | 162650
| iv | Ball clay |  | 957.5 | [19 empty] | 942.5 | 0 | 0 |  |  |  | 942.5 |  |  |  | 1217.5 | 1217.5 | 1217.5 | 461.45 | 1217.5 |  | 1217.5 |  |  |  | 1575 |  |  | 1575 | 1575 |  |  |  | 1575 | 1575 | 1575 | 1575 | 1575 | 1675 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1846 | 1893 | 1975 | 1975 | 1975 | 2025 | 2025 | 2025 | 2275 | 2275 | 2275 | 2275 | 2275 | 2275 | 2409
| v | Bismath |  | 450.12 | [19 empty] | 499 | 0 | 0 |  |  |  | 366.67 |  |  |  | 462.51 | 462.51 | 461.51 | 461.45 | 526 |  | 526 |  |  |  | 393.87 |  |  | 457.1 | 457.1 |  |  |  | 550.99 | 538.49 | 535.53 | 465.31 | 516.54 | 517.64 | 505.75 | 511.61 | 526.8 | 555.84 | 649.34 | 690.01 | 792.79 | 916.72 | 978.7 | 1108.54 | 1402.73 | 1671.45 | 1723.64 | 1658.22 | 1664.86 | 1469.7 | 1315.72 | 1272.41 | 1236.55 | 1103.05 | 1158.03 | 1416.12 | 1525.07 | 1433.9 | 1287.77 | 1158 | 1148.83 | 1182.67 | 1136.94 | 1185.26 | 1066.29 | 1073.42 | 1114.5 | 1086.91 | 972.94 | 873.21 | 798.12 | 763.51 | 780.47 | 982.04 | 992.73 | 951.89 | 865.03
| vi | Fuel |  | 253.2 | [19 empty] | 253.2 | 0 | 0 |  |  |  | 253.2 |  |  |  | 253.2 | 253.2 | 282 | 253.2 | 253.2 |  | 253.2 |  |  |  | 293.2 |  |  | 304 | 304 |  |  |  | 312.4 | 310.7 | 311 | 313.5 | 314.7 | 316.8 | 319.7 | 320.1 | 326.5 | 328.9 | 331.4 | 329.6 | 326.7 | 322.4 | 322.3 | 320.7 | 319.6 | 320.3 | 322 | 321.9 | 321.8 | 322.4 | 321.7 | 323.7 | 326.5 | 334.4 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 350.2 | 331.8 | 329.5 | 323.5 | 321 | 322.6 | 325.2 | 327.1 | 338.4 | 342.8 | 343.6 | 344.6 | 345.4
| vii | Labour |  | 111.9552 | [19 empty] | 117.3648 | 0 | 0 |  |  |  | 118.5408 |  |  |  | 122.7744 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.008 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.1897 | 150.2787 | 151.3677 | 152.46 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 7-B | Surge Arrester (FROM ABROAD)
| i | Zinc | [77 empty] | 0 |  |  | 0 |  |  | 0 |  | 0
| ii | Cobalt | [77 empty] | 0 |  |  | 0 |  |  | 0 |  | 0
| iii | Bismuth | [77 empty] | 0 |  |  | 0 |  |  | 0 |  | 0
| iv | Ball Clay | [77 empty] | 0 |  |  | 0 |  |  | 0 |  | 0
| v | Labour | [77 empty] | 0 |  |  | 0 |  |  | 0 |  | 0
| 8 | 1.1 kV PVC/XLPE Insulated power and control cables
| i | PVC Compound |  | 53200 | [19 empty] | 58200 | 0 | 0 |  |  |  | 63200 |  |  |  | 68000 | 68000 | 68000 | 76000 | 76000 |  | 76000 |  |  |  | 73250 |  |  | 71250 | 71250 |  |  |  | 77250 | 77250 | 77250 | 77250 | 73500 | 73500 | 74750 | 80750 | 84000 | 84000 | 82000 | 82750 | 83750 | 84000 | 84000 | 82650 | 83650 | 83650 | 83650 | 86000 | 89000 | 87000 | 87000 | 87500 | 87500 | 88000 | 89000 | 89000 | 91000 | 92000 | 97000 | 97000 | 97000 | 95000 | 92650 | 85280 | 80250 | 83000 | 84000 | 84500 | 84500 | 84500 | 87000 | 88000 | 91500 | 89000 | 89000 | 90500
| ii | Metal |  | 0 | [19 empty] | 0 | 0 | 0 |  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58000 | 70200 | 63900 | 78600 | 89100 | 86100 | 96200 | 102100 | 114800 | 121700 | 125400 | 127200
| iii | Aluminium |  | 68450 | [19 empty] | 89617 | 0 | 0 |  |  |  | 109025 |  |  |  | 114325 | 114325 | 117325 | 117325 | 117325 |  | 117325 |  |  |  | 124650 |  |  | 117050 | 117050 |  |  |  | 234065 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 343064 | 310398 | 327855 | 350128 | 340897 | 291788 | 271169 | 298979 | 384365 | 356028 | 374688 | 378574 | 3,78,065 | 379097 | 342410 | 3,49,353 | 254789 | 201489 | 131900 | 128400 | 128400 | 128400 | 131400 | 126900 | 132400 | 144650 | 150650 | 146650 | 148150 | 151150 | 162650
| iv | Copper |  | 120215 | [19 empty] | 120620 | 0 | 0 |  |  |  | 180263 |  |  |  | 170202 | 170202 | 171962 | 171962 | 177245 |  | 177245 |  |  |  | 174024 |  |  | 196067 | 196067 |  |  |  | 140300 | 146300 | 147800 | 148800 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 166300 | 162900 | 162900 | 160400 | 159400 | 155900 | 152900 | 155900 | 148900 | 145900 | 147400 | 144900 | 141400 | 143400 | 141317 | 1,63,400 | 1,67,400 | 1,75,400 | 1,74,400 | 178400 | 1,67,400 | 159465 | 151836 | 141398 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258090 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| v | weight in MT of metal KM |  | 0 | [19 empty] | 0 | 0 | 0 |  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0 |  |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | Sub-Station Structures [Lattice Steel Structures & Pipe Structures(including bolts & nuts, Washers & foundation bolts)]
| i | Published Price Index of Structurel Steel |  | 15509 | [19 empty] | 19650 | 0 | 0 |  |  |  | 26510 |  |  |  | 27772 | 27772 | 31234 | 26510 | 25824 |  | 25824 |  |  |  | 24946 |  |  | 30019 | 30019 |  |  |  | 30161 | 30161 | 30180 | 30113 | 32444 | 32255 | 32444 | 32160 | 32538 | 32633 | 32538 | 32538 | 33153 | 38889 | 33209 | 33587 | 33681 | 33587 | 33681 | 33153 | 33775 | 35286 | 35900 | 36245 | 37567 | 38889 | 41323 | 46434 | 46675 | 48117 | 49269 | 49632 | 50305 | 50498 | 50594 | 50794 | 50867 | 49471 | 49894 | 49766 | 49806 | 46805 | 47030 | 47030 | 47360 | 47335 | 47437 | 48047 | 49031
| ii | Published Price Index of Electrolytic Zinc |  | 52800 | [19 empty] | 55900 | 0 | 0 |  |  |  | 66000 |  |  |  | 58600 | 58600 | 57900 | 57900 | 59000 |  | 59000 |  |  |  | 69900 |  |  | 66300 | 66300 |  |  |  | 107100 | 124500 | 121500 | 140200 | 171900 | 197900 | 166200 | 175300 | 181600 | 180500 | 212300 | 228800 | 221500 | 176500 | 178000 | 160400 | 174000 | 166300 | 157800 | 163500 | 144500 | 136700 | 131100 | 111100 | 109800 | 104200 | 107300 | 107300 | 98000 | 97700 | 90300 | 88700 | 83657 | 76145 | 72134 | 68926 | 63400 | 68900 | 67900 | 80700 | 88400 | 88200 | 91000 | 98900 | 106900 | 108300 | 125900 | 123700 | 139800
| iii | Labour |  | 111.9552 | [19 empty] | 117.3648 | 0 | 0 |  |  |  | 118.5408 |  |  |  | 122.7744 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.008 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.1897 | 150.2787 | 151.3677 | 152.46 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 10 | ERECTION PRICE COMPONENT (INCLUDING CIVIL WORKS BUT EXCLUDING 'SUPPLY & PLACEMENT OF REINFORCEMENT STEEL' AND 'CONCRETING'
| i | Labour |  | 111.9552 | [19 empty] | 117.3648 | 0 | 0 |  |  |  | 118.5408 |  |  |  | 122.7744 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.008 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.1897 | 150.2787 | 151.3677 | 152.46 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| ii | Ex-works field Labour | [77 empty] | 0 |  |  | Not applicable |  |  | 0 |  | 0
| 11 | SUPPLY & PLACEMENT OF REINFORCEMENT STEEL
| i | Diesel Oil |  | 372 | [19 empty] | 395 | 0 | 0 |  |  |  | 372 |  |  |  | 446.5 | 446.5 | 446.5 | 400 | 400 |  | 400 |  |  |  | 410 |  |  | 400 | 400 |  |  |  | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 451.5 | 451.5 | 451.5 | 465.8 | 465.8 | 465.8 | 465.8 | 465.8 | 478.9 | 478.9 | 478.9 | 478.9 | 478.9 | 482.3 | 451.1 | 452.2 | 452.2 | 452.2 | 452.2 | 481.4 | 481.4 | 481.4 | 481.4 | 481.4 | 481.4
| ii | Labour |  | 111.9552 | [19 empty] | 117.3648 | 0 | 0 |  |  |  | 118.5408 |  |  |  | 122.7744 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.008 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.1897 | 150.2787 | 151.3677 | 152.46 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| iii | Iron & Steel |  | 258.3 | [19 empty] | 258.3 | 0 | 0 |  |  |  | 258.3 |  |  |  | 258.3 | 258.3 | 258.3 | 258.3 | 258.3 |  | 258.3 |  |  |  | 258.8 |  |  | 186.9 | 186.9 |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 268.3 | 276.7 | 276.7 | 217.22 | 276.7 | 277.3 | 277.9 | 280.1 | 280.6 | 280.6 | 287 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 0 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| 12 | FOR CONCRETING
| i | Diesel Oil |  | 372 | [19 empty] | 395 | 0 | 0 |  |  |  | 372 |  |  |  | 446.5 | 446.5 | 446.5 | 400 | 400 |  | 400 |  |  |  | 410 |  |  | 400 | 400 |  |  |  | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 451.5 | 451.5 | 451.5 | 465.8 | 465.8 | 465.8 | 465.8 | 465.8 | 478.9 | 478.9 | 478.9 | 478.9 | 478.9 | 482.3 | 451.1 | 452.2 | 452.2 | 452.2 | 452.2 | 481.4 | 481.4 | 481.4 | 481.4 | 481.4 | 481.4
| ii | Labour |  | 111.9552 | [19 empty] | 117.3648 | 0 | 0 |  |  |  | 118.5408 |  |  |  | 122.7744 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.008 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147.0118 | 149.1897 | 150.2787 | 151.3677 | 152.46 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| iii | Index No.of whole sell price in india for non metalic mineral products(Structural Clay Product) as published by RBI. |  | 191 | [19 empty] | 191 | 0 | 0 |  |  |  | 191 |  |  |  | 191 | 191 | 191 | 191 | 191 |  | 191 |  |  |  | 191.1 |  |  | 190.4 | 190.4 |  |  |  | 186.2 |  |  | 191.2 | [7 empty] | 191.2 | [6 empty] | 211.7 | 211.7 | 211.7 | 211.7 | 211.7 | 211.7 |  |  |  |  | 219.4 | 219.4 | 219.4 | 219.4 |  |  | 219.4 |  | 223.1 | 224 | 224 | 224 | 227.2 | 227.2 | 227.2 | 227.2 | 227.2 | 227.2 | 227.2 | 227.2
| iv | Cement |  | 163.8 | [19 empty] | 163.8 | 0 | 0 |  |  |  | 163.8 |  |  |  | 213 | 213 | 213 | 163.8 | 163.8 |  | 163.8 |  |  |  | 163.8 |  |  | 162.2 | 162.2 |  |  |  | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.3 | 220.5 | 220.6 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 221.4 | 221.4 | 222.7 | 224.5 | 227.7 | 228.1 | 228.6 | 230.9 | 230.5 | 228.1 | 227.2 | 225.8 | 213.1
| 13 | For Erection Price & Civil Works Component
| i | Indian field Labour (F) Expatriate Field labour (EF) b+c*=0.75 *- In case of Indian Bidder,'c' shall be equal to zero) | [77 empty] | 0 |  |  | 0 |  |  | 0 |  | 0
Note : The exchange correction factor for material and labour (i.e., F) for all the equipments shall be equal to 1
Month and Year of Escalation
| Month and Year of Escalation |  | 2009-12-01
| S.No. | Particulars | Units
| 1 | LT Transformer
| ii | Copper | 326293
| iii | Electrical Steel sheet -CRGO | 157341
| iv | Iron & Steel | 291.4
| v | Insulating Materials | 403.35
| vi | Transformer Oil | 49625
| vii | Labour | 168
| 2 | Power Transformers
| i | Copper | 326293
| ii | Electrical Steel sheet -CRGO | 157341
| iii | Iron & Steel | 291.4
| iv | Insulating Material | 403.35
| v | Oil | 49625
| vi | Labour | 168
| 3-A | Circuit Breaker(From INDIA)
| ii | Iron & Steel | 291.4
| iii | Copper | 326293
| iv | Alluminium | 151150
| v | Epoxy Resin | 188
| vi | Labour | 168
| 3-B | Circuit Breaker(From ABROAD)
| i | Steel
| ii | Copper
| iii | Alluminium
| iv | Labour
| 4-A | Current Transformer (FROM INDIA)
| i | Copper | 326293
| ii | Electrical Steel sheet -CRGO | 157341
| iii | Iron & Steel | 291.4
| iv | Alluminum | 151150
| v | Index no of nsulator | 158.03
| vi | Transformer Oil | 49625
| vii | Labour | 168
0
| 4-B | Current Transformer (FROM ABROAD) | 0
| i | Alluminium | 0
| ii | Electric Energy | 0
| iii | Copper | 0
| iv | Vacuum Gas Oil | 0
| v | Labour | 0
0
| 5-A | Capacitive Voltage Transformer (From INDIA) | 0
| i | Copper | 326293
| ii | Electrical Steel sheet -CRGO | 157341
| iii | Iron & Steel | 291.4
| iv | Index no of nsulator | 158.03
| v | Transformer Oil | 49625
| vi | Labour | 168
0
| 5-B | Capacitive Voltage Transformer (From ABROAD) | 0
| i | Alluminium | 0
| ii | Insulator | 0
| iii | Copper | 0
| iv | Crude Oil | 0
| v | Labour | 0
0
| 6-A | ISOLATORS (FROM INDIA) | 0
| i | Iron & Steel | 291.4
| ii | Copper | 326293
| iii | Alluminium | 151150
| iv | Index no of nsulator | 158.03
| v | Labour | 168
0
| 6-B | ISOLATORS (FROM ABROAD) | 0
| i | Electrolytic Copper Wire / bars | 0
| ii | Bus Bar Grade Aluminium | 0
| iii | Structural Steel | 0
| iv | Procelian | 0
| v | Labour | 0
0
| 7-A | Surge Arrester (FROM INDIA) | 0
| i | Zinc | 123700
| ii | Cobalt | 2336.41
| iii | Alluminum | 151150
| iv | Bismuth | 2275
| v | Ball Clay | 951.89
| vi | Fuel | 344.6
| vii | Labour | 168
0
| 7-B | Surge Arrester (FROM ABROAD) | 0
| i | Zinc | 0
| ii | Cobalt | 0
| iii | Bismuth | 0
| iv | Ball Clay | 0
| v | Labour | 0
0
| 8 | 1.1 kV PVC/XLPE Insulated power and control cables | 0
| i | PVC Compound | 90500
| ii | Metal | 127200
| iii | Alliminium | 151150
| iv | Copper | 326293
| v | weight in MT of metal KM | 0
0
| 9 | Sub-Station Structures [Lattice Steel Structures & Pipe Structures(including bolts & nuts, Washers & foundation bolts)] | 0
| i | Steel Angle | 48047
| ii | Zinc | 123700
| iii | Labour | 168
| 10 | ERECTION PRICE COMPONENT (INCLUDING CIVIL WORKS BUT EXCLUDING 'SUPPLY & PLACEMENT OF REINFORCEMENT STEEL' AND 'CONCRETING' | 0
| i | Labour | 168
| ii | Ex-works field Labour | 0
0
| 11 | SUPPLY & PLACEMENT OF REINFORCEMENT STEEL | 0
| i | Diesel Oil | 481.4
| ii | Labour | 168
| iii | Iron & Steel | 291.4
0
| 12 | FOR CONCRETING | 0
| i | Diesel Oil | 481.4
| ii | Labour | 168
| iii | Non-metallic Mineral products | 227.2
| iv | Cement | 213.1
| 13 | For Erection Price & Civil Works Component | 0
| i | Indian field Labour (F) Expatriate Field labour (EF) b+c*=0.75 *- In case of Indian Bidder,'c' shall be equal to zero) | 0
0
|  | Note : The exchange correction factor for material and labour (i.e., F) for all the equipments shall be equal to 1 | 0

## Escalated Cost
CERC
Capital Cost Benchmarking
Transmission Substations
| Name of sub-station |  | 0 | Auto Transformer Package T4 for Fatehpur and Agra Sub-Station | 765 KV Auto Transformer Package T3 for Balia Sub-Station | 765 KV Auto Transformer T3 for Lucknow Sub-Station | 765/400/220KV S/S, Seoni | 765KV/400KV Lucknow (New) Sub-Station and Extension of 400 kV Lucknow Sub- Station | Upgradation of 400KV Balia Sub-Station to 765 kV Sub-Station | 765/400 KV S/S-Fatehpur | 765/400 KV S/S-Agra | 765KV Seoni Sub-Station & 765 kV Sipat Transmission System | Up Gradation of 400/220KV Wardha Sub-Station to 765/400/220 kV Voltage Level
| Reference Numbers |  | 0 | LOA NO.:C-14807-S016-3/LOA-I/2790 DT:29-12-08 | LOA NO.:C-14803-S016-3/LOA-I/2787 DT: 29-12-2008 | LOA NO.:C-14803-S016-3/LOA-I/2787 DT: 29-12-2008 | Ref : C-32209-S016-7/LOA -1/ 1636 Dated 31-03-2005, | REF.:C-14804-S019A-3/LOA-I 2981 Dated 06/03/2009 | REF.:C-14803-S019 A-3/LOA-I/2963 Dated 05/03/09 | Ref No.C-14807-S019A-3/LOA-I/3020 DATED 26/03/2009 | Ref No.C-14808-S019A-3/LOA-I/3022 DATED 26/03/2009 | Ref. : C-32209-S019A-7/LOA-III/1653 Dated 04/04/2005 | Ref.: RN/JKN/3006-07
| Base Date of Indices |  | 0 | 2008-05-01 | 2008-05-01 | 2008-05-01 | 2004-09-01 | 2008-08-01 | 2008-08-01 | 2008-11-01 | 2008-11-01 | 2004-09-01 | 2008-11-01 | 2009-01-01
| SUPPLY | Unit
1 | POWER TRANSFORMER (Single Phase Units)
i | I.C.T 500 MVA, Single Phase, 765/Root3 / 400/Root3 / 33 KV class including insulating Oil | No |  | 1934.4506 | 2084.1634 | 2046.5002 | 2003.6822
ii | I.C.T 167 MVA, Single Phase, 400/Root3 / 220/Root3 / 33 KV class including insulating Oil | No |  | 488.9265
iii | I.C.T 315 MVA, 3 Phase, 400/220/33 KV including i Insulating Oil | No |  | 951.5373
2 | REACTOR & NGR
i | 110 MVAR, 765/Root3KV, Single Phase with oil | No
ii | 80 MVAR, 765/Root3KV, Single Phase with oil | No |  |  |  |  | 472.8656
iii | 50 MVAR, 765/Root3KV, Single Phase with oil | No |  | 377.4858
iv | NGR (Dry Core Type) for 765KV Reactor | No |  | 0 |  |  | 82.0278
v | Surge Arrestor for NGR - 765KV System | No |  | 0 |  |  | 1.19
vi | 125MVAR, 400KV, 3Ph. Reactor with insulating Oil | No |  | 432.4987
vii | 80MVAR, 400KV, 3Ph. Reactor with insulating Oil | No |  | 424.9059
ix | 63MVAR, 400KV, 3Ph. Reactor with insulating Oil | No |  | 377.4858
x | 50MVAR, 400KV, 3Ph. Reactor with insulating Oil | No |  | 377.4858
xi | NGR for 400KV Reactor with insulating oil | No |  | 22.8965
xii | Surge Arrestor for NGR - 400KV System | No |  | 1.5091
3 | 765 KV EQUIPMENTS
i | 765 kV,3150KA,40KA Circuit Breaker with CR | No | [5 empty] | 195.6356 | 194.6277 | 200.7965 | 184.9869 | 342.6534 | 188.291
ii | 765 kV,3150 KA,40 KA Circuit Breaker without CR | No | [5 empty] | 158.8753 | 155.9158 | 150.8051 | 150.3385 | 254.2099 | 156.7084
iii | 765 kV CTs 3000A, 40KA, 5-Core, | No | [5 empty] | 29.7041 | 29.6848 | 49.8253 | 29.0221 | 34.7049 | 28.7098
iv | 765 kVCVT 8800 PF | No | [5 empty] | 20.6239 | 20.6102 | 21.1907 | 15.3319 | 16.0843 | 15.9728
v | 765 kV,3150 A,40 kA Isolator 3-Phase with 1 E/S | No | [5 empty] | 31.5877 | 30.9133 | 37.6544 | 34.7786 | 27.6445 | 35.1847
vi | 765 kV,3150 A,40 kA Isolator 3-Phase with 2 E/S | No | [5 empty] | 38.3767 | 37.6198 | 43.1687 | 40.2369 | 0 | 0
vii | 765 kV, 2000A, 40KA, S-Phase Isolator with 1 E/S | No | [9 empty] | 9.6115 | 12.1647
viii | 765 kV 3 Phase E/S | No
ix | 624 kV Surge Arrestor | No | [5 empty] | 10.9015 | 10.884 | 11.8546 | 11.7829 | 9.397 | 10.9225
4 | 765KV C & R Panels
| Circuit Breaker panel with Auto Reclose | [6 empty] | 4.7903 | 4.8042 | 6.7193 | 5.6273 | 0 | 5.9496
| Circuit Breaker panel without Auto Reclose | [6 empty] | 0 | 0 | 5.4805 | 5.2473 | 0 | 5.6821
| Line protection panel | [6 empty] | 28.1958 | 28.2777 | 16.6593 | 23.5314 | 34.5112 | 26.7778
| 765/400KV Transf. Protn. Panel(both HV and MV) | [6 empty] | 14.041 | 14.0818 | 11.3918 | 16.3416 | 22.9377 | 12.9202
| Reactor Protection Panel | [6 empty] | 11.8563 | 11.8908 | 7.6727 | 10.8057 | 18.7636 | 11.9914
| Bus Bar Protection Panel | [6 empty] | 39.8245 | 44.2082 | 65.1235 | 0 | 176.6737 | 0
5 | 420KV EQUIPMENTS
| 420 kV, 3150A, 40KA Breaker with CR | [6 empty] | 40.3234 | 36.0968 | 33.3525 | 42.8582 | 46.7932 | 0
| 420 kV, 3150A, 40KA Breaker without CR | [6 empty] | 30.1776 | 27.036 | 29.3955 | 28.0263 | 43.798 | 28.931
| 420 kV, 3000A, 40KA CT, 5 Core Current Transformer with 120% current rating, | [6 empty] | 7.2773 | 6.8483 | 29.3963 | 11.4965 | 8.3838 | 7.1905
| 420 kV CVT 4400 PF | [6 empty] | 0 | 0 | 4.0701 | 3.6039 | 7.4104 | 0
| 420 kV CVT 8800 PF | [6 empty] | 5.3526 | 5.2861 | 0 | 0 | 6.5867 | 0
| 420 kV,3150 A,40 kA DB Isolator 3 Ph. with 1 E/S | [6 empty] | 0 | 0 | 4.6049 | 10.16 | 11.0564 | 10.6616
| 420 kV,2000 A,40 kA Isolator 3 Ph. with 1 E/S | [6 empty] | 6.5719 | 5.9941 | 3.7646 | 8.7162 | 8.9437 | 0
| 420 kV,2000A,40 kA Isolator 3 Ph. with 2 E/S | [6 empty] | 7.5357 | 6.3817 | 5.1125 | 10.1192 | 11.4484 | 5.6238
| 420 kV,2000 A,40 kA DB Isolator S Ph. with 1 E/S | [6 empty] | 0 | 0 | 0 | 0 | 3.632 | 0
| 390 kV Surge Arrestor | [6 empty] | 1.2249 | 1.6108 | 1.2187 | 2.0714 | 2.322 | 1.5958
6 | 400KV C & P Panels
| Circuit Breaker panel with Auto Reclose | [6 empty] | 4.7903 | 4.8042 | 6.7193 | 5.8823 | 0 | 5.6821
| Circuit Breaker panel without Auto Reclose | [6 empty] | 4.7346 | 4.8042 | 5.4619 | 0 | 0 | 4.3708
| Line protection panel | [6 empty] | 15.8957 | 0 | 13.4451 | 0 | 34.5112 | 0
| Transf. protn. Panel | [6 empty] | 0 | 0 | 11.3918 | 0 | 32.1708 | 12.9202
| Reactor protection panel | [6 empty] | 0 | 12.3929 | 7.6727 | 10.8049 | 0 | 11.9914
| Bus Bar Protection Panel | [6 empty] | 43.5566 | 0 | 90.4924 | 77.8815 | 164.8596 | 37.5967
7 | 245KV EQUIPMENTS
i | 245 KV, 1600A, 40KA Class Circuit Breaker | [6 empty] | 0 | 0 | 13.5671 | 0 | 20.8363 | 0
ii | 245 KV, 2500A 40KA Class Circuit Breaker | [6 empty] | 0 | 0 | 13.5671 | 0 | 20.8363 | 0
iii | 245KV,1600 A,40 kA ,5 core, CT with 120% extended current | [6 empty] | 0 | 0 | 3.9571 | 0 | 3.8356 | 0
iv | 245KV,1600 A,40 kA ,5 core, CT with 150% extended current | [6 empty] | 0 | 0 | 3.9571 | 0 | 4.4453 | 0
v | 245KV, CVT 4400 pf with 3 secondaries | [6 empty] | 0 | 0 | 3.1657 | 0 | 3.9819 | 0
vi | 245KV,1600A, 40 kA, 3Ph.Isolator DB Type - 1 E/S | [6 empty] | 0 | 0 | 1.8171 | 0 | 4.8636 | 0
vii | 245KV,1600A, 40 kA, 3-Ph.Isolator DB Type - 2 E/S | [6 empty] | 0 | 0 | 2.4153 | 0 | 5.7555 | 0
viii | 245KV,2500A, 40 kA, 3-Ph. Isolator DB Type 2 E/S | [6 empty] | 0 | 0 | 2.7991 | 0 | 6.2096 | 0
ix | 245KV, 1600A, 40 KA, 3 Ph.DB Tandem Type without E/S | [6 empty] | 0 | 0 | 1.219 | 0 | 4.4186 | 0
xii | 216 kV Surge Arrestors | [6 empty] | 0 | 0 | 0.39215 | 0 | 0 | 0
8 | 220KV C & P Panels
i | Circuit Breaker panel with Auto Reclose |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii | Circuit Breaker panel without Auto Reclose |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii | Line protection panel |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5112 | 0
iv | Bus Bar Protection panel |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.3948 | 0
9 | COMMON EQUIPMENTS
i | C & P Panel.
a | Time Synchronisation Equipment
b | Special Relay Test Kit
c | Video Projection System(VPS) 67" size
d | Complete Substation automation system for 765/400/230kV S/S including hardware and software for remote control station alongthwith associated equipments and Kiosks for the following bays ( bays as defined in the teechnical specification, Sec-Substaion Aut | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
ii | LT Switchgear
a | 415V Main Switch Board | [6 empty] | 15.2745 | 15.0164 | 13.0413 | 12.817 | 21.8044 | 0
b | 415V ACDB | [6 empty] | 16.1029 | 15.2753 | 11.6811 | 13.2157 | 20.707 | 0
c | 415V MLDB | [6 empty] | 14.2544 | 14.1273 | 10.3624 | 9.7271 | 7.4028 | 0
d | 415V Emergency LDB | [6 empty] | 7.0073 | 5.9946 | 4.7243 | 4.4337 | 1.3977 | 0
e | 220V DCDB | [6 empty] | 3.8638 | 3.7102 | 3.359 | 2.4977 | 5.2109 | 0
f | 50V DCDB | [6 empty] | 2.5152 | 2.3738 | 2.3206 | 2.2841 | 4.1135 | 0
iii | Battery & Battery Charger
a | 220V Battery | [6 empty] | 14.0338 | 8.3448 | 8.04 | 18.5796 | 10.6972 | 8.7852
b | 50V Battery | [6 empty] | 3.7708 | 1.435 | 1.931 | 1.9969 | 3.428 | 1.1267
c | Battery Charger for 220V Battery | [6 empty] | 6.233 | 4.5679 | 3.3533 | 4.1996 | 2.2486 | 0
d | Battery Charger for 50V Battery | [6 empty] | 3.3431 | 2.4511 | 1.5379 | 3.3597 | 1.6998 | 0
iv | DG Set-250KVA with control panel | [6 empty] | 28.5018 | 29.8178 | 44.1668 | 52.0472 | 17.692 | 0
v | High Wall Type Split AC unit of 2TR Capacity | [6 empty] | 0.37775 | 0.37138 | 0.33037 | 0.48527 | 0.82125 | 0
vi | Illumination | [6 empty] | 76.9518 | 0 | 116.3 | 0 | 0 | 0
vii | 72.5KV & 36 KV Equipments
a | 800KVA 33/.440 KV Distribution Transformer
72.5KV circuit breakers(3ph.)
b | 72.5KV Isolator without Earthswitch
c | 72.5KV Horn gap Fuse
d | 630KVA, 33/.440 KV Distribution Transformer
e | 33KV Horn gap Fuse
f | 33KV Isolator without ES
g | 33KV Surge Arrestor.
viii | PLCC Equipments | [6 empty] | 142.6298 | 65.4887 | 107.23 | 54.1046 | 239.7407 | 0
3150A, 40KA,Line Trap(For 765KV)
3150A, 40KA, 1 mH Line Trap(for 400KV)
2000A, 40KA, 1 mH Line Trap(for 400KV)
1600, 40KA, 0.5 mH Line Trap(for 220KV)
Coupling device for 765KV
Coupling device for 400KV
Carr Eqpt (for speech+protection and speech+Data)-765KV
Carr Eqpt (for speech+protection and speech+Data)-400KV
Protection coupler-765KV
Protection coupler-400KV
HF Cable
EPAX(24/8) with 24 Telephones,Cables etc.,
Testing and Mainetance equipment
10 | Mandatory Spares | [6 empty] | 369.0534 | 405.0926 | 486.522 | 241.8542 | 222.8598 | 0
11 | ERECTION HARDWARE
i | 765 KV
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary | [6 empty] | 0 | 584.1422 | 727.7895 | 0 | 0 | 0
765KV I Type Layout
a | Line bay
b | Transformer bay
c | Bus Reactor bay
d | Line Reactors
e | Bus(for one diameter)
ii | 400 KV
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary | [6 empty] | 276.3166 | 231.8865 | 530.5056 | 407.2393 | 0 | 0
400 KV I Type Layout
a | Line bay
b | Transformer bay
c | Re-oriented Line bay
d | Spare bay of half dia
e | Line Reactor
f | Bus for two diameters
iii | 220 KV
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary | [8 empty] | 136.2572 | 0 | 123.9772
220 KV DMT Type Layout
a | Line bay
b | Transformer bay
c | Main & Transfer Bus
d | Transfer bus coupler bay
e | Bus coupler bay
12 | Visual Monitoring system for watch & ward
13 | Fire Protection System | [6 empty] | 0 | 0 | 303.05 | 458.9451 | 0 | 0
i | Pumping arrangement forHVW system and Hydrant System, complete with all piping, valves, fittings etc., inside pump House (Set)
ii | Hydrant system, complete U/G and O/G piping and accessories etc., outside the the pump House for(Set)
iii | HVW Sprray system complete with U/G and O/G pipeing and accessories etc out side the pump house along with one hydrant point for each of the following
765KV S-Phase Transformer
400KV 3-Phase Transformer
765KV S-Phase Shunt Reactor
765KV S-Phase Bus Reactor
400KV 3-Phase Shunt Reactor
400KV 3-Phase Bus Reactor
iv | Portable extinguishers (Set)
v | Smoke detection system(Set)
14 | Illumination -- Indoor + Outdoor |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 143.9835 | 0 | 0
i | Switchyard Lighting | [10 empty] | 24.4326
ii | Street Lighting | [9 empty] | 28.713 | 60.3799
15 | Power & Control Cables : Per Km Rate | Lump-Sum
i | Power Cable | [12 empty] | 1.4982
ii | Control Cable | [12 empty] | 1.1211
Cables with associated accessories likeclamps, glands, lugs and straight joints etc.,(LS)
i | 1.1KV Power Cables
a | 1C 630Sq.mm(XLPE)
b | 1C 300Sq.mm(XLPE)
c | 3.5C 300Sq.mm(XLPE)
d | 1C 150Sq. Mm(PVC)
e | 3.5C 70 Sq.mm(PVC)
ii | 1.1KV Power Cables(PVC) for 765KV S/S
a | 3.5C 35Sq.mm
b | 4C 16Sq.mm
c | 4C 6Sq.mm
d | 2C 6Sq.mm
iii | 1.1KV grade control cables(PVC) 765KV S/S
a | 5C 2.5Sq.mm
b | 7C 2.5Sq.mm
c | 10C 2.5Sq.mm
d | 14C 2.5Sq.mm
e | 19C 2.5Sq.mm
f | 27C 2.5Sq.mm
iv | 1.1KV Power Cables(PVC) for 400KV S/S
a | 3.5C 35Sq.mm
b | 4C 16Sq.mm
c | 4C 6Sq.mm
d | 2C 6Sq.mm
v | 1.1KV grade control cables(PVC) 400KV S/S
a | 5C 2.5Sq.mm
b | 7C 2.5Sq.mm
c | 10C 2.5Sq.mm
d | 14C 2.5Sq.mm
e | 19C 2.5Sq.mm
f | 27C 2.5Sq.mm
vi | 1.1KV Power Cables(PVC) for 220KV S/S
a | 3.5C 35Sq.mm
b | 4C 16Sq.mm
c | 4C 6Sq.mm
vii | 1.1KV grade control cables(PVC) 220KV S/S
a | 5C 2.5Sq.mm
b | 7C 2.5Sq.mm
c | 10C 2.5Sq.mm
d | 14C 2.5Sq.mm
e | 19C 2.5Sq.mm
f | 27C 2.5Sq.mm
Power & Control Cables : Total Price
Power Cable -
viii | Control Cable
Control Cable
16 | Main Earthmat - 40 mm MS Rod Rate Per Km | [6 empty] | 5.2342 | 5.1434 | 4.1956 | 5.5025 | 4.7599 | 0
40mm MS Rods - 46Km
Main Earthmat - 40 mm MS Rod : Total Price
17 | Steel Structures (Rate Per MT)
i | MS | [12 empty] | 0.68144
ii | HT | [12 empty] | 0.90858
Steel Structures Total price
Lattice Type - : Total Price
H.T steel - Total Price
ERECTION
1 | POWER TRANSFORMER (Single Phase Units)
i | I.C.T 500 MVA, Single Phase, 765/Root3 / 400/Root3 / 33 KV class including insulating Oil | No
ii | I.C.T 167 MVA, Single Phase, 400/Root3 / 220/Root3 / 33 KV class including insulating Oil | No
iii | I.C.T 315 MVA, 3 Phase, 400/220/33 KV including i Insulating Oil | No
2 | REACTOR & NGR
i | 110 MVAR, 765/Root3KV, Single Phase with oil | No
ii | 80 MVAR, 765/Root3KV, Single Phase with oil | No
iii | 50 MVAR, 765/Root3KV, Single Phase with oil | No
iv | NGR (Dry Core Type) for 765KV Reactor | No
v | Surge Arrestor for NGR - 765KV System | No
vi | 125MVAR, 400KV, 3Ph. Reactor with insulating Oil | No
vii | 80MVAR, 400KV, 3Ph. Reactor with insulating Oil | No
ix | 63MVAR, 400KV, 3Ph. Reactor with insulating Oil | No
x | 50MVAR, 400KV, 3Ph. Reactor with insulating Oil | No
xi | NGR for 400KV Reactor with insulating oil | No
xii | Surge Arrestor for NGR - 400KV System | No
3 | 765 KV EQUIPMENTS
i | 765 Kv,3150KA,40KA Circuit Breaker with CR | No
ii | 765 Kv,3150KA,40KA Circuit Breaker without CR | No
iii | 765 kV CTs 3000A, 40KA, 5-Core, | No
iv | 765 kv CVT 4400 PF | No
v | 765 KV,3150 A,40 kA Isolator 3-Phase with 1 E/S | No
vi | 765 KV,3150 A,40 kA Isolator 3-Phase with 2 E/S | No
vii | 765KV, 2000A, 40KA, S-Phase Isolator with 1 E/S | No
viii | 765 KV 3 Phase E/S | No
ix | 624KV Surge Arrestor | No
4 | 765KV C & R Panels
Circuit Breaker panel with Auto Reclose
Circuit Breaker panel without Auto Reclose
Line protection panel
765/400KV Transf. Protn.Panel (both HV and MV)
Reactor Protection Panel
Bus Bar Protection Panel
5 | 420KV EQUIPMENTS
420KV, 3150A, 40KA Breaker with CR
420KV, 3150A, 40KA Breaker without CR
420KV, 3000A, 40KA CT, 5 Core Current Transformer with 120% current rating,
420 kv CVT 4400 PF
420 kv CVT 8800 PF
420 KV,2000 A,40 kA DB Isolator 3 Ph. with 1 E/S
420 KV,3150A,40 kA Isolator 3 Ph. with 1 E/S
420 KV,3150A,40 kA Isolator 3 Ph. with 2 E/S
420 KV,2000 A,40 kA DB Isolator S Ph. with 1 E/S
390KV Surge Arrestor
6 | 400KV C & P Panels
Circuit Breaker panel without Auto Reclose
Circuit Breaker panel without Auto Reclose
Line protection panel
400/220KV Transf. protn. panel(both HV and MV)
Reactor protection panel
Bus Bar Protection Panel
7 | 245KV EQUIPMENTS
i | 245 KV, 1600A, 40KA Class Circuit Breaker
ii | 245 KV, 2500A 40KA Class Circuit Breaker
iii | 245KV,1600 A,40 kA ,5 core, CT with 120% extended current
iv | 245KV,1600 A,40 kA ,5 core, CT with 150% extended current
v | 245KV, CVT 4400 pf with 3 secondaries
vi | 245KV,1600A, 40 kA, 3Ph.Isolator DB Type - 1 E/S
vii | 245KV,1600A, 40 kA, 3-Ph.Isolator DB Type - 2 E/S
viii | 245KV,2500A, 40 kA, 3-Ph. Isolator DB Type 2 E/S
ix | 245KV, 1600A, 40 KA, 3 Ph.DB Tandem Type without E/S
x | 245KV,1600A, 40kA S Ph. Isolator DB Type - 1E/S
xi | 245KV,1600A, 40kA S Ph. Isolator DB Type w/o E/S
xii | 216 kV Surge Arrestors
8 | 220KV C & P Panels
i | Circuit Breaker panel with Auto Reclose
ii | Circuit Breaker panel without Auto Reclose
iii | Line protection panel
iv | Bus Bar Protection panel
9 | COMMON EQUIPMENTS
i | C & P Panel.
Time Synchronisation Equipment
Special Relay Test Kit
Video Projection System(VPS) 67" size
Complete Substation automation system for 400/230kV S/S including hardware and software for remote control station alongthwith associated equipments and Kiosks for the following bays ( bays as defined in the teechnical specification, Sec-Substaion Automat
ii | LT Switchgear
415V Main Switch Board
415V ACDB
415V MLDB
415V Emergency LDB
220V DCDB
50V DCDB
iii | Battery & Battery Charger
220V Battery
50V Battery
Battery Charger for 220V Battery
Battery Charger for 50V Battery
iv | DG Set-250KVA with control panel
v | High Wall Type Split AC unit of 2TR Capacity
vi | Illumination (Indoor)
vii | 72.5KV & 36 KV Equipments
800KVA 33/.440 KV Distribution Transformer
72.5KV Isolator without Earthswitch
72.5KV Horn gap Fuse
630KVA, 33/.440 KV Distribution Transformer
33KV Horn gap Fuse
33KV Isolator without ES
33KV Surge Arrestor.
viii | PLCC Equipments
3150A, 40KA,Line Trap(For 765KV)
3150A, 40KA, 1 mH Line Trap(for 400KV)
2000A, 40KA, 1 mH Line Trap(for 400KV)
1600, 40KA, 0.5 mH Line Trap(for 220KV)
Coupling device for 765KV
Coupling device for 400KV
Carr Eqpt (for speech+protection and speech+Data)-765KV
Carr Eqpt (for speech+protection and speech+Data)-400KV
Protection coupler-765KV
Protection coupler-400KV
HF Cable
EPAX(24/8) with 24 Telephones,Cables etc.,
Testing and Mainetance equipment
10 | Mandatory Spares
11 | ERECTION HARDWARE
i | 765 KV
Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary
765KV I Type Layout
Line bay
Transformer bay
Bus Reactor bay
Line Reactors
Bus(for one diameter)
ii | 400 KV
Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary
400 KV I Type Layout
Line bay
Transformer bay
Re-oriented Line bay
Spare bay of half dia
Line Reactor
Bus for two diameters
iii | 220 KV
Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary
220 KV DMT Type Layout
Line bay
Transformer bay
Main & Transfer Bus
Transfer bus coupler bay
Bus coupler bay
12 | Visual Monitoring system for watch & ward
13 | Fire Protection System
i | Pumping arrangement forHVW system and Hydrant System, complete with all piping, valves, fittings etc., inside pump House (Set)
ii | Hydrant system, complete U/G and O/G piping and accessories etc., outside the the pump House for(Set)
ii | HVW Sprray system complete with U/G and O/G pipeing and accessories etc out side the pump house along with one hydrant point for each of the following
765KV S-Phase Transformer
400KV 3-Phase Transformer
765KV S-Phase Shunt Reactor
765KV S-Phase Bus Reactor
400KV 3-Phase Shunt Reactor
400KV 3-Phase Bus Reactor
iii | Portable extinguishers (Set)
iv | Smoke detection system(Set)
14 | Illumination(Outdoor)
i | Switchyard Lighting
ii | Street Lighting
15 | Power & Control Cables - Total
Cables with associated accessories likeclamps, glands, lugs and straight joints etc.,(LS)
i | 1.1KV Power Cables
1C 630Sq.mm(XLPE)
1C 300Sq.mm(XLPE)
3.5C 300Sq.mm(XLPE)
1C 150Sq. Mm(PVC)
3.5C 70 Sq.mm(PVC)
ii | 1.1KV Power Cables(PVC) for 765KV S/S
3.5C 35Sq.mm
4C 16Sq.mm
4C 6Sq.mm
2C 6Sq.mm
iii | 1.1KV grade control cables(PVC) 765KV S/S
5C 2.5Sq.mm
7C 2.5Sq.mm
10C 2.5Sq.mm
14C 2.5Sq.mm
19C 2.5Sq.mm
27C 2.5Sq.mm
iv | 1.1KV Power Cables(PVC) for 400KV S/S
3.5C 35Sq.mm
4C 16Sq.mm
4C 6Sq.mm
2C 6Sq.mm
v | 1.1KV grade control cables(PVC) 400KV S/S
5C 2.5Sq.mm
7C 2.5Sq.mm
10C 2.5Sq.mm
14C 2.5Sq.mm
19C 2.5Sq.mm
27C 2.5Sq.mm
vi | 1.1KV Power Cables(PVC) for 220KV S/S
3.5C 35Sq.mm
4C 16Sq.mm
4C 6Sq.mm
vii | 1.1KV grade control cables(PVC) 220KV S/S
5C 2.5Sq.mm
7C 2.5Sq.mm
10C 2.5Sq.mm
14C 2.5Sq.mm
19C 2.5Sq.mm
27C 2.5Sq.mm
viii | HT Cable - 33KV Cable(Single Core)
Erection Rate Per Km
16 | Main Earthmat - 40 mm MS Rod 46Km- Total
Erection Rate Per Km
17 | Steel Structures (MT)
i | Lattice Type - Rate Per MT
ii | Pipe Type - Rate Per MT
Lattice Type - Total Price
Pipe Type - Total Price
CIVIL WORKS
1 | Control room cum Administrative Building | [12 empty] | 72.9672
2 | DG & FFPH Building | [12 empty] | 125.0867
3 | Water supply & Sanitary System | [12 empty] | 31.2717
4 | Foundation
765KV I.C.T 500 MVA, Single Phase(Complete)
765KV Shunt Reactor with NGR & SA(Complete)
765KV Bus Reactor (Complete)
Gantry structures(RCC Portion)
Equipment support structures(RCC Portion)
5 | Roads/Tracks | [12 empty] | 0.019745
Road cum Rail Track (from edge of road to edge of Tr. Foundn)
Road cum Rail Track (from edge of road to edge of Rtr.Foundn)
Roads inside Switchyard (3.75M & 7.0M) with crossings
6 | Cable Trenches (including Buried) | [12 empty] | 0.031272
7 | Site Surfacing & Antiweed Treatment | [12 empty] | 0.0005853
8 | Storm water Drains with culverts | [12 empty] | 0.017492
9 | Switchyard Fencing | [12 empty] | 0.00080738
10 | Rain water Harvesting
11 | Land Scaping
12 | Parking Shed | [12 empty] | 36.4836
Total
Foundations
| Foundation - 765KV S Phase Transformer | [12 empty] | 20.8478
| Foundation - 400/220 KV 3 Phase Transformer | [12 empty] | 15.6358
| Foundation - 400/220 KV S Phase Transformer | [12 empty] | 15.6358
| Fire wall between the Transformers | [12 empty] | 2.0848
| Foundation for 765KV Shunt Reactor | [12 empty] | 10.4239
| Foundation for NGR & SA of 765KV System | [12 empty] | 3.1272
| Foundation for 400KV Reactor with NGR & SA | [12 empty] | 10.4239
| Fire wall between the Shunt Reactors | [12 empty] | 1.0424
| Foundation for 765KV S Phase Bus Reactor | [12 empty] | 10.4239
| Foundation for 400KV 3 Phase Bus Reactor | [12 empty] | 10.4239
| Fire wall between the Bus Reactors | [12 empty] | 1.0424
| Foundations for Gantries, Equipments (Other than ICTs 7 Reactors) and Equipment Support Structures (Lumpsum) | [12 empty] | 1042.3889
Erection,Testing & Commissioning of Common Equipments
| Auxiliary Transformers, LT Switchgear, AC & DC Panels. 72.5 kV, 33kV, 11 kV equipments etc | [12 empty] | 3.3641
| Station D.C Batteries 220 V System | [12 empty] | 0.27989
| Station D.C Batteries 48 / 50 V System | [12 empty] | 0.11662
| Battery Charger for 220 V DC Battery System | [12 empty] | 0.22427
| Battery Charger for 48 / 50 V DC Battery System | [12 empty] | 0.16821
| Sub-Station Automation including Hardware, software, Remote Control Station, DMT scheme, Time Synchronising equipment, A/C kiosks etc., | [12 empty] | 11.2137
| Visual Monitoring System | [12 empty] | 3.3641
| Power cables | [12 empty] | 0.22427
| Control cables | [12 empty] | 0.22427
| Earth mat formation | [12 empty] | 16.8205
| Diesel Generator set with AMF panel 250 kVA | [12 empty] | 1.1214
| Air Conditioning and Ventilation | [12 empty] | 1.1214
| Fire Fighting System | [12 empty] | 26.9128
| Illumination System - Indoor & outdoor | [12 empty] | 11.2137
| PLCC Equipments (Total for the Sub - Station) | [12 empty] | 2.2427
| Erection,Testing & Commng -765KV S Phase Transformer | [12 empty] | 11.2137
| Erection,Testing & Commng-400/220KV 3 Phase Transf | [12 empty] | 6.7282
| Erection, Testng & Commng-400/220KV S Ph. Transformer | [12 empty] | 6.7282
| Erection, Testng & Commng - 765KV Shunt Reactor | [12 empty] | 4.4855
| Erection, Testng & Commng - NGR & SA of 765KV Shunt Reactor | [12 empty] | 4.4855
| Erection, Testng & Commng - 400KV Reactor with NGR & SA | [12 empty] | 1.1214
| Erection, Testng & Commng - 765KV, S Phase Bus Reactor | [12 empty] | 4.4855
| Erection, Testng & Commng - 400KV 3 Phase Bus Reactor | [12 empty] | 4.4855
Erection Testing & commisioning of 765KV Equipments
| 765KV Circuit breakers | [12 empty] | 1.0429
| 765KV Isolators | [12 empty] | 0.97559
| 765KV Current Transformers | [12 empty] | 0.56068
| 765KV CVT | [12 empty] | 0.56068
| 624KV Surge Arrestor | [12 empty] | 0.28034
| Bus Bars formation etc. | [12 empty] | 67.282
| Control & Protection panels | [12 empty] | 0
| 765KV CB relay Panel with Auto Reclosure | [12 empty] | 0.22427
| 765KV CB relay Panel without Auto Reclosure | [12 empty] | 0.22427
| 765KV Line Protection Panel | [12 empty] | 0.22427
| 765-400/33KV Transformer Protection Panel | [12 empty] | 0.22427
| 765KV Reactor Protection Panel | [12 empty] | 0.22427
| Duplicate Bus Bar Protection Panel - 765KV | [12 empty] | 0.89709
Erection Testing & commisioning of 400 kV Equipments
| 420 KV Circuit breakers | [12 empty] | 0.33641
| 420KV Isolators | [12 empty] | 0.22427
| 420 KV Current Transformers | [12 empty] | 0.067282
| 420KV CVT | [12 empty] | 0.067282
| 390KV surge Arrestors | [12 empty] | 0.033641
| Bus Bars formation etc | [12 empty] | 33.641
| C & P panels | [12 empty] | 0
| 400KV CB relay Panel with Reclosure | [12 empty] | 0.33641
| 400KV CB relay Panel without Auto Reclosure | [12 empty] | 1.0092
| 400KV Line Protection Panel | [12 empty] | 0.61285
| 400-220/33KV Transformer Protection Panel | [12 empty] | 0.10717
| 400KV Reactor Protection Panel | [12 empty] | 1.7924
| 400KV Bus Bar Protection panelPanel | [12 empty] | 1.4017
| 245 KV Circuit breakers | [12 empty] | 0.22427
| 245 KV Isolators | [12 empty] | 0.16821
| 245 KV Current Transformers | [12 empty] | 0.056068
| 245 KV CVT | [12 empty] | 0.056068
| 216 KV surge Arrestors | [12 empty] | 0.033641
| 220 kV Bus Bars formation etc | [12 empty] | 16.8205
| 220KV C & P Panels | [12 empty] | 0
| Circuit breaker relay panel | [12 empty] | 0.28034
| Line protection panel | [12 empty] | 0.7401
| Single Bus Bar protection panel | [12 empty] | 2.2427
| Lattice Type | [12 empty] | 0.022315
| Tubular Type | [12 empty] | 0.025791

## Average Cost
CERC
Capital Cost Benchmarking
Transmission Substations
Name of sub-station
Reference Numbers
Month and Year of LoA
| SUPPLY | Unit | Rate | Average Rates
1 | POWER TRANSFORMER (Single Phase Units)
i | I.C.T 500 MVA, Single Phase, 765√3 / 400√3 / 33 KV class including insulating Oil | No |  | 2017.1991
ii | I.C.T 167 MVA, Single Phase, 400/Root3 / 220/Root3 / 33 KV class including insulating Oil | No |  | 488.9265
iii | I.C.T 315 MVA, 3 Phase, 400/220/33 KV including Insulating Oil | No |  | 951.5373
2 | REACTOR & NGR
i | 110 MVAR, 765/Root3KV, Single Phase with oil | No |  | 0
ii | 80 MVAR, 765/Root3KV, Single Phase with oil | No |  | 472.8656
iii | 50 MVAR, 765/Root3KV, Single Phase with oil | No |  | 377.4858
iv | NGR (Dry Core Type) for 765KV Reactor | No |  | 82.0278
v | Surge Arrestor for NGR - 765KV System | No |  | 1.19
vi | 125MVAR, 400KV, 3 Ph. Reactor with insulating Oil | No |  | 432.4987
vii | 80MVAR, 400KV, 3 Ph. Reactor with insulating Oil | No |  | 424.9059
ix | 63MVAR, 400KV, 3 Ph. Reactor with insulating Oil | No |  | 377.4858
x | 50MVAR, 400KV, 3 Ph. Reactor with insulating Oil | No |  | 377.4858
xi | NGR for 400KV Reactor with insulating oil | No |  | 22.8965
xii | Surge Arrestor for NGR - 400KV System | No |  | 1.5091
3 | 765 KV EQUIPMENTS
i | 765 KV, 3150 KA, 40 KA Circuit Breaker with CR | No |  | 217.8318
ii | 765 KV,3150 KA, 40 KA Circuit Breaker without CR | No |  | 171.1422
iii | 765 KV CTs 3000A, 40 KA, 5-Core, | No |  | 33.6085
iv | 765 KV CVT 8800 PF | No |  | 18.3023
v | 765 KV,3150 A,40 kA Isolator 3-Phase with 1 E/S | No |  | 32.9605
vi | 765 KV,3150 A,40 kA Isolator 3-Phase with 2 E/S | No |  | 39.8505
vii | 765 KV, 2000A, 40KA, S-Phase Isolator with 1 E/S | No |  | 10.8881
viii | 765 KV 3 Phase E/S | No |  | 0
ix | 624 KV Surge Arrestor | No |  | 10.9571
4 | 765 KV C & R Panels
| Circuit Breaker Panel with Auto Reclose |  |  | 5.5782
| Circuit Breaker Panel without Auto Reclose |  |  | 5.4699
| Line Protection Panel |  |  | 26.3255
| 765/400KV Transf. Protn. Panel (both HV and MV) |  |  | 15.2857
| Reactor Protection Panel |  |  | 12.1634
| Bus Bar Protection Panel |  |  | 81.4575
5 | 420 KV EQUIPMENTS
| 420KV, 3150A, 40KA Breaker with CR |  |  | 39.8848
| 420KV, 3150A, 40KA Breaker without CR |  |  | 31.2274
| 420KV, 3000A, 40KA CT, 5 Core Current Transformer with 120% current rating, |  |  | 11.7655
| 420 KV CVT 4400 PF |  |  | 5.0281
| 420 KV CVT 8800 PF |  |  | 5.7418
| 420 KV,3150 A,40 kA DB Isolator 3 Ph. with 1 E/S |  |  | 9.1207
| 420 KV,2000 A,40 kA Isolator 3 Ph. with 1 E/S |  |  | 6.7981
| 420 KV,2000A,40 kA Isolator 3 Ph. with 2 E/S |  |  | 7.7035
| 420 KV,2000 A,40 kA DB Isolator S Ph. with 1 E/S |  |  | 3.632
| 390 KV Surge Arrestor |  |  | 1.6739
6 | 400KV C & P Panels
| Circuit Breaker panel with Auto Reclose |  |  | 5.5757
| Circuit Breaker panel without Auto Reclose |  |  | 4.8429
| Line protection panel |  |  | 21.284
| Transf. protn. Panel |  |  | 18.8276
| Reactor protection panel |  |  | 10.7155
| Bus Bar Protection Panel |  |  | 82.8774
7 | 245KV EQUIPMENTS
i | 245 KV, 1600A, 40KA Class Circuit Breaker |  |  | 17.2017
ii | 245 KV, 2500A 40KA Class Circuit Breaker |  |  | 17.2017
iii | 245KV,1600 A,40 kA ,5 core, CT with 120% extended current |  |  | 3.8963
iv | 245KV,1600 A,40 kA ,5 core, CT with 150% extended current |  |  | 4.2012
v | 245KV, CVT 4400 pf with 3 secondaries |  |  | 3.5738
vi | 245KV,1600A, 40 kA, 3Ph.Isolator DB Type - 1 E/S |  |  | 3.3404
vii | 245KV,1600A, 40 kA, 3-Ph.Isolator DB Type - 2 E/S |  |  | 4.0854
viii | 245KV,2500A, 40 kA, 3-Ph. Isolator DB Type 2 E/S |  |  | 4.5043
ix | 245KV, 1600A, 40 KA, 3 Ph.DB Tandem Type without E/S |  |  | 2.8188
xii | 216 kV Surge Arrestors |  |  | 0.39215
8 | 220KV C & P Panels
i | Circuit Breaker panel with Auto Reclose |  |  | 8.12
ii | Circuit Breaker panel without Auto Reclose |  |  | 6.45
iii | Line protection panel |  |  | 18.18
iv | Bus Bar Protection panel |  |  | 63.3948
9 | COMMON EQUIPMENTS
i | C & P Panel.
a | Time Synchronisation Equipment |  |  | 0
b | Special Relay Test Kit |  |  | 0
c | Video Projection System(VPS) 67" size |  |  | 0
d | Complete Substation automation system for 765/400/230kV S/S including hardware and software for remote control station alongthwith associated equipments and Kiosks for the following bays ( bays as defined in the teechnical specification, Sec-Substaion Aut |  |  | 250
ii | LT Switchgear
| 415V Main Switch Board |  |  | 15.5907
| 415V ACDB |  |  | 15.3964
| 415V MLDB |  |  | 11.1748
| 415V Emergency LDB |  |  | 4.7115
| 220V DCDB |  |  | 3.7283
| 50V DCDB |  |  | 2.7214
iii | Battery & Battery Charger
a | 220V Battery |  |  | 11.4135
b | 50V Battery |  |  | 2.2814
c | Battery Charger for 220V Battery |  |  | 4.1205
d | Battery Charger for 50V Battery |  |  | 2.4783
iv | DG Set-250KVA with control panel |  |  | 34.4451
v | High Wall Type Split AC unit of 2TR Capacity |  |  | 0.47721
vi | Illumination |  |  | 96.6259
vii | 72.5KV & 36 KV Equipments |  |  | 0
a | 800KVA 33/.440 KV Distribution Transformer |  |  | 0
| 72.5KV circuit breakers(3ph.) |  |  | 0
b | 72.5KV Isolator without Earthswitch |  |  | 0
c | 72.5KV Horn gap Fuse |  |  | 0
d | 630KVA, 33/.440 KV Distribution Transformer |  |  | 0
e | 33KV Horn gap Fuse |  |  | 0
f | 33KV Isolator without ES |  |  | 0
g | 33KV Surge Arrestor. |  |  | 0
viii | PLCC Equipments |  |  | 121.8388
| 3150A, 40KA,Line Trap(For 765KV) |  |  | 0
| 3150A, 40KA, 1 mH Line Trap(for 400KV) |  |  | 0
| 2000A, 40KA, 1 mH Line Trap(for 400KV) |  |  | 0
| 1600, 40KA, 0.5 mH Line Trap(for 220KV) |  |  | 0
| Coupling device for 765KV |  |  | 0
| Coupling device for 400KV |  |  | 0
| Carr Eqpt (for speech+protection and speech+Data)-765KV |  |  | 0
| Carr Eqpt (for speech+protection and speech+Data)-400KV |  |  | 0
| Protection coupler-765KV |  |  | 0
| Protection coupler-400KV |  |  | 0
| HF Cable |  |  | 0
| EPAX(24/8) with 24 Telephones,Cables etc., |  |  | 0
| Testing and Mainetance equipment |  |  | 0
10 | Mandatory Spares |  |  | 345.0764
11 | ERECTION HARDWARE |  |  | 0
i | 765 KV
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary |  |  | 655.9658
| 765KV I Type Layout |  |  | 0
| Line bay |  |  | 0
| Transformer bay |  |  | 0
| Bus Reactor bay |  |  | 0
| Line Reactors |  |  | 0
| Bus(for one diameter) |  |  | 0
0
ii | 400 KV
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary |  |  | 361.487
| 400 KV I Type Layout |  |  | 0
| Line bay |  |  | 0
| Transformer bay |  |  | 0
| Re-oriented Line bay |  |  | 0
| Spare bay of half dia |  |  | 0
| Line Reactor |  |  | 0
Bus for two diameters
iii | 220 KV
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary |  |  | 130.1172
| 220 KV DMT Type Layout |  |  | 0
| Line bay |  |  | 0
| Transformer bay |  |  | 0
| Main & Transfer Bus |  |  | 0
| Transfer bus coupler bay |  |  | 0
Bus coupler bay
12 | Visual Monitoring system for watch & ward |  |  | 0
13 | Fire Protection System |  |  | 380.9976
i | Pumping arrangement forHVW system and Hydrant System, complete with all piping, valves, fittings etc., inside pump House (Set) |  |  | 0
ii | Hydrant system, complete U/G and O/G piping and accessories etc., outside the the pump House for(Set) |  |  | 0
iii | HVW Sprray system complete with U/G and O/G pipeing and accessories etc out side the pump house along with one hydrant point for each of the following |  |  | 0
| 765KV S-Phase Transformer |  |  | 0
| 400KV 3-Phase Transformer |  |  | 0
| 765KV S-Phase Shunt Reactor |  |  | 0
| 765KV S-Phase Bus Reactor |  |  | 0
| 400KV 3-Phase Shunt Reactor |  |  | 0
| 400KV 3-Phase Bus Reactor |  |  | 0
iv | Portable extinguishers (Set) |  |  | 0
v | Smoke detection system(Set) |  |  | 0
14 | Illumination -- Indoor + Outdoor |  |  | 143.9835
i | Switchyard Lighting
ii | Street Lighting
15 | Power & Control Cables : Per Km Rate | Lump-Sum
i | Power Cable - |  |  | 1.4982
ii | Control Cable |  |  | 1.1211
Cables with associated accessories likeclamps, glands, lugs and straight joints etc.,(LS)
i | 1.1KV Power Cables
| 1C 630Sq.mm(XLPE) |  |  | 0
| 1C 300Sq.mm(XLPE) |  |  | 0
| 3.5C 300Sq.mm(XLPE) |  |  | 0
| 1C 150Sq. Mm(PVC) |  |  | 0
| 3.5C 70 Sq.mm(PVC) |  |  | 0
ii | 1.1KV Power Cables(PVC) for 765KV S/S
| 3.5C 35Sq.mm |  |  | 0
| 4C 16Sq.mm |  |  | 0
| 4C 6Sq.mm |  |  | 0
| 2C 6Sq.mm |  |  | 0
iii | 1.1KV grade control cables(PVC) 765KV S/S
| 5C 2.5Sq.mm |  |  | 0
| 7C 2.5Sq.mm |  |  | 0
| 10C 2.5Sq.mm |  |  | 0
| 14C 2.5Sq.mm |  |  | 0
| 19C 2.5Sq.mm |  |  | 0
| 27C 2.5Sq.mm |  |  | 0
iv | 1.1KV Power Cables(PVC) for 400KV S/S
| 3.5C 35Sq.mm |  |  | 0
| 4C 16Sq.mm |  |  | 0
| 4C 6Sq.mm |  |  | 0
| 2C 6Sq.mm |  |  | 0
v | 1.1KV grade control cables(PVC) 400KV S/S
| 5C 2.5Sq.mm |  |  | 0
| 7C 2.5Sq.mm |  |  | 0
| 10C 2.5Sq.mm |  |  | 0
| 14C 2.5Sq.mm |  |  | 0
| 19C 2.5Sq.mm |  |  | 0
| 27C 2.5Sq.mm |  |  | 0
vi | 1.1KV Power Cables(PVC) for 220KV S/S
| 3.5C 35Sq.mm |  |  | 0
| 4C 16Sq.mm |  |  | 0
| 4C 6Sq.mm |  |  | 0
vii | 1.1KV grade control cables(PVC) 220KV S/S
| 5C 2.5Sq.mm |  |  | 0
| 7C 2.5Sq.mm |  |  | 0
| 10C 2.5Sq.mm |  |  | 0
| 14C 2.5Sq.mm |  |  | 0
| 19C 2.5Sq.mm |  |  | 0
| 27C 2.5Sq.mm |  |  | 0
| Power & Control Cables : Total Price |  |  | 0
| Power Cable - |  |  | 0
viii | Control Cable
| Control Cable |  |  | 0
16 | Main Earthmat - 40 mm MS Rod Rate Per Km |  |  | 4.9671
| 40mm MS Rods - 46Km |  |  | 0
| Main Earthmat - 40 mm MS Rod : Total Price |  |  | 0
17 | Steel Structures (Rate Per MT)
i | MS |  |  | 0.68144
ii | HT |  |  | 0.90858
Steel Structures Total price
Lattice Type - : Total Price
H.T steel - Total Price
ERECTION
1 | POWER TRANSFORMER (Single Phase Units)
i | I.C.T 500 MVA, Single Phase, 765/Root3 / 400/Root3 / 33 KV class including insulating Oil | No |  | 0
ii | I.C.T 167 MVA, Single Phase, 400/Root3 / 220/Root3 / 33 KV class including insulating Oil | No |  | 0
iii | I.C.T 315 MVA, 3 Phase, 400/220/33 KV including i Insulating Oil | No |  | 0
0
2 | REACTOR & NGR |  |  | 0
i | 110 MVAR, 765/Root3KV, Single Phase with oil | No |  | 0
ii | 80 MVAR, 765/Root3KV, Single Phase with oil | No |  | 0
iii | 50 MVAR, 765/Root3KV, Single Phase with oil | No |  | 0
iv | NGR (Dry Core Type) for 765KV Reactor | No |  | 0
v | Surge Arrestor for NGR - 765KV System | No |  | 0
vi | 125MVAR, 400KV, 3Ph. Reactor with insulating Oil | No |  | 0
vii | 80MVAR, 400KV, 3Ph. Reactor with insulating Oil | No |  | 0
ix | 63MVAR, 400KV, 3Ph. Reactor with insulating Oil | No |  | 0
x | 50MVAR, 400KV, 3Ph. Reactor with insulating Oil | No |  | 0
xi | NGR for 400KV Reactor with insulating oil | No |  | 0
xii | Surge Arrestor for NGR - 400KV System | No |  | 0
0
3 | 765 KV EQUIPMENTS |  |  | 0
i | 765 Kv,3150KA,40KA Circuit Breaker with CR | No |  | 0
ii | 765 Kv,3150KA,40KA Circuit Breaker without CR | No |  | 0
iii | 765 kV CTs 3000A, 40KA, 5-Core, | No |  | 0
iv | 765 kv CVT 4400 PF | No |  | 0
v | 765 KV,3150 A,40 kA Isolator 3-Phase with 1 E/S | No |  | 0
vi | 765 KV,3150 A,40 kA Isolator 3-Phase with 2 E/S | No |  | 0
vii | 765KV, 2000A, 40KA, S-Phase Isolator with 1 E/S | No |  | 0
viii | 765 KV 3 Phase E/S | No |  | 0
ix | 624KV Surge Arrestor | No |  | 0
0
4 | 765KV C & R Panels |  |  | 0
| Circuit Breaker panel with Auto Reclose |  |  | 0
| Circuit Breaker panel without Auto Reclose |  |  | 0
| Line protection panel |  |  | 0
| 765/400KV Transf. protn. panel(both HV and MV) |  |  | 0
| Reactor protection panel |  |  | 0
| Bus Bar Protection Panel |  |  | 0
0
5 | 420KV EQUIPMENTS |  |  | 0
| 420 KV, 3150A, 40KA Breaker with CR |  |  | 0
| 420 KV, 3150A, 40KA Breaker without CR |  |  | 0
| 420 KV, 3000A, 40KA CT, 5 Core Current Transformer with 120% current rating |  |  | 0
| 420 KV CVT 4400 PF |  |  | 0
| 420 KV CVT 8800 PF |  |  | 0
| 420 KV,2000 A,40 kA DB Isolator 3 Ph. with 1 E/S |  |  | 0
| 420 KV,3150A,40 kA Isolator 3 Ph. with 1 E/S |  |  | 0
| 420 KV,3150A,40 kA Isolator 3 Ph. with 2 E/S |  |  | 0
| 420 KV,2000 A,40 kA DB Isolator S Ph. with 1 E/S |  |  | 0
| 390 KV Surge Arrestor |  |  | 0
0
6 | 400KV C & P Panels |  |  | 0
| Circuit Breaker panel without Auto Reclose |  |  | 0
| Circuit Breaker panel without Auto Reclose |  |  | 0
| Line Protection Panel |  |  | 0
| 400/220KV Transf.Protn.Panel (both HV and MV) |  |  | 0
| Reactor Protection Panel |  |  | 0
| Bus Bar Protection Panel |  |  | 0
0
7 | 245KV EQUIPMENTS |  |  | 0
i | 245 KV, 1600A, 40KA Class Circuit Breaker |  |  | 0
ii | 245 KV, 2500A 40KA Class Circuit Breaker |  |  | 0
iii | 245KV,1600 A,40 kA ,5 core, CT with 120% extended current |  |  | 0
iv | 245KV,1600 A,40 kA ,5 core, CT with 150% extended current |  |  | 0
v | 245KV, CVT 4400 pf with 3 secondaries |  |  | 0
vi | 245KV, 1600A, 40 kA, 3-Ph.Isolator DB Type - 1 E/S |  |  | 0
vii | 245KV, 1600A, 40 kA, 3-Ph.Isolator DB Type - 2 E/S |  |  | 0
viii | 245KV, 2500A, 40 kA, 3-Ph. Isolator DB Type 2 E/S |  |  | 0
ix | 245KV, 1600A, 40 kA, 3 Ph.DB Tandem Type without E/S |  |  | 0
x | 245KV, 1600A, 40 kA S Ph. Isolator DB Type - 1E/S |  |  | 0
xi | 245KV,1600A, 40 kA S Ph. Isolator DB Type w/o E/S |  |  | 0
xii | 216 kV Surge Arrestors |  |  | 0
0
8 | 220KV C & P Panels |  |  | 0
i | Circuit Breaker panel with Auto Reclose |  |  | 0
ii | Circuit Breaker panel without Auto Reclose |  |  | 0
iii | Line protection panel |  |  | 0
iv | Bus Bar Protection panel |  |  | 0
9 | COMMON EQUIPMENTS
i | C & P Panel.
| Time Synchronisation Equipment |  |  | 0
| Special Relay Test Kit |  |  | 0
| Video Projection System(VPS) 67" size |  |  | 0
| Complete Substation automation system for 400/230kV S/S including hardware and software for remote control station alongthwith associated equipments and Kiosks for the following bays ( bays as defined in the teechnical specification, Sec-Substaion Automat |  |  | 0
ii | LT Switchgear
| 415V Main Switch Board |  |  | 0
| 415V ACDB |  |  | 0
| 415V MLDB |  |  | 0
| 415V Emergency LDB |  |  | 0
| 220V DCDB |  |  | 0
| 50V DCDB |  |  | 0
iii | Battery & Battery Charger
| 220V Battery |  |  | 0
| 50V Battery |  |  | 0
| Battery Charger for 220V Battery |  |  | 0
| Battery Charger for 50V Battery |  |  | 0
iv | DG Set-250KVA with control panel |  |  | 0
v | High Wall Type Split AC unit of 2TR Capacity |  |  | 0
vi | Illumination (Indoor) |  |  | 0
vii | 72.5KV & 36 KV Equipments
| 800KVA 33/.440 KV Distribution Transformer |  |  | 0
| 72.5KV Isolator without Earthswitch |  |  | 0
| 72.5KV Horn gap Fuse |  |  | 0
| 630KVA, 33/.440 KV Distribution Transformer |  |  | 0
| 33KV Horn gap Fuse |  |  | 0
| 33KV Isolator without ES |  |  | 0
| 33KV Surge Arrestor. |  |  | 0
viii | PLCC Equipments |  |  | 0
| 3150A, 40KA,Line Trap(For 765KV) |  |  | 0
| 3150A, 40KA, 1 mH Line Trap(for 400KV) |  |  | 0
| 2000A, 40KA, 1 mH Line Trap(for 400KV) |  |  | 0
| 1600, 40KA, 0.5 mH Line Trap(for 220KV) |  |  | 0
| Coupling device for 765KV |  |  | 0
| Coupling device for 400KV |  |  | 0
| Carr Eqpt (for speech+protection and speech+Data)-765KV |  |  | 0
| Carr Eqpt (for speech+protection and speech+Data)-400KV |  |  | 0
| Protection coupler-765KV |  |  | 0
| Protection coupler-400KV |  |  | 0
| HF Cable |  |  | 0
| EPAX(24/8) with 24 Telephones,Cables etc., |  |  | 0
| Testing and Mainetance equipment |  |  | 0
0
10 | Mandatory Spares |  |  | 0
0
11 | ERECTION HARDWARE |  |  | 0
i | 765 KV |  |  | 0
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary |  |  | 0
| 765KV I Type Layout |  |  | 0
| Line bay |  |  | 0
| Transformer bay |  |  | 0
| Bus Reactor bay |  |  | 0
| Line Reactors |  |  | 0
| Bus(for one diameter) |  |  | 0
0
ii | 400 KV |  |  | 0
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary |  |  | 0
| 400 KV I Type Layout |  |  | 0
| Line bay |  |  | 0
| Transformer bay |  |  | 0
| Re-oriented Line bay |  |  | 0
| Spare bay of half dia |  |  | 0
| Line Reactor |  |  | 0
| Bus for two diameters |  |  | 0
0
iii | 220 KV |  |  | 0
| Bus post insulators & insulator strings, Disc Insulators, Hardware, Spacers, ACSR Brersimis Conductor, Bus Bar material, Cable Trays, Bay MB, Clamps, Connectors including equipment connectors, Junction box, Earthwire, Earthing material, Risers, Auxiliary |  |  | 0
| 220 KV DMT Type Layout |  |  | 0
| Line bay |  |  | 0
| Transformer bay |  |  | 0
| Main & Transfer Bus |  |  | 0
| Transfer bus coupler bay |  |  | 0
| Bus coupler bay |  |  | 0
0
12 | Visual Monitoring system for watch & ward |  |  | 0
0
13 | Fire Protection System |  |  | 0
i | Pumping arrangement forHVW system and Hydrant System, complete with all piping, valves, fittings etc., inside pump House (Set) |  |  | 0
ii | Hydrant system, complete U/G and O/G piping and accessories etc., outside the the pump House for(Set) |  |  | 0
ii | HVW Sprray system complete with U/G and O/G pipeing and accessories etc out side the pump house along with one hydrant point for each of the following |  |  | 0
| 765KV S-Phase Transformer |  |  | 0
| 400KV 3-Phase Transformer |  |  | 0
| 765KV S-Phase Shunt Reactor |  |  | 0
| 765KV S-Phase Bus Reactor |  |  | 0
| 400KV 3-Phase Shunt Reactor |  |  | 0
| 400KV 3-Phase Bus Reactor |  |  | 0
iii | Portable extinguishers (Set) |  |  | 0
iv | Smoke detection system(Set) |  |  | 0
0
14 | Illumination(Outdoor) |  |  | 0
i | Switchyard Lighting |  |  | 0
ii | Street Lighting |  |  | 0
0
15 | Power & Control Cables - Total |  |  | 0
| Cables with associated accessories likeclamps, glands, lugs and straight joints etc.,(LS) |  |  | 0
i | 1.1KV Power Cables |  |  | 0
| 1C 630Sq.mm(XLPE) |  |  | 0
| 1C 300Sq.mm(XLPE) |  |  | 0
| 3.5C 300Sq.mm(XLPE) |  |  | 0
| 1C 150Sq. Mm(PVC) |  |  | 0
| 3.5C 70 Sq.mm(PVC) |  |  | 0
ii | 1.1KV Power Cables(PVC) for 765KV S/S |  |  | 0
| 3.5C 35Sq.mm |  |  | 0
| 4C 16Sq.mm |  |  | 0
| 4C 6Sq.mm |  |  | 0
| 2C 6Sq.mm |  |  | 0
iii | 1.1KV grade control cables(PVC) 765KV S/S |  |  | 0
| 5C 2.5Sq.mm |  |  | 0
| 7C 2.5Sq.mm |  |  | 0
| 10C 2.5Sq.mm |  |  | 0
| 14C 2.5Sq.mm |  |  | 0
| 19C 2.5Sq.mm |  |  | 0
| 27C 2.5Sq.mm |  |  | 0
iv | 1.1KV Power Cables(PVC) for 400KV S/S |  |  | 0
| 3.5C 35Sq.mm |  |  | 0
| 4C 16Sq.mm |  |  | 0
| 4C 6Sq.mm |  |  | 0
| 2C 6Sq.mm |  |  | 0
v | 1.1KV grade control cables(PVC) 400KV S/S |  |  | 0
| 5C 2.5Sq.mm |  |  | 0
| 7C 2.5Sq.mm |  |  | 0
| 10C 2.5Sq.mm |  |  | 0
| 14C 2.5Sq.mm |  |  | 0
| 19C 2.5Sq.mm |  |  | 0
| 27C 2.5Sq.mm |  |  | 0
vi | 1.1KV Power Cables(PVC) for 220KV S/S |  |  | 0
| 3.5C 35Sq.mm |  |  | 0
| 4C 16Sq.mm |  |  | 0
| 4C 6Sq.mm |  |  | 0
vii | 1.1KV grade control cables(PVC) 220KV S/S |  |  | 0
| 5C 2.5Sq.mm |  |  | 0
| 7C 2.5Sq.mm |  |  | 0
| 10C 2.5Sq.mm |  |  | 0
| 14C 2.5Sq.mm |  |  | 0
| 19C 2.5Sq.mm |  |  | 0
| 27C 2.5Sq.mm |  |  | 0
viii | HT Cable - 33KV Cable(Single Core) |  |  | 0
| Erection Rate Per Km |  |  | 0
0
16 | Main Earthmat - 40 mm MS Rod 46Km- Total |  |  | 0
| Erection Rate Per Km |  |  | 0
0
17 | Steel Structures (MT) |  |  | 0
i | Lattice Type - Rate Per MT |  |  | 0
ii | Pipe Type - Rate Per MT |  |  | 0
| Lattice Type - Total Price |  |  | 0
| Pipe Type - Total Price |  |  | 0
0
| CIVIL WORKS |  |  | 0
1 | Control room cum Administrative Building |  |  | 72.9672
2 | DG & FFPH Building |  |  | 125.0867
3 | Water supply & Sanitary System |  |  | 31.2717
4 | Foundation |  |  | 0
| 765KV I.C.T 500 MVA, Single Phase(Complete) |  |  | 0
| 765KV Shunt Reactor with NGR & SA(Complete) |  |  | 0
| 765KV Bus Reactor (Complete) |  |  | 0
| Gantry structures(RCC Portion) |  |  | 0
| Equipment support structures(RCC Portion) |  |  | 0
5 | Roads/Tracks |  |  | 0.019745
| Road cum Rail Track (from edge of road to edge of Tr. Foundn) |  |  | 0
| Road cum Rail Track (from edge of road to edge of Rtr.Foundn) |  |  | 0
| Roads inside Switchyard (3.75M & 7.0M) with crossings |  |  | 0
6 | Cable Trenches (including Buried) |  |  | 0.031272
7 | Site Surfacing & Antiweed Treatment |  |  | 0.0005853
8 | Storm water Drains with culverts |  |  | 0.017492
9 | Switchyard Fencing |  |  | 0.00080738
10 | Rain water Harvesting
11 | Land Scaping |  |  | 0
12 | Parking Shed |  |  | 36.4836
| Total |  |  | 0
Foundations
| Foundation - 765KV S Phase Transformer |  |  | 20.8478
| Foundation - 400/220 KV 3 Phase Transformer |  |  | 15.6358
| Foundation - 400/220 KV S Phase Transformer |  |  | 15.6358
| Fire wall between the Transformers |  |  | 2.0848
| Foundation for 765KV Shunt Reactor |  |  | 10.4239
| Foundation for NGR & SA of 765KV System |  |  | 3.1272
| Foundation for 400KV Reactor with NGR & SA |  |  | 10.4239
| Fire wall between the Shunt Reactors |  |  | 1.0424
| Foundation for 765KV S Phase Bus Reactor |  |  | 10.4239
| Foundation for 400KV 3 Phase Bus Reactor |  |  | 10.4239
| Fire wall between the Bus Reactors |  |  | 1.0424
| Foundations for Gantries, Equipments (Other than ICTs 7 Reactors) and Equipment Support Structures (Lumpsum) |  |  | 1042.3889
Erection,Testing & Commissioning of Common Equipments
| Auxiliary Transformers, LT Switchgear, AC & DC Panels. 72.5 kV, 33kV, 11 kV equipments etc |  |  | 3.3641
| Station D.C Batteries 220 V System |  |  | 0.27989
| Station D.C Batteries 48 / 50 V System |  |  | 0.11662
| Battery Charger for 220 V DC Battery System |  |  | 0.22427
| Battery Charger for 48 / 50 V DC Battery System |  |  | 0.16821
| Sub-Station Automation including Hardware, software, Remote Control Station, DMT scheme, Time Synchronising equipment, A/C kiosks etc., |  |  | 11.2137
| Visual Monitoring System |  |  | 3.3641
| Power cables |  |  | 0.22427
| Control cables |  |  | 0.22427
| Earth mat formation |  |  | 16.8205
| Diesel Generator set with AMF panel 250 kVA |  |  | 1.1214
| Air Conditioning and Ventilation |  |  | 1.1214
| Fire Fighting System |  |  | 26.9128
| Illumination System - Indoor & outdoor |  |  | 11.2137
| PLCC Equipments (Total for the Sub - Station) |  |  | 2.2427
| Erection,Testing & Commng -765KV S Phase Transformer |  |  | 11.2137
| Erection,Testing & Commng-400/220KV 3 Phase Transf |  |  | 6.7282
| Erection, Testng & Commng-400/220KV S Ph. Transformer |  |  | 6.7282
| Erection, Testng & Commng - 765KV Shunt Reactor |  |  | 4.4855
| Erection, Testng & Commng - NGR & SA of 765KV Shunt Reactor |  |  | 4.4855
| Erection, Testng & Commng - 400KV Reactor with NGR & SA |  |  | 1.1214
| Erection, Testng & Commng - 765KV, S Phase Bus Reactor |  |  | 4.4855
| Erection, Testng & Commng - 400KV 3 Phase Bus Reactor |  |  | 4.4855
Erection Testing & commisioning of 765KV Equipments
| 765KV Circuit breakers |  |  | 1.0429
| 765KV Isolators |  |  | 0.97559
| 765KV Current Transformers |  |  | 0.56068
| 765KV CVT |  |  | 0.56068
| 624KV Surge Arrestor |  |  | 0.28034
| Bus Bars formation etc. |  |  | 67.282
Control & Protection panels
| 765KV CB relay Panel with Auto Reclosure |  |  | 0.22427
| 765KV CB relay Panel without Auto Reclosure |  |  | 0.22427
| 765KV Line Protection Panel |  |  | 0.22427
| 765-400/33KV Transformer Protection Panel |  |  | 0.22427
| 765KV Reactor Protection Panel |  |  | 0.22427
| Duplicate Bus Bar Protection Panel - 765KV |  |  | 0.89709
Erection Testing & commisioning of 400 kV Equipments
| 420 KV Circuit breakers |  |  | 0.33641
| 420KV Isolators |  |  | 0.22427
| 420 KV Current Transformers |  |  | 0.067282
| 420KV CVT |  |  | 0.067282
| 390KV surge Arrestors |  |  | 0.033641
| Bus Bars formation etc |  |  | 33.641
| C & P panels |  |  | 0
| 400KV CB relay Panel with Reclosure |  |  | 0.33641
| 400KV CB relay Panel without Auto Reclosure |  |  | 1.0092
| 400KV Line Protection Panel |  |  | 0.61285
| 400-220/33KV Transformer Protection Panel |  |  | 0.10717
| 400KV Reactor Protection Panel |  |  | 1.7924
| 400KV Bus Bar Protection panelPanel |  |  | 1.4017
| 245 KV Circuit breakers |  |  | 0.22427
| 245 KV Isolators |  |  | 0.16821
| 245 KV Current Transformers |  |  | 0.056068
| 245 KV CVT |  |  | 0.056068
| 216 KV surge Arrestors |  |  | 0.033641
| 220 kV Bus Bars formation etc |  |  | 16.8205
| 220KV C & P Panels |  |  | 0
| Circuit breaker relay panel |  |  | 0.28034
| Line protection panel |  |  | 0.7401
| Single Bus Bar protection panel |  |  | 2.2427
| Lattice Type |  |  | 0.022315
| Tubular Type |  |  | 0.025791

## Alternates
CERC
Capital Cost Benchmarking
Transmission Substations
BOQ FOR 765 / 400 / 220 KV SUB - STATION : ALT - 765 / 1, ALT - 765 / 2 AND ALT - 765 / 3
SUB - STATIONS
| S. No | Description | Unit | Rate | ALT-765 / 1 |  | ALT-765 / 2 |  | ALT- 765 / 3 |  | 765KV Line Ter. Bay with Shunt Reactor |  | 765KV Line Ter. Bay without Sh. Reactor |  | 765/400KV Transformer. Bay |  | 765KV Bus Reactor bay |  | 765KV Shunt Reactor (Add or Delete) |  | 400KV Line Ter. Bay with Shunt Reactor |  | 400KV Line Ter. Bay without Sh. Reactor |  | 400KV Bus Reactor bay |  | 400KV Shunt Reactor (Add or Delete) |  | 220KV Line Ter. bay |  | 400/220 kV ICT
[5 empty] | Quantity | Amount - INR | Quantity | Amount - INR | Quantity | Amount - INR | Qnty | Amount INR | Qnty | Amount INR | Qnty | Amount INR | Qnty | Amount INR | Qnty | Amount INR | Qnty | Amount INR | Qnty | Amount INR | Qnty | Amount INR | Qnty | Amount INR | Qnty | Amount INR | Qnty | Amount INR
| 1 | Common General Works
| 1-A | Land devolopment & Civil engineering works
| a) | Soil Investigation (lump Sum) | No | 10 | 1 | 10 | 1 | 10 | 1 | 10
| b) | Intial Civil Engineering Works like Levelling,Retaining walls,Appoch Road,Peripheral Fencing etc (lump Sum) | No | 150 | 1 | 150 | 1 | 150 | 1 | 150
| c) | Ant weed treatment & Site Surfing Cost per Meter | Sq mt | 0.0005853 | 362676 | 212.2755 | 342676 | 200.5695 | 362676 | 212.2755
| e) | Road work (Cost per Meter) | Metre | 0.019745 | 350 | 6.9107 | 320 | 6.3183 | 350 | 6.9107
| d) | Storm water drain, Road culverts drain crossing, cable trench crossing | Metre | 0.00080738 | 500 | 0.40369 | 500 | 0.40369 | 500 | 0.40369
| e) | Switch yard fencing | Metre | 0.00080738 | 3000 | 2.4222 | 2900 | 2.3414 | 3000 | 2.4222
| f) | DG room & Fire fighting Room (FFPH) | No | 72.9672 | 1 | 72.9672 | 1 | 72.9672 | 1 | 72.9672
| g) | Control room with cable vaults | No | 125.0867 | 1 | 125.0867 | 1 | 125.0867 | 1 | 125.0867
| h) | Cable ducts | Metre | 0.031272 | 4000 | 125.0867 | 3500 | 109.4508 | 3500 | 109.4508 | 200 | 6.2543 | 200 | 6.2543 | 300 | 9.3815 | 200 | 6.2543 | 150 | 4.6908 | 200 | 6.2543 | 200 | 6.2543 | 200 | 6.2543 | 100 | 3.1272 | 150 | 4.6908 | 300 | 9.3815
| i) | Providing water supply including drinking water & water for fire fighting system and sewage system | No | 31.2717 | 1 | 31.2717 | 1 | 31.2717 | 1 | 31.2717
| j) | Parking sheds,Rain water Harvesting systems & land scaping etc., | No | 36.4836 | 1 | 36.4836 | 1 | 36.4836 | 1 | 36.4836
|  | Sub-Total -1-A |  |  |  | 772.9079 |  | 744.8929 |  | 757.2721 |  | 6.2543 |  | 6.2543 |  | 9.3815 |  | 6.2543 |  | 4.6908 |  | 6.2543 |  | 6.2543 |  | 6.2543 |  | 3.1272 |  | 4.6908 |  | 9.3815
| 1-B | Electrical works
| a) | LT Switch Gear consisting of 415 V main switch board, ACDB, MLDB, Emergency LDB, A/C DB, 220 V DCDB, 50V DCDB, 1 trasformer each of rating 630KVA, 11kV/440V and 800KVA, 33KV/440V,72.5KV Isolator, CT, PT, CB/Fuse 33KV and 11KV Isolator, fuse, SA | No | 80 | 1 | 80 | 1 | 80 | 1 | 80
| b) | Station D.C Batteries 220 V, 500 AH |  | 11.4135 | 2 | 22.8269 | 2 | 22.8269 | 2 | 22.8269
| c) | Station D.C Batteries 50 V, 500 AH |  | 2.2814 | 2 | 4.5628 | 2 | 4.5628 | 2 | 4.5628
| d) | Battery Charger System 220 V, 70A / 50 A Float cum Boost |  | 4.1205 | 2 | 8.2409 | 2 | 8.2409 | 2 | 8.2409
| e) | Battery Charger System 50 V, 70 A / 50 A Float cum Boost | Set | 2.4783 | 2 | 4.9567 | 2 | 4.9567 | 2 | 4.9567
| f) | Sub-Station Automation including Hardware, software, Remote Control Station, DMT scheme, Time Synchronising equipment, A/C kiosks etc., | LumpSum | 250 | 1 | 250 | 0.9 | 225 | 1 | 250 | 0.1 | 25 | 0.1 | 25 | 0.15 | 37.5 | 0.1 | 25 |  |  | 0.1 | 25 | 0.1 | 25 | 0.1 | 25 |  |  |  |  | 0.25 | 62.5
| g) | Visual Monitoring System | Set | 26 | 1 | 26 | 1 | 26 | 1 | 26
| h) | Power Cables | Km | 1.4982 | 62 | 92.8861 | 52 | 77.9045 | 120 | 179.7796 | 12 | 17.978 | 10 | 14.9816 | 16 | 23.9706 | 10 | 14.9816 | 5 | 7.4908 | 8 | 11.9853 | 10 | 14.9816 | 8 | 11.9853 | 4 | 5.9927 | 6 | 8.989 | 10 | 14.9816
| i) | Control Cables | Km | 1.1211 | 55 | 61.6591 | 45 | 50.4484 | 110 | 123.3182 | 12 | 13.4529 | 10 | 11.2107 | 16 | 17.9372 | 10 | 11.2107 | 5 | 5.6054 | 8 | 8.9686 | 10 | 11.2107 | 8 | 8.9686 | 4 | 4.4843 | 6 | 6.7264 | 8 | 8.9686
| j) | Earth mat - 40mm dia MS rods | Km | 4.9671 | 50 | 248.3562 | 46 | 228.4877 | 60 | 298.0275 | 10 | 49.6712 | 10 | 49.6712 | 15 | 74.5069 | 10 | 49.6712 |  |  | 8 | 39.737 | 8 | 39.737 | 8 | 39.737 |  |  |  |  | 7.5 | 37.2534
| k) | Diesel Generator set along with AMF panel 250 kVA | Set | 34.4451 | 1 | 34.4451 | 1 | 34.4451 | 1 | 34.4451
| l) | A/C and ventilation - High Valve Type split AC unit of 2TR capacity | No | 0.47721 | 19 | 9.0669 | 19 | 9.0669 | 19 | 9.0669
| m) | Fire fighting system(Lumpsum) | Set | 200 | 1 | 200 | 0.85 | 170 | 1.2 | 240 | 0.05 | 10 |  |  | 0.05 | 10 | 0.05 | 10 | 0.05 | 10 | 0.05 | 10 |  |  | 0.05 | 10 | 0.05 | 10 |  |  | 0.05 | 10
| n) | Illumination System - Indoor and Outdoor(Lumpsum) | Set | 96.627 | 1 | 96.627 | 0.91 | 87.9306 | 1 | 96.627 | [9 empty] | 0
| o) | Mandatory spares | No | 330.0723 | 1 | 330.0723 | 0.85 | 280.5615 | 1.2 | 396.0868
| p) | PLCC Equipments (Total for the Sub - Station) | Set | 135.9263 | 1 | 135.9263 | 0.75 | 101.9447 | 1.4 | 190.2968 | 0.2 | 27.1853 | 0.2 | 27.1853 | [6 empty] | 0.2 | 27.1853 | 0.2 | 27.1853
|  | Sub Total -1-B |  |  |  | 1605.6265 |  | 1412.3768 |  | 1964.2353 |  | 143.2874 |  | 128.0489 |  | 163.9147 |  | 110.8636 |  | 23.0962 |  | 122.8762 |  | 118.1146 |  | 95.6909 |  | 20.477 |  | 15.7154 | 25.8 | 133.7037
| 1-C | Erection,Testing & Commissioning of Common Equipments
| a) | Auxiliary Transformers, LT Switchgear, AC & DC Panels. 72.5 kV, 33kV, 11 kV equipments etc | SetSet | 3.3641 | 1 | 3.3641 | 1 | 3.3641 | 1 | 3.3641
| b) | Station D.C Batteries 220 V System | No | 0.27989 | 2 | 0.55979 | 2 | 0.55979 | 2 | 0.55979
| c) | Station D.C Batteries 48 / 50 V System | No | 0.11662 | 2 | 0.23324 | 2 | 0.23324 | 2 | 0.23324
| d) | Battery Charger for 220 V DC Battery System | No | 0.22427 | 2 | 0.44855 | 2 | 0.44855 | 2 | 0.44855
| e) | Battery Charger for 48 / 50 V DC Battery System | No | 0.16821 | 2 | 0.33641 | 2 | 0.33641 | 2 | 0.33641
| f) | Sub-Station Automation including Hardware, software, Remote Control Station, DMT scheme, Time Synchronising equipment, A/C kiosks etc., | Set | 11.2137 | 1 | 11.2137 | 0.9 | 10.0923 | 1.4 | 15.6991 | 0.1 | 1.1214 | 0.1 | 1.1214 | 0.15 | 1.6821 | 0.1 | 1.1214 |  |  | 0.1 | 1.1214 | 0.1 | 1.1214 | 0.1 | 1.1214 |  |  | 0.05 | 0.56068 | 0.25 | 2.8034
| g) | Visual Monitoring System | Set | 3.3641 | 1 | 3.3641 | 1 | 3.3641 | 1 | 3.3641
| h) | Power cables | KM | 0.22427 | 62 | 13.905 | 53 | 11.8865 | 124 | 27.8099 | 0.2 | 0.044855 | 0.2 | 0.044855 | 0.25 | 0.056068 | 0.2 | 0.044855 | 0.1 | 0.022427 | 0.1 | 0.022427 | 0.1 | 0.022427 | 0.1 | 0.022427 | 0.06 | 0.013456 | 0.1 | 0.022427 | 10 | 2.2427
| i) | Control cables | Set | 0.22427 | 55 | 12.335 | 46.75 | 10.4848 | 120 | 26.9128 |  |  | 0.2 | 0.044855 | 0.24 | 0.053826 | 0.2 | 0.044855 | 0.1 | 0.022427 | 0.1 | 0.022427 | 0.1 | 0.022427 | 0.1 | 0.022427 | 0.06 | 0.013456 | 0.1 | 0.022427 | 8 | 1.7942
| j) | Earth mat formation | Set | 16.8205 | 1 | 16.8205 | 0.9 | 15.1385 | 1.2 | 20.1846 | 0.2 | 3.3641 |  |  | 15 | 252.3077 | 0.2 | 3.3641 |  |  | 0.9 | 15.1385 | 0.9 | 15.1385 | 0.9 | 15.1385 |  |  |  |  | 7.5 | 126.1538
| k) | Diesel Generator set with AMF panel 250 kVA | No | 1.1214 | 1 | 1.1214 | 1 | 1.1214 | 1 | 1.1214 |  | 0
| l) | Air Conditioning and Ventilation | Set | 1.1214 | 19 | 21.306 | 19 | 21.306 | 19 | 21.306
| m) | Fire Fighting System | Set | 26.9128 | 1 | 26.9128 | 0.85 | 22.8759 | 1.2 | 32.2954 | 0.15 | 4.0369 |  |  | 0.15 | 4.0369 | 0.05 | 1.3456 |  | 0 | 0.05 | 1.3456 |  |  | 0.05 | 1.3456 | 0.05 | 1.3456 |  |  | 0.05 | 1.3456
| n) | Illumination System - Indoor & outdoor | Set | 11.2137 | 1 | 11.2137 | 1 | 11.2137 | 1 | 11.2137
| o) | PLCC Equipments (Total for the Sub - Station) | Set | 2.2427 | 1 | 2.2427 | 0.75 | 1.6821 | 1.6 | 3.5884 | 0.2 | 0.44855 | 0.2 | 0.44855 | [6 empty] | 0.2 | 0.44855 | 0.2 | 0.44855
|  | Sub Total -1-C |  |  |  | 125.3769 |  | 114.1072 |  | 168.4375 |  | 9.0158 |  | 1.6596 |  | 258.1365 |  | 5.9208 |  | 0.044855 |  | 18.0989 |  | 16.7532 |  | 17.6503 |  | 1.3726 |  | 0.60554 |  | 134.3398
|  | Total -1 (1-A+1-B+1-C) |  |  |  | 2503.9114 |  | 2271.3769 |  | 2889.9449 |  | 158.5575 |  | 135.9628 |  | 431.4327 |  | 123.0388 |  | 27.8318 |  | 147.2294 |  | 141.1222 |  | 119.5956 |  | 24.9767 |  | 21.0117 |  | 277.425
| 2 | ICTs
| a) | 500 MVA, 765/400/33 KV, S-Phase, Auto Transformer | No | 2017.1991 | 10 | 20171.9914 | 7 | 14120.394 | 7 | 14120.394 |  | 0 |  |  | 3 | 6051.5974
| b) | 315 MVA, 400/220/33 KV, 3-Phase, Auto Transformer | No | 951.5373 | 2 | 1903.0747 | 0 | 0 | 2 | 1903.0747 | [20 empty] | 1 | 951.5373
| c) | I.C.T 167 MVA, S-Phase, 400/220/33 kV ( Single Ph. 167 MVA Units) | No | 488.9265
| d) | Erection,Testing & Commng -765KV S Phase Transformer | No | 11.2137 | 10 | 112.1367 | 7 | 78.4957 | 7 | 78.4957 |  |  |  |  | 3 | 33.641
| e) | Erection,Testing & Commng-400/220KV 3 Phase Transformer | No | 6.7282 | 2 | 13.4564 | 2 | 13.4564 | 2 | 13.4564
| f) | Erection, Testng & Commng-400/220KV S Ph. Transformer | No | 6.7282 | [26 empty] | 1 | 6.7282
| g) | Foundation - 765KV S Phase Transformer | No | 20.8478 | 10 | 208.4778 | 7 | 145.9345 | 7 | 145.9345 |  |  |  |  | 3 | 62.5433
| h) | Foundation - 400/220 KV 3 Phase Transformer | No | 15.6358 | 2 | 31.2717 | 0 | 0 | 2 | 31.2717 | [20 empty] | 1 | 15.6358
| i) | Foundation - 400/220 KV S Phase Transformer | No | 15.6358
| j) | Fire wall between the Transformers | No | 2.0848 | 7 | 14.5934 | 4 | 8.3391 | 4 | 8.3391 |  |  |  |  | 2 | 4.1696
|  | Total : 2 |  |  |  | 22455.0021 |  | 14366.6197 |  | 16300.966 |  | 0 |  | 0 |  | 6151.9513 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 973.9014
| 3 | REACTORs
| 3A | Shunt Reactor
| a) | 765KV, 110MVAR, S-Phase Shunt Reactor | No
| b) | 765KV, 80MVAR, S-Phase Shunt Reactor | No | 472.8656 | 7 | 3310.0593 | 4 | 1891.4624 | 7 | 3310.0593 | 3 | 1418.5968 | [6 empty] | 3 | 1418.5968
| c) | NGR for 765kv Shunt Reactor | No | 82.0278 | 2 | 164.0556 | 1 | 82.0278 | 2 | 164.0556 | 1 | 82.0278 | [6 empty] | 1 | 82.0278
| d) | Surge Arrestor for NGR - 765KV System | No | 1.19 | 2 | 2.38 | 1 | 1.19 | 2 | 2.38 | 1 | 1.19
| e) | 420KV, 80MVAR, 3-Phase Shunt Reactor | No | 366.8289 | 2 | 733.6578 | 1 | 366.8289 | 1 | 366.8289 | [10 empty] | 1 | 366.8289 |  |  |  |  | 1 | 366.8289
| f) | 420KV, 63/50MVAR, 3-Phase Shunt Reactor | No | 318.0349
| g) | NGR for 400kv Shunt Reactor | No | 19.4159 | 2 | 38.8318 | 1 | 19.4159 | 1 | 19.4159 | [10 empty] | 1 | 19.4159 |  |  |  |  | 1 | 19.4159
| h) | Surge Arrestor for NGR - 400KV System | No | 1.2752 | 2 | 2.5505 | 1 | 1.2752 | 1 | 1.2752 | [16 empty] | 1 | 1.2752
| i) | Erection, Testng & Commng - 765KV Shunt Reactor | No | 4.4855 | 7 | 31.3983 | 4 | 17.9419 | 7 | 31.3983 | 3 | 13.4564 | [6 empty] | 3 | 13.4564
| j) | Erection, Testng & Commng - NGR & SA of 765KV Shunt Reactor | Set | 4.4855 | 2 | 8.9709 | 1 | 4.4855 | 2 | 8.9709 | 1 | 4.4855 | [6 empty] | 1 | 4.4855
| k) | Erection, Testng & Commng - 400KV Reactor with NGR & SA | Set | 1.1214 | 2 | 2.2427 | 1 | 1.1214 | 1 | 1.1214 | [10 empty] | 1 | 1.1214 |  |  |  |  | 1 | 1.1214
| l) | Foundation for 765KV Shunt Reactor | No | 10.4239 | 7 | 72.9672 | 4 | 41.6956 | 7 | 72.9672 | 3 | 31.2717 | [6 empty] | 3 | 31.2717
| m) | Foundation for NGR & SA of 765KV System | No | 3.1272 | 2 | 6.2543 | 1 | 3.1272 | 2 | 6.2543 | 1 | 3.1272 | [6 empty] | 1 | 3.1272
| n) | Foundation for 400KV Reactor with NGR & SA | No | 10.4239 | 2 | 20.8478 | 1 | 10.4239 | 1 | 10.4239 | [10 empty] | 1 | 10.4239 |  |  |  |  | 1 | 10.4239
| o) | Fire wall between the Shunt Reactors | No | 1.0424 | 4 | 4.1696 | 2 | 2.0848 | 4 | 4.1696 | 2 | 2.0848 | [6 empty] | 2 | 2.0848
|  | Sub-Total : 3A |  |  |  | 4398.3858 |  | 2443.0804 |  | 3999.3205 |  | 1556.2401 |  | 0 |  | 0 |  | 0 |  | 1555.0501 |  | 397.7901 |  | 0 |  | 0 |  | 399.0653 |  | 0 | 0 | 0
| 3B | Bus Reactor
| a) | 765KV, 110MVAR, S-Phase Bus Reactor | Set
| b) | 765KV, 80MVAR, S-Phase Bus Reactor | Set | 472.8656 | 3 | 1418.5968 | 3 | 1418.5968 | 3 | 1418.5968 | [6 empty] | 3 | 1418.5968
| c) | 420KV, 125MVAR, 3-Phase Bus Reactor | Set | 366.8289 |  |  |  |  | 2 | 733.6578 | [14 empty] | 1 | 366.8289
| d) | 420KV, 80MVAR, 3-Phase Bus Reactor | Set | 360.3907 |  |  | 1 | 360.3907
| e) | 420KV, 63/50MVAR, 3-Phase Bus Reactor | Set | 318.0349
| f) | Erection, Testng & Commng - 765KV, S Phase Bus Reactor | Set | 4.4855 | 3 | 13.4564 | 3 | 13.4564 | 3 | 13.4564 | [6 empty] | 3 | 13.4564
| g) | Erection, Testng & Commng - 400KV 3 Phase Bus Reactor | Set | 4.4855 |  |  | 1 | 4.4855 | 2 | 8.9709 | [14 empty] | 1 | 4.4855
| h) | Foundation for 765KV S Phase Bus Reactor | Set | 10.4239 | 3 | 31.2717 | 3 | 31.2717 | 3 | 31.2717 | [6 empty] | 3 | 31.2717
| i) | Foundation for 400KV 3 Phase Bus Reactor | Set | 10.4239 |  |  | 1 | 10.4239 | 2 | 20.8478
| j) | Fire wall between the Bus Reactors | No | 1.0424 | 2 | 2.0848 | 2 | 2.0848 | 4 | 4.1696 | [6 empty] | 2 | 2.0848
|  | Sub-Total : 3B |  |  |  | 1465.4097 |  | 1840.7098 |  | 2230.9709 |  | 0 |  | 0 |  | 0 |  | 1465.4097 |  | 0 |  | 0 |  | 0 |  | 371.3143 |  | 0 |  | 0 | 0 | 0
|  | Total : 3 - (3A+3B) |  |  |  | 5863.7955 |  | 4283.7902 |  | 6230.2915 |  | 1556.2401 |  | 0 |  | 0 |  | 1465.4097 |  | 1555.0501 |  | 397.7901 |  | 0 |  | 371.3143 |  | 399.0653 |  | 0 | 0 | 0
| 4 | 765KV Bays & Equipments
| 4-A | 765KV Equipments
| a) | 765 KV,3150KA,40KA Circuit Breakers with CR | No | 217.8318 | 4 | 871.3274 | 4 | 871.3274 | 8 | 1742.6547 | 2 | 435.6637 | 2 | 435.6637 | 2 | 435.6637
| b) | 765 KV,3150KA,40KA Circuit Breakers without CR | No | 171.1422 | 5 | 855.7108 | 4 | 684.5687 | 3 | 513.4265 | [6 empty] | 2 | 342.2843
| c) | 765 KV CTs 3000A, 40KA, 5-Core, | No | 33.6085 | 27 | 907.4291 | 24 | 806.6036 | 33 | 1109.08 | 6 | 201.6509 | 6 | 201.6509 | 3 | 100.8255 | 6 | 201.6509
| d) | 765 KV CVT 4400 PF | No | 18.3023 | 12 | 219.6276 | 12 | 219.6276 | 18 | 329.4415 | 3 | 54.9069 | 3 | 54.9069
| e) | 765 KV,3150 A,40 kA Isolators 3-Phase with 1 E/S | No | 32.9605 | 14 | 461.4475 | 13 | 428.4869 | 19 | 626.2501 | 5 | 164.8027 | 4 | 131.8421 | 3 | 98.8816 | 3 | 98.8816
| f) | 765 KV,3150 A,40 kA Isolators 3-Phase with 2 E/S | No | 39.8505 | 6 | 239.1031 | 5 | 199.2526 | 7 | 278.9537 | 1 | 39.8505 | 1 | 39.8505 | 1 | 39.8505 | 1 | 39.8505
| g) | 765 KV, 2000A, 40KA, S-Phase Isolator with 1 E/S | No | 10.8881 | 20 | 217.7619 | 14 | 152.4333 | 17 | 185.0976 | 3 | 32.6643 |  |  | 3 | 32.6643 | 3 | 32.6643 | 3 | 32.6643
| h) | 624 KV Surge Arrestors | No | 10.9571 | 24 | 262.9702 | 18 | 197.2276 | 27 | 295.8415 | 6 | 65.7425 | 3 | 32.8713 | 3 | 32.8713 | 3 | 32.8713 | 3 | 32.8713
|  | Sub-Total : 4A |  |  |  | 4035.3776 |  | 3559.5278 |  | 5080.7455 |  | 995.2815 |  | 896.7854 |  | 740.7568 |  | 748.2029 |  | 65.5356 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
| 4B | 765KV C&P Panels
| a) | Circuit Breaker panel with Auto Reclose | No | 5.5782 | 4 | 22.3126 | 4 | 22.3126 | 8 | 44.6252 | 2 | 11.1563 | 2 | 11.1563
| b) | Circuit Breaker panel without Auto Reclose | No | 5.4699 | 5 | 27.3497 | 4 | 21.8798 | 3 | 16.4098 |  |  |  | 0 | 2 | 10.9399 | 2 | 10.9399
| c) | Line protection panel | No | 26.3255 | 2 | 52.6511 | 2 | 52.6511 | 4 | 105.3021 | 1 | 26.3255 | 1 | 26.3255
| d) | 765/400KV Transformer protection panel(both HV and MV) | L/S | 15.2857 | 3 | 45.8571 | 2 | 30.5714 | 2 | 30.5714 |  |  |  |  | 1 | 15.2857
| e) | Reactor protection panel | No | 12.1634 | 3 | 36.4903 | 2 | 24.3268 | 3 | 36.4903 | 1 | 12.1634 |  | 0 |  |  | 1 | 12.1634 | 1 | 12.1634
| f) | Bus Bar Protection Panel | No | 65.17 | 1 | 65.17 | 1 | 65.17 | 1 | 65.17
|  | Sub-Total : 4B |  |  |  | 249.8307 |  | 194.599 |  | 253.9436 |  | 38.489 |  | 26.3255 |  | 26.2256 |  | 23.1033 |  | 12.1634 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
| 4C | Bus bar & Hard ware materials for 765 kV Switchyard
| a) | 4.5" Nominal diametre IPS Aluminium Tube | No | 655.9658 | 1 | 655.9658 | 0.9 | 590.3693 | 1.8 | 1180.7385 | 0.35 | 229.588 | 0.3 | 196.7898 | 0.3 | 23.52 | 0.3 | 196.7898 | 0.2 | 131.1932
| b) | AAC Bull / ACSR Bersimis
| c) | Anti Fog Disc Iinsulator string - 4 Nos with Tension Hardware for Quad AAC Bull / ACSR Bersimis.
| d) | Anti Fog Disc Iinsulator string - 2 Nos with Suspension Hardware for Quad AAC Bull / ACSR Bersimis.
| e) | Anti Fog Disc Iinsulator string -2 Nos with Tension Hardware for Twin AAC Bull / ACSR Bersimis
| f) | Antifog Disc insulator string - 1 No, with suspension Hardware for Twin AAC Bull / ACSR Bersimis
| g) | 765KV Class Bus post insulators
| h) | BPI Clamps for 765KV Class
| i) | Tee Clamps Quad AAC Bull / ACSR Bersimis to Twin AAC Bull
| j) | Tee Clamps Twin AAC Bull / ACSR Bersimis to IPS Al Tube 4.5"Nom. dia
| k) | Tee Clamps Twin AAC Bull / ACSR Bersimis to Twin AAC Bull / ACSR Bersimis
| l) | PG Clamps
| m) | Spacer Clamps for Quad AAC Bull / ACSR Bersimis
| n) | Spacer Clamps for Twin AAC Bull / ACSR Bersimis
| o) | Ground wire with accessories
|  | Sub Total - 4-C |  |  |  | 655.9658 |  | 590.3693 |  | 1180.7385 |  | 229.588 |  | 196.7898 |  | 23.52 |  | 196.7898 |  | 131.1932 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
| 4-D | Erection Testing & commisioning of 765KV Equipments
| a) | 765KV Circuit breakers | No | 1.0429 | 9 | 9.3858 | 8 | 8.343 | 11 | 11.4716 | 2 | 2.0857 | 2 | 2.0857 | 2 | 2.0857 | 2 | 2.0857
| b) | 765KV Isolators | No | 0.97559 | 40 | 39.0236 | 32 | 31.2189 | 43 | 41.9504 | 9 | 8.7803 | 5 | 4.8779 | 7 | 6.8291 | 7 | 6.8291 | 3 | 2.9268
| c) | 765KV Current Transformers | No | 0.56068 | 27 | 15.1385 | 24 | 13.4564 | 33 | 18.5026 | 6 | 3.3641 | 6 | 3.3641 | 3 | 1.6821 | 3 | 1.6821
| d) | 765KV CVT | No | 0.56068 | 12 | 6.7282 | 12 | 6.7282 | 18 | 10.0923 | 3 | 1.6821 | 3 | 1.6821
| e) | 624KV Surge Arrestor | No | 0.28034 | 24 | 6.7282 | 18 | 5.0462 | 27 | 7.5692 | 6 | 1.6821 | 3 | 0.84103 | 3 | 0.84103 | 3 | 0.84103 | 3 | 0.84103
| f) | Bus Bars formation etc. | L/S | 67.282 | 1 | 67.282 | 0.9 | 60.5538 | 1.8 | 121.1077 | 0.35 | 23.5487 | 0.3 | 20.1846 | 0.3 | 20.1846 | 0.3 | 20.1846 | 0.2 | 13.4564
|  | Control & Protection panels | [7 empty] | 0 |  | 0
| g) | 765KV CB relay Panel with Auto Reclosure | No | 0.22427 | 4 | 0.89709 | 4 | 0.89709 | 8 | 1.7942 | 2 | 0.44855 | 2 | 0.44855
| h) | 765KV CB relay Panel without Auto Reclosure | No | 0.22427 | 2 | 0.44855 | 4 | 0.89709 | 3 | 0.67282 |  | 0 |  |  | 2 | 0.44855 | 2 | 0.44855
| i) | 765KV Line Protection Panel | No | 0.22427 | 2 | 0.44855 | 2 | 0.44855 | 4 | 0.89709 | 1 | 0.22427 |  |  |  | 0
| j) | 765-400/33KV Transformer Protection Panel | No | 0.22427 | 1 | 0.22427 | 2 | 0.44855 | 2 | 0.44855 |  | 0 |  |  | 1 | 0.22427
| k) | 765KV Reactor Protection Panel | No | 0.22427 | 3 | 0.67282 | 2 | 0.44855 | 3 | 0.67282 |  | 0 |  |  |  |  | 1 | 0.22427 | 1 | 0.22427
| l) | Duplicate Bus Bar Protection Panel - 765KV | No | 0.89709 | 1 | 0.89709 | 1 | 0.89709 | 1 | 0.89709 |  | 0
|  | Sub Total - 4-D |  |  |  | 147.8747 |  | 129.3834 |  | 216.0763 |  | 41.8158 |  | 33.484 |  | 32.2954 |  | 32.2954 |  | 17.4485 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
|  | Total - 4 (4A+4B+4C+4D) |  |  |  | 5089.0488 |  | 4473.8795 |  | 6731.5039 |  | 1305.1743 |  | 1153.3847 |  | 822.7978 |  | 1000.3914 |  | 226.3406 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
| 5 | 400 kV Bays & Equipments
| 5A | 400KV Equipments
| a) | 420 kV, 3150A, 40KA Breakers with CR | No | 39.8848 | 8 | 319.0788 | 3 | 119.6545 | 13 | 518.503 |  | 0 | [8 empty] | 2 | 79.7697 | 2 | 79.7697
| b) | 420 kV, 3150A, 40KA Breakers without CR | No | 31.2274 | 7 | 218.5918 | 6 | 187.3644 | 8 | 249.8192 |  | 0 |  |  | 2 | 62.4548 | [8 empty] | 2 | 62.4548 |  |  |  |  | 2 | 62.4548
| c) | 420 kV, 3000A, 40 kA, 5 Core CT with 120% current rating, | No | 11.7655 | 45 | 529.4454 | 30 | 352.9636 | 72 | 847.1127 |  | 0 |  |  | 3 | 35.2964 |  |  |  |  | 3 | 35.2964 | 3 | 35.2964 | 3 | 35.2964 |  |  |  |  | 3 | 35.2964
| d) | 420 kV CVT 4400 PF | No | 5.0281 | 6 | 30.1688 | 6 | 30.1688 | 6 | 30.1688 |  | 0 | [19 empty] | 0
| d) | 420 kV CVT 8800 PF | No | 5.7418 | 12 | 68.9018 | 6 | 34.4509 | 24 | 137.8037 |  | 0 | [8 empty] | 3 | 17.2255 | 3 | 17.2255 | [7 empty] | 0
| f) | 420 kV,2000 A,40 kA DB Isolators 3-Phase with 1 E/S | No | 9.1207 | 32 | 291.8626 | 18 | 164.1727 | 45 | 410.4318 |  | 0 |  |  | 3 | 27.3621 |  |  |  |  | 4 | 36.4828 | 3 | 27.3621 | 4 | 36.4828 | 1 | 9.1207 |  |  | 5 | 45.6035
| g) | 420 kV,3150A,40 kA Isolators 3-Phase with 1 E/S | No | 6.7981 | 4 | 27.1925 | 2 | 13.5962 | 8 | 54.3849 |  | 0 | [8 empty] | 1 | 6.7981 | 1 | 6.7981 | [7 empty] | 0
| h) | 420 kV,3150A,40 kA Isolators 3-Phase with 2 E/S | No | 6.7981 | 2 | 13.5962 | 2 | 13.5962 | 2 | 13.5962 |  | 0 |  |  | 1 | 6.7981 |  |  |  |  | 1 | 6.7981 | 1 | 6.7981 | 1 | 6.7981 | [5 empty] | 0
| i) | 420 kV, 3150 A,40 kA DB Isolators S-Phase with 1 E/S | No | 3.632 | 10 | 36.3201 | 7 | 25.4241 | 7 | 25.4241 |  | 0 |  |  | 3 | 10.896 | [8 empty] | 3 | 10.896 | [5 empty] | 0
| k) | 390 kV Surge Arrestors | No | 1.6739 | 33 | 55.2402 | 18 | 30.131 | 45 | 75.3276 |  | 0 | [8 empty] | 6 | 10.0437 | 3 | 5.0218 |  |  | 3 | 5.0218 |  |  | 3 | 5.0218
|  | Sub-Total : 5A |  |  |  | 1590.3983 |  | 971.5226 |  | 2362.572 |  | 0 |  | 0 |  | 142.8074 |  | 0 |  | 0 |  | 192.4143 |  | 178.2717 |  | 151.9281 |  | 14.1425 |  | 0 | 13 | 148.3765
| 5B | 400KV C & P Panels
| a) | Circuit Breaker panel with Auto Reclose | No | 5.5757 | 8 | 44.6052 | 3 | 16.727 | 13 | 72.4835 | [10 empty] | 2 | 11.1513 | 2
| b) | Circuit Breaker panel without Auto Reclose | No | 4.8429 | 7 | 33.9002 | 6 | 29.0573 | 8 | 38.743 |  |  |  |  | 2 | 9.6858 | [8 empty] | 2 | 9.6858 |  |  |  |  | 2 | 9.6858
| c) | Line protection panel | No | 21.284 | 4 | 85.136 | 2 | 42.568 | 6 | 127.704 | [10 empty] | 1 | 21.284 | 1 | [8 empty] | 0
| d) | 400/220KV Transformer protection panel (both400 & 220 kV) | No | 18.8276 | 2 | 37.6552 | 2 | 37.6552 | 2 | 37.6552 |  |  |  |  | 1 | 18.8276 | [14 empty] | 1 | 18.8276
| e) | Reactor protection panel | No | 10.7155 | 2 | 21.431 | 1 | 10.7155 | 3 | 32.1464 | [10 empty] | 1 | 10.7155 |  |  | 1 | 10.7155 | 1 | 10.7155
| f) | Double Bus Bar protection panel | No | 82.8774 | 1 | 82.8774 | 1 | 82.8774 | 1 | 82.8774
|  | Sub-Total : 5B |  |  |  | 305.6049 |  | 219.6003 |  | 391.6096 |  | 0 |  | 0 |  | 28.5134 |  | 0 |  | 0 |  | 43.1508 |  | 0 |  | 20.4012 |  | 10.7155 |  | 0 | 3 | 28.5134
| 5-C | Bus Bar & Hard ware materials for 400 kV
| a) | 4.5" Nominal dia IPS Alluminium Tube | Metre | 361.487 | 1 | 361.487 | 0.8 | 289.1896 | 2 | 722.974 |  |  |  |  | 0.25 | 90.3717 |  |  |  |  | 0.25 | 90.3717 | 0.28 | 101.2164 | 0.25 | 90.3717 | 0.1 | 36.1487 |  |  | 0.3 | 108.4461
| b) | 4" Nominal dia IPS Alluminium Tube | Metre
| c) | Moose ACSR | Metre
| e) | Anti Fog Type Disc Iinsulator string - 2 Nos with Tension Hardware for Twin Moose | Set
| f) | Anti Fog Type Disc Iinsulator string - 1 No with suspension Hardware for Twin Moose | Set
| g) | 400 KV Class Bus post insulators | No
| h) | BPI Clamps | No
| i) | Tee Clamps Twin Moose to Twin Moose | No
| j) | Tee Clamps Twin Moose to IPS Al Tube 4.5"dia | No
| k) | Tee Clamps Twin Moose to IPS Al Tube 4" dia | No
| l) | PG Clamps
| m) | Spacer Clamps for Twin Moose ACSR
| n) | Ground wire with Accessories | L/S
|  | Sub Total - 5-C |  |  |  | 361.487 |  | 289.1896 |  | 722.974 |  | 0 |  | 0 |  | 90.3717 |  | 0 |  | 0 |  | 90.3717 |  | 101.2164 |  | 90.3717 |  | 36.1487 |  | 0 | 0.3 | 108.4461
| 5-D | Erection Testing & commisioning of 400 kV Equipments
| a) | 420 KV Circuit breakers | No | 0.33641 | 15 | 5.0462 | 9 | 3.0277 | 21 | 7.0646 |  |  |  |  | 2 | 0.67282 |  |  |  |  | 2 | 0.67282 | 2 | 0.67282 | 2 | 0.67282 |  |  |  |  | 2 | 0.67282
| b) | 420KV Isolators | No | 0.22427 | 48 | 10.7651 | 29 | 6.5039 | 62 | 13.905 |  |  |  |  | 7 | 1.5699 |  |  |  |  | 6 | 1.3456 | 5 | 1.1214 | 5 | 1.1214 | 1 | 0.22427 |  |  | 5 | 1.1214
| c) | 420 KV Current Transformers | No | 0.067282 | 45 | 3.0277 | 30 | 2.0185 | 72 | 4.8443 |  |  |  |  | 3 | 0.20185 |  |  |  |  | 6 | 0.40369 | 6 | 0.40369 | 6 | 0.40369 |  |  |  |  | 3 | 0.20185
| e) | 420KV CVT | No | 0.067282 | 18 | 1.2111 | 12 | 0.80738 | 30 | 2.0185 | [10 empty] | 3 | 0.20185 | 3 | 0.20185
| f) | 390KV surge Arrestors | No | 0.033641 | 33 | 1.1102 | 18 | 0.60554 | 45 | 1.5138 |  |  |  |  | 3 | 0.10092 |  |  |  |  | 6 | 0.20185 | 3 | 0.10092 | 3 | 0.10092 | 3 | 0.10092 |  |  | 3 | 0.10092
| g) | Bus Bars formation etc | L/S | 33.641 | 1 | 33.641 | 1 | 33.641 | 2 | 67.282 | [10 empty] | 0.25 | 8.4103 | 0.28 | 9.4195 | 0.25 | 8.4103 | 0.1 | 3.3641 |  |  | 0.3 | 10.0923
|  | C & P panels | [7 empty] | 0
| h) | 400KV CB relay Panel with Reclosure | No | 0.33641 | 8 | 2.6913 | 3 | 1.0092 | 13 | 4.3733 | [10 empty] | 2 | 0.67282 | 2 | 0.67282
| i) | 400KV CB relay Panel without Auto Reclosure | No | 1.0092 | 7 | 7.0646 | 6 | 6.0554 | 8 | 8.0738 |  |  |  |  | 2 | 2.0185 | [8 empty] | 2 | 2.0185 |  |  |  |  | 2 | 2.0185
| j) | 400KV Line Protection Panel | No | 0.61285 | 4 | 2.4514 | 2 | 1.2257 | 8 | 4.9028 | [10 empty] | 1 | 0.61285 | 1 | 0.61285 | [7 empty] | 0
| k) | 400-220/33KV Transformer Protection Panel | No | 0.10717 | 2 | 0.21433 | 2 | 0.21433 | 2 | 0.21433 | [20 empty] | 1 | 0.10717
| l) | 400KV Reactor Protection Panel | No | 1.7924 | 4 | 7.1697 | 1 | 1.7924 | 3 | 5.3772 | [10 empty] | 1 | 1.7924 |  | 0 | 1 | 1.7924 | 1 | 1.7924
| m) | 400KV Bus Bar Protection panelPanel | No | 1.4017 | 1 | 1.4017 | 1 | 1.4017 | 1 | 1.4017
|  | Sub Total - 5-D |  |  |  | 75.7942 |  | 58.3028 |  | 120.9715 |  | 0 |  | 0 |  | 4.564 |  | 0 |  | 0 |  | 14.3142 |  | 13.2058 |  | 14.5199 |  | 5.4817 |  | 0 |  | 14.3149
|  | Total - 5 (5A+5B+5C+5D) |  |  |  | 2333.2845 |  | 1538.6153 |  | 3598.1271 |  | 0 |  | 0 |  | 266.2565 |  | 0 |  | 0 |  | 340.251 |  | 292.6939 |  | 277.2211 |  | 66.4884 |  | 0 |  | 299.6509
| 6 | 220 kV Bays & Equipments
| 6-A | 245 kV equipments
| a) | 245KV Circuit Breakers, 1600A, 40KA | No | 17.2017 | 7 | 120.4121 |  |  | 7 | 120.4121 | [18 empty] | 1 | 17.2017 | 1 | 17.2017
| b) | 245KV Circuit Breakers, 2500A, 40KA | No | 17.2017 | 1 | 17.2017 |  |  | 1 | 17.2017 | [21 empty] | 0
| c) | 245KV CT,1600 A, 40 kA , 5 core, with 120% extended current | No | 3.8963 | 21 | 81.8227 |  |  | 21 | 81.8227 | [18 empty] | 3 | 11.689 | 3 | 11.689
| e) | 245KV CT,1600 A, 40 kA , 5 core, with 150% extended current | No | 4.2012 | 3 | 12.6035 |  |  | 3 | 12.6035 | [21 empty] | 0
| f) | 245 Kv CVT 8800pF, | No | 3.5738 | 12 | 42.8854 |  |  | 12 | 42.8854 | [18 empty] | 3 | 10.7214 |  | 0
| g) | 245 Kv CVT 4400pF, | No | 3.5738 | 6 | 21.4427 |  |  | 6 | 21.4427 | [21 empty] | 0
| h) | 1600A, 40 kA, DB Type Isolator, 3 Phase with two E/S | No | 4.0854 | 7 | 28.5979 |  |  | 7 | 28.5979 | [18 empty] | 1 | 4.0854 | 1 | 4.0854
| i) | 1600A, 40 kA, DB Type Isolator, 3 Phase with one E/S | No | 3.3404 | 7 | 23.3825 |  |  | 7 | 23.3825 | [18 empty] | 1 | 3.3404 | 1 | 3.3404
| j) | 1600A, 40 kA, DB, Tandem Type Isolator, 3Phase without E/S | No | 2.8188 | 13 | 36.6438 |  |  | 13 | 36.6438 | [18 empty] | 2 | 5.6375 | 2 | 5.6375
| k) | 2500A, 40 K, DB Type Isolator, 3Phase with Two E/S | No | 4.5043 | 2 | 9.0087 |  |  | 2 | 9.0087 | [21 empty] | 0
| l) | 1600A, 40 kA, DB Type Isolator, S Phase with E/S |  |  | 0 | 0 |  |  |  | 0 | [21 empty] | 0
| m) | 216 kV Surge Arrestors | No | 0.39215 | 18 | 7.0587 |  |  | 18 | 7.0587 | [18 empty] | 3 | 1.1764 | 3 | 1.1764
|  | Sub Total - 6-A |  |  |  | 401.0598 |  | 0 |  | 401.0598 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 53.8518 |  | 43.1304
| 6-B | 220KV C & P Panels
| b | Circuit breaker relay panel With Auto reclosure | No | 8.12 | 4 | 32.48 |  |  | 4 | 32.48 | [18 empty] | 1 | 8.12
| c) | Circuit breaker relay panel Without Auto reclosure | No | 6.45 | 4 | 25.8 |  |  | 4 | 25.8 | [20 empty] | 1 | 6.45
| d) | Line protection panel | No | 18.18 | 4 | 72.72 |  |  | 4 | 72.72 | [18 empty] | 1 | 18.18
| e) | Single Bus Bar protection panel | No | 63.3948 | 1 | 63.3948 |  |  | 1 | 63.3948
|  | Sub Total - 6-B |  |  |  | 194.3948 |  | 0 |  | 194.3948 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 26.3 | 1 | 6.45
| 6-C | Bus Bar & Hard ware materials for 220 kV
| a) | Disc Iinsulator string - 4Nos; with Tension Hardware for Quad Moose (220KV Main Bus &220KV Bus Coupler)) | Set | 130.1172 | 1 | 130.1172 |  |  | 1.4 | 182.1641 | [18 empty] | 0.2 | 26.0234 | 0.25 | 32.5293
| b) | Disc Iinsulator string - 2Nos; with Suspension Hardware for Quad Moose (220KV Main Bus &220KV Bus Coupler)) | Set
| c) | Disc Iinsulator string - 2Nos, with Tension Hardware for Twin Moose (220KV Transfer Bus and Jack Bus exceptfor Bus Coupler)) | Set
| d) | Disc Iinsulator string - 2Nos, with Suspension Hardware for Twin Moose (220KV Transfer Bus and Jack Bus exceptfor Bus Coupler)) | Set
| e) | 220KV Bus post I nsulators | No
| f) | 4" EH-IPS Alluminium Tube(OD- 114.2, ID-97.18) | Metre
| g) | Moose ACSR | Metre
| h) | Tee Clamps Quad Moose to Twin Moose | No
| i) | Tee Clamps Twin Moose to Twin Moose - 220kv side | No
| j) | Tee Clamps Twin Moose to 4' IPS Al Tube - 220kv side | No
| k) | Spacer Clamps for Quad Moose ACSR | No
| l | Spacer Clamps for Twin Moose ACSR | No
| j) | PG Clamps | No
| k) | Ground wire with Accessories | Lump Sum
|  | Sub Total - 6-C |  |  |  | 130.1172 |  | 0 |  | 182.1641 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 26.0234 |  | 32.5293
| 6-D | Erection,Testing & commissioning of 220 kV Equipments
| a) | 245 KV Circuit breakers | No | 0.22427 | 8 | 1.7942 |  |  | 8 | 1.7942 | [18 empty] | 1 | 0.22427 | 1 | 0.22427
| b) | 245 KV Isolators | No | 0.16821 | 29 | 4.8779 |  |  | 29 | 4.8779 | [18 empty] | 4 | 0.67282 | 4 | 0.67282
| c) | 245 KV Current Transformers | No | 0.056068 | 24 | 1.3456 |  |  | 24 | 1.3456 | [18 empty] | 3 | 0.16821 | 3 | 0.16821
| e) | 245 KV CVT | No | 0.056068 | 18 | 1.0092 |  |  | 18 | 1.0092 | [18 empty] | 3 | 0.16821 |  | 0
| f) | 216 KV surge Arrestors | No | 0.033641 | 18 | 0.60554 |  |  | 18 | 0.60554 | [18 empty] | 3 | 0.10092 | 3 | 0.10092
| g) | 220 kV Bus Bars formation etc | Set | 16.8205 | 1 | 16.8205 |  |  | 1 | 16.8205 | [18 empty] | 0.2 | 3.3641 |  | 0
|  | 220KV C & P Panels |  | 0 | [5 empty] | 0 | [21 empty] | 0
| i) | Circuit breaker relay panel | No | 0.28034 | 4 | 1.1214 |  |  | 8 | 2.2427 | [20 empty] | 1 | 0.28034
| j) | Line protection panel | No | 0.7401 | 4 | 2.9604 |  |  | 4 | 2.9604 | [18 empty] | 1 | 0.7401 |  | 0
| k) | Single Bus Bar protection panel | No | 2.2427 | 1 | 2.2427 |  |  | 1 | 2.2427
|  | Sub Total - 6-D |  |  |  | 32.7776 |  | 0 |  | 33.8989 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 5.4386 |  | 1.4466
|  | Total - 6 (6A+6B+6C+6D) |  |  |  | 758.3494 |  | 0 |  | 811.5176 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 111.6138 |  | 83.5563
| 7 | Steel Structurals
| 7-A | Lattice Type
| i) | M.S. Steel | MT | 0.68144 | 1100 | 749.5809 | 750 | 511.0779 | 1900 | 1294.7306 | 80 | 54.515 | 80 | 54.515 | 110 | 74.9581 | 72 | 49.0635 | 0 |  | 58 | 39.5234 | 58 | 39.5234 | 49 | 33.3904 |  |  | 15 |  | 113.85 | 77.5816
| ii) | High Tension Steel | MT | 0.90858 | 60 | 54.515 | 50 | 45.4291 | 70 | 63.6008 | [5 empty] | 0 |  |  | 0 | [12 empty] | 0
| iii) | M.S. Tubular Steel | MT | 0.90858 | 150 | 136.2874 | 100 | 90.8583 | 205 | 186.2595 | 15 | 13.6287 | 13 | 11.8116 | 20 | 18.1717 | 15 | 13.6287 | 3 | 2.7257 | 15 | 13.6287 | 17 | 15.4459 | 13 | 11.8116 | 4 | 3.6343 | 8 |  | 26.15 | 23.7594
|  | Sub Total - 7-A |  |  |  | 940.3833 |  | 647.3653 |  | 1544.5909 |  | 68.1437 |  | 66.3265 |  | 93.1297 |  | 62.6922 |  | 2.7257 |  | 53.1521 |  | 54.9693 |  | 45.202 |  | 3.6343 |  | 0 | 140 | 101.3411
| 7-B | Erection of Steel Structures
| a) | Lattice Type | MT | 0.022315 | 1160 | 25.8856 | 800 | 17.8522 | 1970 | 43.961 | 80 | 1.7852 | 80 | 1.7852 | 110 | 2.4547 | 72 | 1.6067 |  |  | 58 | 1.2943 | 58 | 1.2943 | 49 | 1.0934 |  |  | 15 |  | 113.85 | 2.5406
| b) | Tubular Type | MT | 0.025791 | 150 | 3.8687 | 100 | 2.5791 | 205 | 5.2872 | 15 | 0.38687 | 13 | 0.33529 | 20 | 0.51583 | 15 | 0.38687 | 3 | 0.077374 | 15 | 0.38687 | 17 | 0.43845 | 13 | 0.33529 | 4 | 0.10317 | 4 |  | 26.15 | 0.67445
|  | Sub Total - 7B |  |  |  | 29.7544 |  | 20.4313 |  | 49.2482 |  | 2.1721 |  | 2.1205 |  | 2.9705 |  | 1.9936 |  | 0.077374 |  | 1.6812 |  | 1.7327 |  | 1.4287 |  | 0.10317 |  | 0 |  | 3.215
|  | Total -7 (7A+7B) |  |  |  | 970.1376 |  | 667.7966 |  | 1593.8391 |  | 70.3158 |  | 68.4471 |  | 96.1002 |  | 64.6858 |  | 2.8031 |  | 54.8333 |  | 56.702 |  | 46.6307 |  | 3.7375 |  | 0 |  | 104.5561
| 8 | Civil Works
|  | Foundations for Gantries, Equipments (Other than ICTs & Reactors) and Equipment Support Structures (Lumpsum) |  | 1042.3889 | 1 | 1042.3889 | 0.75 | 781.7917 | 1.5 | 1563.5834 | 0.2 | 208.4778 | 0.2 | 208.4778 | 0.3 | 312.7167 | 0.1 | 104.2389 |  | 0 | 0.1 | 104.2389 | 0.1 | 104.2389 | 0.1 | 104.2389 |  | 0 | 0.1 | 104.2389 | 0.1 | 104.2389
|  | Total - 8 |  |  |  | 1042.3889 |  | 781.7917 |  | 1563.5834 |  | 208.4778 |  | 208.4778 |  | 312.7167 |  | 104.2389 |  | 0 |  | 104.2389 |  | 104.2389 |  | 104.2389 |  | 0 |  | 104.2389 |  | 104.2389
|  | Total Hard cost of Sub-station |  |  |  | 41015.9183 |  | 28383.8698 |  | 39719.7735 |  | 3298.7655 |  | 1566.2724 |  | 8081.2552 |  | 2757.7645 |  | 1812.0257 |  | 1044.3425 |  | 594.757 |  | 919.0006 |  | 494.2679 |  | 236.8645 |  | 1843.3285
|  | Total cost of taxable Materials & equipments |  |  | 38370.5751 |  | 26280.671 |  | 36536.4519 |  | 2987.7921 |  | 1318.0563 |  | 7621.9438 |  | 2568.163 |  | 1735.461 |  | 907.9899 |  | 471.0579 |  | 789.502 |  | 474.1138 |  | 122.4962 |  | 1691.5826
| 9 | Taxes and Duties for Jan-09 at ED-10%,cess at 3 on Duty and CST at 2% on cost including ED,Totalling 12.51% |  |  |  | 4800.1589 |  | 3287.7119 |  | 4570.7101 |  | 373.7728 |  | 164.8888 |  | 953.5052 |  | 321.2772 |  | 217.1062 |  | 113.5895 |  | 58.9293 |  | 98.7667 |  | 59.3116 |  | 15.3243 |  | 211.617
| 10 | Total cost of sub-station including Taxes & Duties |  |  |  | 45816.0772 |  | 31671.5817 |  | 44290.4836 |  | 3672.5383 |  | 1731.1613 |  | 9034.7604 |  | 3079.0417 |  | 2029.1319 |  | 1157.9321 |  | 653.6863 |  | 1017.7673 |  | 553.5795 |  | 252.1887 |  | 2054.9455

## Summary
CERC
Capital Cost Benchmarking
Transmission Substations
Alternates
| S.No. | Unit | Alt-1 | Alt-2 | Alt-3
| 1 | INR Crore | 410.1592 | 283.8387 | 397.1977
Combinations
| S.No. | Unit | Combination-1 | Combination-2 | Combination-3 | Combination-4 | Combination-5 | Combination-6 | Combination-7 | Combination-8 | Combination-9 | Combination-10 | Combination-11
|  |  | 765KV Line Ter. Bay with Shunt Reactor | 765KV Line Ter. Bay without Sh. Reactor | 765/400KV Transformer. Bay | 765KV Bus Reactor bay | 765KV Shunt Reactor (Add or Delete) | 400KV Line Ter. Bay with Shunt Reactor | 400KV Line Ter. Bay without Sh. Reactor | 400KV Bus Reactor bay | 400KV Shunt Reactor (Add or Delete) | 220KV Line Ter. bay | 400/220 kV ICT
| 1 | INR Crore | 32.9877 | 15.6627 | 80.8126 | 27.5776 | 18.1203 | 10.4434 | 5.9476 | 9.19 | 4.9427 | 2.3686 | 18.4333