Annexure - III

Details of discussions w.r.t constraints for power transfer from Eastern to North-Eastern Region

- On the ER-NER transfers, the constraints on 400 kV Farakka-Malda D/C was highlighted, particularly during winter.  Re-conductoring this section was under implementation. Even after 400 kV Purnea-Biharsharif D/C was commissioned last Sep 2013, the transfers were from Purnea to Biharsharif direction during winters, which accentuated the loading on 400 kV Farakka-Malda D/C. It was further informed that during last winter, after further studies such as bus splitting at 220 kV Dalkhola and standing instructions for opening of 400 kV Malda-Purnea D/C one by one in case of any overload on the 400 kV Farakka-Malda section, the ER to NER TTC was enhanced from 500-550 MW to 720 MW. However, with Palatana GPS getting commissioned, there was a need for having more TRM of the order of 280 MW as the intra NER system was quite weak to withstand a 363 MW loss at Palatana.