## Annexure-III 1 to 3
Annexure-III
SH 1/3
Pro-forma for furnishing Actual annual performance/operational data for the Hydro Electric generating stations for the 5-year period from 2012-13 to 2016-17
| Particulars |  | Units | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | Name of Company |  |  | NHPC LTD.
2 | Name of Station |  |  | Uri-I Power Station
3 | Installed Capacity and Configuration |  | (MW) | 480
4 | Station Location |  | Under ground or Surface | Under Ground
5 | Type of Excitation System |  |  | Static
6 | Live Storage Capacity |  | (Million Cubic) | -
7 | Rated Head |  | Metres | 222.5 M | 222.5 M | 222.5 M | 222.5 M | 222.5 M
8 | Head at Full Reservoir Level (FRL) |  | Metres | 256.53 M | 256.53 M | 256.53 M | 256.53 M | 256.53 M
9 | Head at Minimum Draw down Level (MDDL) |  | Metres | -
10 | MW Capability at FRL |  | MW | 480 MW | 480 MW | 480 MW | 480 MW | 480 MW
11 | MW Capability at MDDL |  | MW
12 | Cost of spares :
12.1 | Cost of spares capitalized in books of accounts |  | (Rs. Lakhs) | 1183.37 | 187.37 | 839.39 | 164.79 | 284.54
12.2 | Cost of spares included in the capital cost for the purpose of tariff |  | (Rs. Lakhs) | 0 | 0 | 0 | 0 | 0
Period
13 | Generation :
13.1 | Actual Gross Generation at Generator Terminals |  | (MU) | 2966.71 | 2520.78 | 3076.5532 | 3282.972 | 2803.0703
13.2 | Actual Net Generation Ex-bus including free power |  | (MU) | 2964.4897 | 2516.0692 | 3090.0447 | 3303.0824 | 2812.951
13.3 | Scheduled generation Ex-bus including free power |  | (MU) | 2942.5243 | 2512.5764 | 3010.4386 | 3187.3313 | 2730.942
14 | Actual Auxiliary Energy Consumption excluding colony consumption |  | (MU) | 28.8 | 24.62 | 29.9013 | 32.3607 | 28.445
15 | Actual Energy supplied to Colony from the station |  | (MU) | NIL | NIL | NIL | NIL | NIL
16 | Average Declared Capacity (DC) during the year |  | (MW) | 382.85 | 346.23 | 377.12 | 408.84 | 375.11
Annexure-III
SH 2/3
| Period |  | Units | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
17 | Weighted Average duration of outages ( Unit-wise details)
17.1 | Scheduled outages |  | (Days) | 106.141 | 93.4757 | 109.3507 | 94.8958 | 94.9257
17.2 | Forced outages |  | (Days) | 3.2236 | 56.1076 | 7.5931 | 2.3632 | 2.15
18 | Cost of spares actually consumed |  | (Rs. Lakhs) | 21.62 | 179.8 | 159.81 | 117.12 | 35.26 | 7.57 | 679.58 | 47.67 | 249.28
19 | Average stock of spares |  | (Rs. Lakhs) | 999.58 | 1573.45 | 1925.26 | 2320.34 | 2453.18 | 573.87 | 351.81 | 395.08 | 132.84
Month wise Design Energy
Month |  | Period | Design Energy as approved by CEA (MU) |  | Month | Period | Design Energy as approved by CEA (MU)
April |  | 1-10 | 109.44 |  | October | 1-10 | 48.64
|  | 11-20 | 109.44 | 109.44 |  | 11-20 | 37.45 | 37.45
|  | 21-30 | 109.44 | 109.44 |  | 21-31 | 31.6 | 31.6
May |  | 1-10 | 109.44 | 109.44 | November | 1-10 | 25.26 | 25.26
|  | 11-20 | 109.44 | 109.44 |  | 11-20 | 23.68 | 23.68
|  | 21-31 | 120.38 | 120.38 |  | 21-30 | 23.28 | 23.28
June |  | 1-10 | 109.44 | 109.44 | December | 1-10 | 22.59 | 22.59
|  | 11-20 | 109.44 | 109.44 |  | 11-20 | 22.59 | 22.59
|  | 21-30 | 109.44 | 109.44 |  | 21-31 | 26.21 | 26.21
July |  | 1-10 | 109.44 | 109.44 | January | 1-10 | 25.96 | 25.96
|  | 11-20 | 109.44 | 109.44 |  | 11-20 | 24.12 | 24.12
|  | 21-31 | 120.38 | 120.38 |  | 21-31 | 31 | 31
August |  | 1-10 | 109.44 | 109.44 | February | 1-10 | 47.8 | 47.8
|  | 11-20 | 91.84 | 91.84 |  | 11-20 | 46.56 | 46.56
|  | 21-31 | 101.35 | 101.35 |  | 21-28 | 38.73 | 38.73
September |  | 1-10 | 85.55 | 85.55 | March | 1-10 | 62.71 | 62.71
|  | 11-20 | 67.02 | 67.02 |  | 11-20 | 85.4 | 85.4
|  | 21-30 | 56.67 | 56.67 |  | 21-31 | 116.77 | 116.77
[5 empty] | Total |  | 2587.38
Storage Hydro plants shall also furnish actual monthly average peaking generation in MW achieved during the period 2012-13 to 2016-17 against the monthly average peaking capability approved by CEAas per following format:
Month |  | Expected Avg. of daily 3-hour peaking capacity as approved by CEA |  |  | Actual monthly average of daily 3-hour peaking (MW) for the period 2012-13 to 2016-17
April
May
June
July
August
September
October
November
December
January
February
March
Annexure III
SH 3/3
1 | List of beneficiaries/customers along with allocation by GoI including (allocation of unallocated share) / capacity as contracted should also be furnished separately for each generating station.
2 | Declared Capacity should be as per Regulation 31(3) of CERC Tariff Regulations for the period 2014-19 including month wise information may be furnished.
3 | Any relevant point or a specific fact having bearing on performance or operating parameters may also be highlighted or brought to the notice of the Commission.

## Annexure-IV
Annexure –IV
PLANT AVAILABILITY/SCHEDULED PLANT LOAD FACTOR ACHIEVED Generating company: NHPC LTD. Name of Generating station: URI Power Station Installed Capacity (MW) : 480 MW Normative Annual Plant Availability Factor (%) approved by Commission : 70%
Plant Availability Factor Achieved (%)
Month | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | Reasons for shortfall in PAF achieved vis-a-vis NAPAF
April | 101.2146 | 101.1794 | 100.1603 | 100.1603 | 100.1603
May | 101.2146 | 101.2146 | 100.1603 | 100.1603 | 100.1603
June | 101.2146 | 100.4414 | 100.1603 | 99.8473 | 100.0636
July | 100.0582 | 87.1343 | 100.1603 | 100.1603 | 91.2326
August | 85.6719 | 68.8368 | 86.8736 | 100.1603 | 89.9347
September | 94.1506 | 67.7224 | 85.7894 | 80.3976 | 81.4287
October | 66.8982 | 50.6073 | 82.1972 | 82.0837 | 51.4462
November | 49.7638 | 50.6073 | 53.6297 | 92.8503 | 48.4987
December | 46.1179 | 46.5261 | 43.8081 | 68.7915 | 48.4987
January | 47.8865 | 49.3829 | 40.0811 | 56.7745 | 52.2252
February | 73.6517 | 62.5813 | 59.9581 | 61.0177 | 86.52
March | 101.2146 | 89.7191 | 100.1603 | 91.3856 | 100.1603
Annual | 80.7492 | 73.0051 | 79.5279 | 86.2081 | 79.0972
Plant Load Factor Achieved (%)
Month | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | Reasons for shortfall in PLF achieved vis-a-vis Target PLF
April
May
June
July
August
September
October
November
December
January
February
March
Annual

## Annexure-XIX (URI-I)
Annexure-XIX
Name of the Utility |  | NHPC LTD.
Name of the Generating Station |  | URI Power Station
Station/ Stage/ Unit |  | 4 x 120 MW
Fuel Type (Coal/ Lignite/ Gas/ Liquid Fuel/ Nuclear/ Hydro | [7 empty] | Hydro
Capacity of Plant (MW) |  | 480 MW
COD |  | 1997-06-01
|  | 2004-05 | 2005-06 | 2006-07 | 2007-08 | 2008-09 | 2009-10 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | Plant Availability Factor (PAF) (%) | 99.104 | 100 | 98.7806 | 99.7893 | 100 | 72.5146 | 82.1409 | 75.9474 | 80.7492 | 73.0051 | 79.5279 | 86.2081 | 79.0972
2 | Plant Load Factors (PLF) (%)
3 | Scheduled Energy (MU) | 2210.6066 | 2678.3975 | 2778.1387 | 2542.8177 | 3004.6075 | 2677.0881 | 3027.2524 | 2681.024 | 2942.527 | 2512.6199 | 3009.9533 | 3187.5332 | 2730.9419
4 | Scheduled Generation (MU)
5 | Actual Generation (MU) | 2206.65 | 2724.83 | 2818.086 | 2595.67 | 3032.12 | 2703.36 | 3040 | 2704.1246 | 2966.71 | 2520.78 | 3076.5532 | 3282.972 | 2803.0703
6 | Quantum of coal consumption (MT) | 1997-06-01 2004-05: Not Applicable
7 | Value of coal (Rs. Lakh)
8 | Specific Coal Consumption (kg/kwh)
9 | Gross Calorific Value of Coal (Kcal/ Kg)
10 | Heat Contribution of Coal (Kcal/ kwh)
11 | Cost Of Specific Coal Consumption (Rs./Kwh) – Finally admitted by CERC
12 | Quantum of Oil Consumption (Lit.)
13 | Value of Oil (Rs. lakh)
14 | Gross calorific value of oil (kcal/lit)
15 | Specific Oil Consumption (ml/ kwh)
16 | Cost Of Specific Oil Consumption (Rs./Kwh) – Finally admitted by CERC
17 | Heat Contribution of Oil (Kcal/ kwh)
18 | Station Heat Rate (kcal/kwh)
19 | Auxiliary Energy Consumption (%) | 0.5592 | 0.57503 | 0.5014 | 0.51278 | 0.97292 | 0.98766 | 0.96382 | 0.97998 | 0.971 | 0.976 | 0.972 | 0.982 | 1.014
20 | Debt at the end of the year (Rs. Crore) ^ | 514.4302 | 373.5648 | 81.0687 | 61.4752 | 41.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Equity (Rs. Crore) * | 1087.0687 | 1087.1287 | 1087.0645 | 1087.3533 | 1087.4166 | 1088.0576 | 1085.4783 | 1085.5977 | 1085.7699 | 1085.8874 | 1087.6438 | 1089.3449 | 1092.8672
22 | Working Capital (Rs. Crore) – finally admitted by CERC | 122.6223 | 116.918 | 133.4041 | 109.9775 | 113.7497 | 103.4711 | 82.3755 | 83.6574 | 78.9852 | 81.4403 | 74.6964 | 76.8348 | 79.1564
23 | Capital cost (Rs. Crore) – finally admitted by CERC | 3421.4447 | 3421.6447 | 3421.4307 | 3422.3934 | 3422.6046 | 3424.741 | 3416.1433 | 3416.5415 | 3418.0456 | 3418.3206 | 3423.3617 | 3429.0322 | 3440.7731
24 | Capacity Charges/ Annual Fixed Cost (AFC)
(a) Return on equity – pre tax (admitted by CERC)
| Absolute value | 152.181 | 152.1938 | 152.1935 | 152.2092 | 152.2339 | 255.4116 | 252.2388 | 249.0658 | 210.373 | 212.931 | 213.1147 | 213.4537 | 213.9659
| Rate (%) | 14% | 14% | 14% | 14% | 14% | 23.48% | 23.21% | 22.94% | 19.38% | 19.61% | 19.61% | 19.61% | 19.61%
(b) interest on Loan
| Absolute value | 38.2822 | 30.8365 | 15.291 | 1.7987 | 1.2921 | 0.5176 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rate (%) – Weighted Average Rate | 1997-06-01 2004-05: 6.302%; 1997-06-01 2005-06: 6.947%; 1997-06-01 2006-07: 6.727%; 1997-06-01 2007-08: 2.524%; 1997-06-01 2008-09: 2.524%; 1997-06-01 2009-10: 2.524%
(c) Depreciation (finally allowed by CERC)
| Absolute value | 186.5326 | 141.0228 | 233.4516 | 87.2814 | 87.2964 | 176.9257 | 46.6001 | 46.7068 | 46.7321 | 46.7559 | 46.9142 | 47.2863 | 47.7734
| Rate (%) | 1997-06-01 2004-05: 2.551%; 1997-06-01 2005-06: 2.551%; 1997-06-01 2006-07: 2.551%; 1997-06-01 2007-08: 2.551%; 1997-06-01 2008-09: 2.551%; 1997-06-01 2009-10: 5.168%; 1997-06-01 2010-11: As the power station has completed 12 years, remaining depreciation is uniformily distributed over the balance useful life.
(d) Interest on working Capital
| Absolute value | 12.5699 | 11.9841 | 13.6737 | 11.2725 | 11.6591 | 12.6752 | 10.091 | 10.248 | 9.6757 | 9.9764 | 10.084 | 10.3727 | 10.6861
| Rate (%) | 10.25% | 10.25% | 10.25% | 10.25% | 10.25% | 12.25% | 12.25% | 12.25% | 12.25% | 12.25% | 13.5% | 13.5% | 13.5%
(e) Operation and maintenance cost (finally admitted by CERC)
| Absolute value | 51.1724 | 53.2193 | 55.3481 | 57.562 | 59.8645 | 73.0401 | 77.218 | 81.6349 | 86.3044 | 91.241 | 74.194 | 79.1234 | 84.3804
Rate (%)
(f) Compensation Allowances | bar: 1997-06-01 2004-05
25 | AFC (Rs. Crores) | 440.7381 | 389.2565 | 469.9579 | 310.1238 | 312.346 | 518.5702 | 386.1479 | 387.6555 | 353.0852 | 360.9043 | 344.3069 | 350.2361 | 356.8058 | 2249.5717
26 | Energy Charge (Rs./Kwh) | 0.9796 | 0.86518 | 1.0445 | 0.6893 | 0.69423 | 1.1526 | 0.85827 | 0.86162 | 0.78478 | 0.80216 | 0.76527 | 0.77845 | 0.79305
27 | Total tariff (Rs. Kwh) | 1.9592 | 1.7304 | 2.0891 | 1.3786 | 1.3885 | 2.3052 | 1.7165 | 1.7232 | 1.5696 | 1.6043 | 1.5305 | 1.5569 | 1.5861
28 | Revenue realisation before tax (Rs. Crore) | 582.5646 | 478.2191 | 580.7126 | 372.9664 | 356.9351 | 440.5878 | 482.3946 | 725.0358 | 668.3803 | 555.0979 | 616.9291 | 681.2126 | 600.9893
29 | Revenue realisation after tax (Rs. Crore) #
30 | Profit/ loss before tax (Rs. Crore) | 313.4202 | 473.9886 | 379.64 | 314.8056 | 339.6812 | 202.4814 | 396.3384 | 539.2861 | 384.5744 | 306.7064 | 303.2554 | 326.7788 | 332.3988
31 | DSM Generation (MU) | -16.2832 | 27.1338 | 18.1606 | 26.4578 | -0.79803 | 6.6431 | -0.42397 | 14.6665 | 21.9654 | 3.4928 | 79.6061 | 115.7511 | 82.009
32 | DSM Rate (Ps/Kwh)
33 | Revenue from DSM (Rs. Crore) |  |  | 8.12 | 8.44 | 2.66 | 1.78 | 10.671 | 0.088051 | 13.035 | 9.4324 | 24.131 | 23.1919 | 15.3387
Note:
1. The data at Sl No. 20 to 27 has been filled based on CERC orders dated 13.07.2016, 18.02.2014 & 05.01.2010
2. The capital cost sl no. 23 & equity at sl no. 21 has been considered as closing equity & capital cost respectively as on 31st March of respective year.
3. The depreciation at Sl No. 24(c) for the period 2004-09 is inclusive of Advance Against Depreciation (AAD)
4. * The Return On Equity (ROE) at Sl No. 24(a) for the period 2004-09 is exclusive of Tax as the same was not part of AFC & separately reimbursable from beneficiaries.
5. ^ The Normative debt at the end of the year (sl no.20) has been considered as ZERO from 2009-10 onwards as the gross normative loan is fully repaid & allowed depreciation in respectve years are more than 70% of admitted additional capitalization.
6. Composite tariff shown at sl no. 27 is exclusive of J&K water usage charges.
7. # NHPC calculate Corporate Tax as a whole after considering all the admissible deductions, exemptions etc. as per Income Tax Act. Therefore unitwise calculation has not been made.
Note: Generating Companies are required to submit data for all generating stations.
This is a general format. Plants of different fuel users have to fill the cells as applicable to them. Tariff for the Hydro may be understood as composite tariff.
The data provided for the corresponding years need to mention as Actual or provisional.
Data for each Unit and Stage is required to be submitted in additional sheets as per the format.

## 2015-16-17
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC LTD.
| Name of Power Station: | URI-I POWER STATION
Sl. No. | ITEMS | 2015-16 | 2016-17 | Variance% | Remarks
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 11711619 | 3526138 | -69.89 | This is to mention that due to change in accounting policy regarding Capital Spares, Expenditure on Consumption of stores and spares in the year 2016-17 is less in comparison to previous year. After regrouping of the previous year figure 2015-16, the expenditure on capital spares comes to Rs.51,36,456. This has happened due to IND AS Policy.
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 19297682 | 11814079 | -38.78 | In the year 2015-16 repairs of eroded portion of HRT culvert at Boniyar Nallah and repair of eroded portion down stream of apron in the vicinity of silt excluder gallery had been carried out. | 7483603 | 63.3448
2.2 | For Power House and all other works | 29062420 | 49287839 | 69.59 | The power station was commissioned in Year 1997. With the passage of time, requirements of repair and maintenance activities of power plant and other equipment are on rise. To avoid unforeseen machine breakdown of machines, the R&M of various plants / equipment are taken cyclically on year to year basis. Moreover with the commissioning of Kishanganga HE Project, the available time for machine maintenance will be less due to increase in river inflow from Kishenganga HE Project. Keeping this in view O&M division has advised to take up the Major maintenance of two units per year (compared to one unit in previous years) , which involves replacement of all under water parts. Accordingly from year 2016-17 onwards, major maintenance of two units are being undertaken. Hence repair of runner (2 nos) and refurbishment of guide vanes ( 2 sets ) are also done each year along with other replacement of capital parts of machine. Previously only Major maintenance of machine was carried out from outside agency. But due to lack of manpower from year 2016-17, annual maintenance as well as Major maintenance of machines are carried out from outside agency. Which also lead to increase in R&M expenditure. All these reasons contributed to the increase in R&M expenditure of power plants & others from year to year. | -20225419 | -41.0353
| Sub-Total (Repair and Maintenance) | 48360102 | 61101918
|  | 0 | 0
3 | Insurance | 156109355 | 165319350 | 5.9
4 | Security Expenses | 208293936 | 243737893 | 17.02 | Increase in expenditure due to provision made against the pay revision for the year 2016-17. | -35443957 | -14.5418
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 15935720 | 15992371 | 0.36 |  | -56651 | -0.35424
5.2 | Electricity charges | 5197411 | 2889210 | -44.41 | In the year 2016-17 electricity expenditure decreased in comparison to year 2015-16. It has happened due to surrender of electricity connection of Ghantamulla Colony. | 2308201 | 79.8904
5.3 | Travelling & Conveyance | 4232566 | 5939880 | 40.34 | as per actual
5.4 | Telephone, Telex & Postage (Communication) | 3633702 | 3260614 | -10.27 | As per Actual | 373088 | 11.4423
5.5 | Advertisement | 2210404 | 1921538 | -13.07 | Advertisement cost decrease due to poor law & order condition of the valley. | 288866 | 15.0331
5.6 | Donation | 0 | 0
5.7 | Entertainment | 27000 | 27650 | 2.41
|  | 0 | 0
| Sub-total (Administrative expenses) | 31236803 | 30031263
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 318722063 | 373138809 | 17.07 | Provision of wage revision due to 3rd PRC and due to change in ceiling of Gratuity from 10 lacs to 20 lacs
6.2 | Staff welfare expenses | 41225253 | 15642189 | -62.06 | Due to Decrease in Retired Employee Medical Benefit Acturial valuation provision and Exps of Medical claims.
6.3 | Productivity Linked incentive | 11679058 | 27135231 | 132.34 | Increase due to payment of arear of PLGI at revised rate from F.Y 2010-11 to F.Y 2013-14 and provision of PLGI for Q4 of FY 2016-17 made on revised pay
6.4 | VRS-Ex-gratia | 0 | 0
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 12577868 | 13412846 | 6.64
| Sub-total (Employee Cost) | 384204242 | 429329075 |  |  | -45124833 | -10.5105
7 | Loss of Store | 0 | 33420 |  | as per actuaL.
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 243236560 | 449017852 | 84.6 | As per allocation received from C.O/R.O.
|  | 0 | 0
10 | Others (Specify items) | 16717587 | 19036544 | 13.87 | Due to Increase in Payment to Kendriya Vidyalya and maintenance of Guest House and Training Exps.
11 | Total (1 to 10) | 1099870204 | 1401133453
12 | Revenue /Recoveries | 16985081 | 16289883 | -4.09
13 | Net Expenses | 1082885123 | 1384843570
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation
Note on D28: 922204
Note on D34: 900185
Note on D39: 923401

## 2014-15-16
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC LTD.
| Name of Power Station: | URI-I POWER STATION
Sl. No. | ITEMS | 2014-15 | 2015-16 | Variance% | Remarks
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 15981189 | 11711619 | -26.72 | As per actual consumption.
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 7420593 | 19297682 | 160.06 | In the year 2015-16 repairs of eroded portion of HRT culvert at Boniyar Nallah and repair of eroded portion down stream of apron in the vicinity of silt excluder gallery had been carried out.
2.2 | For Power House and all other works | 28217927 | 29062420 | 2.99
| Sub-Total (Repair and Maintenance) | 35638520 | 48360102
|  | 0 | 0
3 | Insurance | 112970574 | 156109355 | 38.19 | In case of Mega Insurance Police 1. Increase in premium rates on account of deteriorating claim ratio as a result of loss due Fire incident at Uri-II Power Station and submergence of Chutak power Station in November 2014 and June 2015 respectively and other claims during policy period 2014-15 2. Increase in sum-insured due to increase in reinstatement cost of assets on Valuation. 3. Increase in the rate of Service Tax and WCT from 12.36% to 14% and 10.5% to 12.6% respectively. In case of CPM policy, Increase in Sum insured due to valuation of Assets, additional Construction equipment purchased and increase in premium rates & Service Tax/WCT rates as above.
4 | Security Expenses | 174910840 | 208293936 | 19.09 | Increase in expenditure due to provision made against the pay revision w.e.f. 01.01.2016.
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 16359847 | 15935720 | -2.59
5.2 | Electricity charges | 5409095 | 5197411 | -3.91
5.3 | Travelling & Conveyance | 6541716 | 4232566 | -35.3 | as per actual
5.4 | Telephone, Telex & Postage (Communication) | 3159594 | 3633702 | 15.01 | As per actual, variation is only 13%
5.5 | Advertisement | 1826410 | 2210404 | 21.02 | Increase in the Advertisement cost in the year 2015-16 in comparison to previous year is mainly due to advertisement of various works and purchase undertaken.
5.6 | Donation | 0 | 0
5.7 | Entertainment | 12150 | 27000 | 122.22 | as per actuaL.
|  | 0 | 0
| Sub-total (Administrative expenses) | 33308812 | 31236803
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 297072046 | 318722063 | 7.29
6.2 | Staff welfare expenses | 20194972 | 41225253 | 104.14 | Due to Increase in Retired Employee Medical Benefit Acturial valuation provision, and Medical claims.
6.3 | Productivity Linked incentive | 10400720 | 11679058 | 12.29 | Increase in PLI due to normal incease of salary as compared to previous year.
6.4 | VRS-Ex-gratia | 0 | 0
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 12215651 | 12577868 | 2.97
| Sub-total (Employee Cost) | 339883389 | 384204242
7 | Loss of Store | 13237 | 0 | -100 | as per actuaL.
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 236525250 | 243236560 | 2.84 | As per allocation received from C.O/R.O.
|  | 0 | 0
10 | Others (Specify items) | 12771044 | 16717587 | 30.9 | Due to Increase in Payment to Kendriya Vidyalya and maintenance of Guest House Exps.
11 | Total (1 to 10) | 962002855 | 1099870204
12 | Revenue /Recoveries | 4024789 | 16985081 | 322.01 | Increase in Other Income & Provision/Liability not required written back
13 | Net Expenses | 957978066 | 1082885123
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 2013-14-15
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC LTD.
| Name of Power Station: | URI-I POWER STATION
Sl. No. | ITEMS | 2013-14 | 2014-15 | Variance | Remarks
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 17980471 | 15981189 | -11.1192 | On the basis of actual requirement and there is variation of approx 13%. | 1999282 | 12.5102
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 6242561 | 7420593 | 18.871 | Increase of cost of Trash cleaning and other works. | -1178032 | -15.8752
2.2 | For Power House and all other works | 31206057 | 28217927 | -9.5755 |  | 2988130 | 10.5895
| Sub-Total (Repair and Maintenance) | 37448618 | 35638520
|  | 0 | 0
3 | Insurance | 82833551 | 112970574 | 36.3826 | 1). Increase in premium rates on account of deteriorating claim ratio as a result of loss at Dhauliganga & Tanak Pur Power Station due to flood in June 2013 and other factors in the reinsurance market. 2). Increase in sum-insured due to Increase in reinstatement cost of assets on Valuation 3).Increase in premium rates of CPM Policy on account of deteriorating claim ratio as a result of loss at Dhauliganga Power Station due to flood in June 2013.
4 | Security Expenses | 166066154 | 174910840 | 5.326 |  | -8844686 | -5.0567
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 22597304 | 16359847 | -27.6027 | In the year 2013-14 provision for rent of Rs.97,28,250 had been made against the demand raised for Ghantamulla Colony by Executive Engineer hence expenditure in year 2013-14 is more in comaprison year 2014-15.
5.2 | Electricity charges | 5411449 | 5409095 | -0.0435 | Expenditure is almost equal. | 2354 | 0.043519
5.3 | Travelling & Conveyance | 4586719 | 6541716 | 42.623 | Increase in Travelling allowance Rate and as per actual requirement.
5.4 | Telephone, Telex & Postage (Communication) | 2313789 | 3159594 | 36.555 | Services of MPLS Port had been availed from the last quater of the 2013-14. In the year 2014-15 expenditure for the whole year booked, this is the main reason of variation between the two year. | -845805 | -26.7694
5.5 | Advertisement | 554345 | 1826410 | 229.4717 | Increase in the Advertisement cost in the year 2014-15 in comparison to previous year is mainly due to advertisement of various works and purchase undertaken.
5.6 | Donation | 0 | 0
5.7 | Entertainment | 8250 | 12150 | 47.2727 | as per actuaL.
|  | 0 | 0
| Sub-total (Administrative expenses) | 35471856 | 33308812
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 276426424 | 297072046 | 7.4688
6.2 | Staff welfare expenses | 15399856 | 20194972 | 31.1374 | Due to Increase in Retired Employee Medical Benefit Acturial valuation provision, Exps of Uniform and Medical claims.
6.3 | Productivity Linked incentive | 7104742 | 10400720 | 46.3912 | PLGI limit was enhanced to 20% from 12.5% of basic pay.
6.4 | VRS-Ex-gratia | 0 | 0
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 6650497 | 12215651 | 83.6803 | 1). Increased in Expenditure is due to Provision for incremental profit was not taken in F.Y 2013-14. Incremental profit was taken while providing for F.Y 2014-15.
| Sub-total (Employee Cost) | 305581519 | 339883389 | 11.2251 |  | -34301870 | -10.0922
7 | Loss of Store | 48283 | 13237 | -72.5846 | as per actuaL.
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 234135916 | 236525250 | 1.0205 | As per allocation received from C.O/R.O.
|  | 0 | 0
10 | Others (Specify items) | 11966912 | 12771044 | 6.7196
11 | Total (1 to 10) | 891533280 | 962002855
12 | Revenue /Recoveries | 28547068 | 4024789 | -85.9012 | Provision/Liability not required written back and Other Income
13 | Net Expenses | 862986212 | 957978066
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 2012-13 -14
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC LTD.
| Name of Power Station: | URI-I POWER STATION
Sl. No. | ITEMS | 2012-13 | 2013-14 | Variance% | Remarks
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 2161861 | 17980471 | 731.7126 | Consumption of the Capital Spares as per actual and Annual Maintenance requirement.
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 3628212 | 6242561 | 72.0561 | Increase of cost of Trash cleaning and other works.
2.2 | For Power House and all other works | 26829788 | 31206057 | 16.3112 | As per actual.
| Sub-Total (Repair and Maintenance) | 30458000 | 37448618
|  | 0 | 0
3 | Insurance | 60779071 | 82833551 | 36.2863 | 1). Increase in premium rates on account of deteriorating claim ratio as a result of loss at Dhauliganga & Tanak Pur Power Station due to flood in June 2013 and other factors in the reinsurance market. 2). Increase in sum-insured due to Increase in reinstatement cost of assets on Valuation. 3).Increase in premium rates of CPM Policy on account of deteriorating claim ratio as a result of loss at Dhauliganga Power Station due to flood in June 2013 and increase in Sum-insured.
4 | Security Expenses | 162844920 | 166066154 | 1.9781
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 10857802 | 22597304 | 108.1204 | In the year 2013-14 provision for rent of Rs.97,28,250 had been made against the demand raised for Ghantamulla Colony by Executive Engineer resulted in increased expenditure in this head.
5.2 | Electricity charges | 4289713 | 5411449 | 26.1494 | Change in cost of electricity.
5.3 | Travelling & Conveyance | 4959727 | 4586719 | -7.5207
5.4 | Telephone, Telex & Postage (Communication) | 2163356 | 2313789 | 6.9537
5.5 | Advertisement | 706964 | 554345 | -21.5879 | Expenditure decrease due to less adverisement for the works and supplies.
5.6 | Donation | 0 | 0
5.7 | Entertainment | 34050 | 8250 | -75.7709 | as per actuaL.
|  | 0 | 0
| Sub-total (Administrative expenses) | 23011612 | 35471856 | 54.1476
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 240973536 | 276426424 | 14.7124 | Due to annual increment, increase in DA Rate and promotion etc.
6.2 | Staff welfare expenses | 14596020 | 15399856 | 5.5072
6.3 | Productivity Linked incentive | 13060071 | 7104742 | -45.5995 | Decrease in expenditure because during F.Y 2012-13, PLGI was paid from 2007-2010 on revised pay.
6.4 | VRS-Ex-gratia | 0 | 0
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 11196635 | 6650497 | -40.6027 | Decrease in expenditure because during F.Y 2012-13, PRP for F.Y 2010-11 & F.Y 2011-12 was paid.
| Sub-total (Employee Cost) | 279826262 | 305581519 | 9.204
7 | Loss of Store | 21534 | 48283 | 124.2175 | as per actuaL.
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 276094186 | 234135916 | -15.1971 | As per allocation received from C.O/R.O.
|  | 0 | 0
10 | Others (Specify items) | 10779828 | 11966912 | 11.0121 | Due to Increase in Training Exps.
11 | Total (1 to 10) | 845977274 | 891533280 | 5.385
12 | Revenue /Recoveries | 51165612 | 28547068 | -44.2065 | Due to Provision not required written back Rs. 0.40 crore in comparison to 3.84 crore in 2012-13.
13 | Net Expenses | 794811662 | 862986212 | 8.5774
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation
Note on C25: LESS EDC 980121