## Sheet2
NOx ABATEMENT & SNCR SYSTEM AT 2x525 MW MAITHON POWER LIMITED PRELIMINARY ELECTRICAL LOAD LIST
Sl. NO. | Description of Feeder | Rating (KW/ KVA) | Supply Type |  |  |  | Quantity
|  |  |  | UNITISED(U)/ STATION(S) | NORMAL(N) / EMERGENCY(E) | Service (Continuous(C)/ Intermittent(I)) | Working | Standby | Remarks | Energy Consumption
In-Combustion Loads
1 | Dynamic Classifier for Unit 1 | 45 | 415 V 3 Ph AC | U | N | C | 7 | 1
2 | Dynamic Classifier for Unit 2 | 45 | 415 V 3 Ph AC | U | N | C | 7 | 1
3 | UPS DB for analyzer loads for Unit 1 | 3 | 240 V AC UPS Supply | U | UPS | C | 1 | 1 |  | 26280
4 | UPS DB for analyzer loads for Unit 2 | 3 | 240 V AC UPS Supply | U | UPS | C | 1 | 1 |  | 26280
SNCR Loads
3 | Urea Circulation Pumps for Unit 1 | 1.5 | 415 V 3 Ph AC | U | N | C | 1 | 1 |  | 13140
4 | Urea Circulation Pumps for Unit 2 | 1.5 | 415 V 3 Ph AC | U | N | C | 1 | 1 |  | 13140
5 | Dilution Pump for Unit 1 | 3 | 415 V 3 Ph AC | U | N | C | 1 | 1 |  | 26280
6 | Dilution Pump for Unit 2 | 3 | 415 V 3 Ph AC | U | N | C | 1 | 1 |  | 26280
7 | Dilution Water Transfer Pump | 160 | 415 V 3 Ph AC | S | N | I | 1 | 1 |  | 700800
8 | Urea Bulk Storage Forwarding Pump | 55 | 415 V 3 Ph AC | S | N | I | 1 | 1 |  | 240900
9 | Urea Transfer Pump from Solution Tank | 45 | 415 V 3 Ph AC | S | N | I | 1 | 1 |  | 197100
10 | Cooling Water Pump | 15 | 415 V 3 Ph AC | S | N | C | 2 | 0 |  | 262800
11 | Agitator for Day Storage Tank | 7.5 | 415 V 3 Ph AC | S | N | I | 1 | 0 |  | 32850
12 | Agitator for Bulk Storage Tank | 30 | 415 V 3 Ph AC | S | N | I | 1 | 0 |  | 131400
13 | Agitator for Solutionizing Tank | 7.5 | 415 V 3 Ph AC | S | N | I | 1 | 0 |  | 32850
14 | Urea Transfer Conveyor | 15 | 415 V 3 Ph AC | S | N | I | 1 | 1 |  | 65700
15 | Lance Motor for Unit 1 | 3 | 415 V 3 Ph AC | U | E | I | 4 | 0
16 | Lance Motor for Unit 2 | 3 | 415 V 3 Ph AC | U | E | I | 4 | 0
17 | Compressor | 150 | 415 V 3 Ph AC | S | N | C | 1 | 1 |  | 1314000
18 | HVAC | 20 | 415 V 3Ph AC | S | N | C | 1 | 1 | Assumed load for HVAC. To be updated as per the final building/area design. | 175200
19 | Lighting Load | 20 | 415 V 3Ph AC | S | N | C | 1 | 1 | Assumed load for Lighting System. To be updated as per the final building/area design. | 175200
20 | Emergency Lighting Load | 8 | 415 V 3Ph AC | S | E | C | 1 | 1 | Assumed load for Emergency Lighting System. To be updated as per the final building/area design. | 70080
21 | Heater Load for Various Tanks | 350 | 415 V 3Ph AC | S | N | I | 1 | 1 | Assumed lump load for all the heaters. To be updated as per final tanks/pipe design. | 1533000
[9 empty] | Likely Total Consumption | 5063280
[9 empty] | % in terms of Gross Generation' | 0.05505%
NOTE: Please note that this is a preliminary load list. The loads indicated may change as the engineering progresses. As of now Dynamic Classifier at sl nos. 1 and 2 are not applicable.
Further, duty factor of 0.5 has been considered for intermittent load
LEGEND
1) UNITISED(U) /STATION(S): U-is applied for each unit, S-STN (Is applied for common equipment load)
2) NORMAL/ EMERGENCY: N-normal Supply, E-Emergency Supply (i.e DG supply), UPS = UPS Supply
3) RUNNING MODE: C-Continuous, I-Intermittent