## Slide 1
NTPC submission on Draft CERC (Indian Electricity Grid Code) (First Amendment) Regulations, 2024
/ntpc1
/ntpcltd1
/ntpclimited
/Company/ntpc
/ntpclimited
Follow us on:
NTPC R&R Colony, Darlipali
NTPC Bhadla
NTPC Rojmal
NTPC Koldam
NTPC Kayamkulam
NTPC Kudgi

## Slide 2: Requirement of furnishing efforts to achieve a schedule of Minimum Turn Down level (MTL).
Regulation 49(2)(a)(5)(a) of the Draft Amendment provides that in case a generating station has received schedule up to MTL in peak hours but not during off peak hours, it shall be provided schedule up to MTL through SCED.
However, for that, Generating station has to furnish the efforts made to achieve schedule up to MTL through the sale of power in the Power market to respective RLDCs.
Electricity (Late Payment Surcharge and Related Matters) (Amendment) Rules-2024 has made it mandatory for generators to bid the URS power in the power exchange.
In case generating company fails to offer such URS power in the power exchange, there are penal provisions of deduction of Fixed Charges. Hence requirement of arranging schedule through market is being taken care by LPS rules.
Further, as per the procedure issued by NLDC for the implementation of above provisions all market participation related information is being furnished to RLDCs. Therefore, the additional requirement of furnishing the efforts by the generators to RLDCs may be relaxed.
Since LPS rules has made it mandatory to offer 100% URS power in market, the requirement of furnishing the efforts to get MTL schedule may be dropped.

## Slide 3: Non-Revision of Schedule under T-GNA bilateral transactions in case of Partial Outage
Vide Suo-motto order dt. 30.09.2023, Hon’ble Commission has allowed revision of DC and schedule under bilateral transactions in case of partial outage. Draft amendment in Regulation 49(7)(a) also provides the same.
In case of partial outage, though the revisions of DC and schedule under bilateral transactions have been allowed, however, the revision of schedule under T-GNA bilateral transaction is not being allowed due to clause 49(4)(a) of IEGC 2023, which provides as follows:
“…………scheduled transactions under T-GNA once scheduled cannot be revised other than in case of forced outage as per clause (7) of this Regulation.”
In case of partial outage, non-revision of schedule under T-GNA bilateral transaction is causing an imbalance between actual injection by the generator and drawal by the beneficiaries.
Considering that the partial outages are inevitable, the Hon'ble commission has pleased to consider partial outage akin to forced outage and has provided equal treatment for DC and schedule revisions.
Therefore, to give effect to the provision of the proposed amendment, clause 49 (4)(a) of IEGC 2023 also needs be modified as follows:
“…Provided that scheduled transactions under T-GNA once scheduled cannot be revised other than in case of forced/partial outage as per clause (7) & 7 (a) of this Regulation.”

## Slide 4: Restriction on number of DC revisions on account of Partial outage
As per Regulation 49 (7-a) of Draft amendment, Coal based generating stations are allowed a maximum of 4 numbers of DC revisions in a day subject to a maximum of 60 revisions during a month.
Operation of thermal power plants involves running of a large number of auxiliary systems and some of these systems do not have in-built redundancy. Such partial outages are inevitable and cannot be avoided in spite of having best operation practices.
The proposed provision is independent of the number of units in a station and is insufficient for the stations having number of units more than 2. It is also putting restriction in declaring their correct generation capabilities.
In case downward revision is not allowed there shall be a mismatch in actual injection and corresponding drawal schedule of the beneficiaries which is not conducive for Grid security. Similarly, if upward revision in DC is not allowed, it shall deprive Grid from available power.
It is pertinent to mention that such DC revisions are allowed only on account of technical reasons be recorded in writing.
In view of above following may please be provided:
Stations having more than two units, 6 DC revisions per day may be allowed subject to maximum of 90 revisions in a month.

## Slide 5: Procedure for Revival of Units from USD....(1/2)
Grid code provides that, if a unit has not received schedule up to MTL, it may go under Unit Shut Down (USD).
NLDC has issued a procedure for SCUC, SCED and USD on 16.04.2024. The procedure provides methodology for revival of a unit from USD for system requirement (SCUC) after considering the technical requirements of the unit such as startup time and commitment for minimum On-bar time.
However, no such methodology has been provided for revival of a unit from USD in other cases such as schedule given by beneficiaries.
For the revival of an Off-bar unit from USD, a prior intimation and requisite time from intimation to achieve the desired load is required.
The above time varies based on the unit condition i.e. cold/warm/hot. Further, in order to avoid frequent start/stop of the unit, commitment of Minimum on bar time is also required.
It is pertinent to mention that beneficiaries give schedule as per their own requirement which may be even up to 2 Hrs before actual delivery of power and without considering the above requirements.
In the absence of the procedure the generators are facing operational difficulties, and a suitable procedure is required for bringing the unit on bar.

## Slide 6: Procedure for Revival of Units from USD … (2/2)
  Such difficulties get more aggravated in case of Gas based stations because these are generally under USD and undergo frequent start/stops. Moreover, Gas based stations require 4-6 hours open cycle operation to achieve Combined cycle operation.
  Further, a min ramp rate of 1% is required to be prescribed for gas stations in combined cycle mode in line with coal stations as combined cycle operation involves steam generation in WHRB.
Earlier, the RSD procedure issued under IEGC 2010 used to facilitate the revival of units under shut down by providing a provision of declaration of OFF bar DC, Schedules considering start up time, ramp rate, minimum on bar time etc.
In order to facilitate the revival of unit under shut down, similar procedure may be provided as was exiting before IEGC 2023.
Procedure for revival of a unit from USD may please be provided in the Procedure issued for SCUC, SCED & USD

## Slide 7: Revision in estimated restoration time of a unit in case of planned outage
In case of outage of a unit there can be variation in the restoration time of the unit from the anticipated time.
As per the provisions of the Regulation 49(7) of IEGC 2023, generating station may revise its estimated restoration time in case of forced outage. However, the provision is silent on revision of restoration time of unit coming on bar after planned outage.
Similar to the case of forced outage, some unexpected issues may arise during the restoration process after the planned outage.
It may necessitate revision in the DC declared on Day ahead basis, however the same is not being allowed in absence of provision of revision of restoration time in case of Planned outages.
Restrictions placed on the revision of restoration time of the unit results in :
Deprivation of the grid from the power &
Financial implications on the generators
Provision for revision in restoration time in case of forced outage may be extended to planned outage also.

## Slide 8: Facilitation of requisite scheduling for carrying out Equipment Testing
IEGC-2023 mandates a generating station to conduct the following tests on periodic basis:
Real & Reactive Power Capability test,
Assessment of Reactive Power Control Capability.
Model Validation and verification test for the complete Generator and Excitation System model including PSS.
Model Validation and verification of Turbine/Governor and Load Control or Active Power/ Frequency Control.
Testing of Governor performance and Testing of Automatic Generation Control.
Similarly, certain systems like emission control system (ECS) etc are required to be installed to meets various guidelines issued by the appropriate authorities.
Tariff Regulations-2024 mandate that the ECS can be put into use only after meeting all applicable technical and environmental standards and the same is to be certified by the generator through the Management Certificate.
The testing of such systems and periodic tests require operation of the unit on full load and corresponding schedule.
Many times, the non-availability of the requisite schedule leads to delay in the testing or start of operation of such critical equipment.
A facilitation may be provided in the IEGC-2023 to provide requisite schedule to the generators to carry out equipment testing and periodic tests.

## Slide 9: Enabling provision for higher DC Declaration by hydro station during high inflows
As per Regulation 45(10)(a), hydro stations are allowed to declare DC up to 110% of normative ex-bus capacity during high inflow periods. The high inflow periods are notified by the respective RPCs in advance.
Due to change in climatic conditions, high inflow periods declared by the RPCs may not necessarily coincide with the actual high inflow of water.
For instance, high inflow period in respect of NTPC Koldam which is on Satluj basin has been declared by RPC for FY 2024-25 is June to September, but actual high inflow of water occurred in the month of May 24 also.
Since the stations can declare higher DC only during high inflow periods specified by RPCs, it deprives grid from availing extra power and may cause spillage of water.
Further Hydro stations with pondage (like Koldam) can provide 110% of normative ex-bus capacity at any day, So provision of declaration of higher DC may be given to the station as per their pondage capacity.
In view of the above, the following provision may please be provided.
Hydro stations may declare DC up to 110% of normative ex-bus capacity if there is actual high inflow of water which may be beyond the high inflow period declared by respective RPC and based on their pondage capacity

## Slide 10: Restriction on DC declaration
Clause 45 (8) of the IEGC Regulations-2023 provides that a thermal generating station shall declare ex-bus Declared Capacity limited to 100% MCR less auxiliary power consumption.
Considering the fact that there is significant capacity on bar which can provide requisite 4500 MW of Primary frequency response, putting restriction on DC declaration on all the thermal stations, results in artificially depriving the Grid from power.
It is suggested that pit head coal stations having low ECR, may be allowed to declare DC up to 105% of MCR less auxiliary power consumption and scheduled up to their declared capacity.
Removal of ceiling on DC declaration on pit head stations shall result in
Reduction of the power procurement cost of DISCOMs due increased generation from cheaper pit head stations.
Higher availability of power during high demand days.
Regulation 45(8) may be modified and the DC & SG restriction of 100% MCR less auxiliary power consumption on may be removed for pit head stations.

## Slide 11
Thanks