###### Appendix- VI

###### Procedure for calculation of Transmission System Availability

- Transmission System Availability shall be certified by Member Secretary, RPC of the region concerned separately for each AC and HVDC Transmission System for which transmission charge is payable by a particular long-term transmission customer or is shared by same set of long-term transmission customers. The transmission elements shall be grouped into following categories for the purpose of calculation of availability of Transmission Systems :

- AC transmission lines: Each circuit of AC transmission line shall be considered as one element.

- Inter-Connecting Transformers (ICTs): Each ICT bank (three single phase transformer together) shall form one element.

- Static VAR Compensator (SVC): SVC along with SVC transformer shall form one element.  However, 50% credit to inductive and 50% to capacitive rating shall be given.

- Switched Bus Reactor: Each switched Bus Reactor shall be considered as one element.

- HVDC Bi-pole links: Each pole of HVDC link along with associated equipment at both ends shall be considered as one element.

- HVDC back-to-back station: Each block of HVDC back-to-back station shall be considered as one element.  If associated AC line (necessary for transfer of inter-regional power through HVDC back-to-back station) is not available, the HVDC back-to-back station block shall also be considered as unavailable.

- The Availability of AC and HVDC portion of Transmission system shall be calculated as under:

% System Availability for AC system

o X AVo + p X AVp + q X AVq + r X AVr

=  ------------------------------------------------------------ X 100

o + p + q + r

% System Availability for HVDC system

s  X  AVs  +  t   X AVt

= ----------------------------------  X  100

s + t

Where

o  	is	Total number of AC lines.

AVo   	is 	Availability of o number of AC lines.

p	is	Total number of switched bus reactors .

AVp	is	Availability of p number of switched bus reactors.

q	is	Total number of ICTs.

AVq	is	Availability of q number of ICTs.

r	is	Total number of SVCs.

AVr	is	 Availability of r number of SVCs.

s	is	Total number of HVDC poles

AVs	is	 Availability of s number of HVDC poles

t	is	Total number of HVDC back-to-back station blocks.

AVt     is	 Availability of t number of HVDC back-to-back station blocks

- The weightage factor for each category of transmission elements shall be as under:

- For each circuit of AC line – Surge Impedance Loading for Uncompensated line (SIL) multiplied by Circuit Km.

SIL rating for various voltage level and conductor configuration is given in Annexure-I to this Appendix. However, for the voltage levels and/or conductor configurations not listed in Annexure-I, appropriate SIL based on technical considerations may be used for availability calculation under intimation to long-term transmission customers.

- For each HVDC pole – The rated MW capacity x Circuit

Km.

(c)	For each ICT bank – The rated MVA capacity.

(d)	For SVC – The rated MVAR capacity (inductive &

capacitive).

(e)	For switched Bus reactor – The rated MVAR capacity.

- For HVDC back-to-back station connecting two Regional grids –Rated MW capacity of each block.

- The availability for each category of transmission elements shall be calculated based on the weightage factor, total hours under consideration and non-available hours for each element of that category.

- If a HVDC pole or a block of HVDC back-to-back station is constrained to operate on part load for a particular duration, for reasons not attributable to system conditions, the corresponding non-availability hours shall be considered as product of duration for such operation and partial non-availability during such period.

- The formulae for calculation of Availability of each category of the Transmission elements are as per Annexure-II to this Appendix.

- The transmission elements under outage due to following reasons not attributable to the transmission licensee shall be deemed to be available:

- Shut down of transmission elements availed by other agency/agencies for maintenance or construction of their transmission system.

- Manual tripping of line due to over voltage and manual tripping of switched bus reactor as per the directions of RLDC.

- Outage time of transmission elements for the following contingencies shall be excluded from the total time of the element under period of consideration.

- Outage of elements due to acts of God and force majeure events beyond the control of the transmission licensee. However, onus of satisfying the Member Secretary, RPC that element outage was due to aforesaid events and not due to design failure shall rest with the transmission licensee.  A reasonable restoration time for the element shall be considered by Member Secretary, RPC and any additional time taken by the transmission licensee for restoration of the element beyond the reasonable time shall be treated as outage time attributable to the transmission licensee.  Member Secretary RPC may consult the transmission licensee or any expert for estimation of reasonable restoration time.  Circuits restored through ERS (Emergency Restoration System) shall be considered as available.

- Outage caused by grid incident/disturbance not attributable to the transmission licensee, e.g. faults in substation or bays owned by other agency causing outage of the transmission licensee's elements, tripping of lines, ICTs, HVDC back-to-back stations etc. due to grid disturbance. However, if the element is not restored on receipt of direction from RLDC while normalising the system following grid incident/disturbance within reasonable time, the element will be considered not available for whole period of outage and outage time shall be attributable to the transmission licensee.

- If the outage of any element causes loss of generation at ISGS then the outage period for that element shall be deemed to be twice the actual outage period for the day(s) on which such loss of generation has taken place.

- RLDC shall furnish relevant information to Member Secretary, RPC on monthly basis.

- The Member Secretary, RPC shall calculate the availability for the each transmission system for which availability is required to be calculated separately and the detailed calculations shall be kept on the website of RPC for the comments of the long-term transmission customers.    Final certificate shall be issued after consideration of the comments so received.

- Once availability has been certified by Member Secretary, RPC following the due process, the bills shall be issued accordingly and there shall be no need to file the petition for determination of incentives. Only in case of any dispute about certification of availability or billing, the aggrieved party may file a petition with the Commission.

ANNEXURE-I

SURGE IMPEDANCE LOADING (SIL) OF AC LINES

| S.No. | Line voltage (kv) | Conductor Configuration | SIL (MW) |
| --- | --- | --- | --- |
| 1 | 765 | Quad Bersimis | 2250 |
| 2 | 400 | Quad Bersimis | 691 |
| 3 | 400 | Twin Moose | 515 |
| 4 | 400 | Twin AAAC | 425 |
| 5 | 400 | Quad Zebra | 647 |
| 6 | 400 | Quad AAAC | 646 |
| 7 | 400 | Tripple Snowbird | 605 |
| 8 | 400 | ACKC(500/26) | 556 |
| 9 | 400 | Twin ACAR | 557 |
| 10 | 220 | Twin Zebra | 175 |
| 11 | 220 | Single Zebra | 132 |
| 12 | 132 | Single Panther | 50 |
| 13 | 66 | Single Dog | 10 |

# ANNEXURE-II

Formulae for calculation of Availability of each category of transmission elements

o			o

AVo(Availability of o no. of AC lines) 	=  Wi(Ti -TNAi)	  Wi

i=1     Ti	         i=1

p			     p

AVp(Availability of p no. of Switched	=   Wm(Tm-TNAm)	       Wm

Bus reactors)				   m=1     Tm		   m=1

q			  q

AVq(Availability of q no. of ICTs) 		=  Wk(Tk - TNAk)	    Wk

K=1     Tk		 k=1

s			    s

AVs(Availability of s no. of HVDC pole)	=  Wj(Tj -TNAj)	    Wj

j=1     Tj	   	  j=1

t			   t

AVt (Availability of t no. of HVDC 		 =   Wn(Tn-TNAn)	    Wn

Back-to-back Blocks)			   n=1     Tn		 n=1

Where	 Wi		=	Weightage factor for ith  transmission line

Wm		=	Weightage factor for mth bus reactor

Wk		=	Weightage factor for kth ICT

WIl & WCl     =	Weightage factors for inductive & capacitive operation of lth  SVC

Wj		=	Weightage factor for jth HVDC pole

Wn		=	Weightage factor for nth HVDC back to back block.

Ti, Tm, Tk, TIl, TCl, Tj & Tn -	The total hours of ith AC line, mth Switched Bus Reactor, kth ICT, lth SVC	(Inductive  	Operation), lth SVC (Capacitive Operation), jth HVDC pole & nth HVDC back-to-back block during the period under consideration (excluding time period for outages not attributable to transmission licensee for reasons given in Para 6 of the procedure)

TNAi, TNAm, , TNAk, TNAIl, TNACl, TNAj , TNAn  -	The non-availability hours (excluding the time period for outages not attributable to transmission licensee taken as deemed availability as per Para 5 of the procedure) for ith AC line, kth ICT, mth  Switched Bus Reactor, lth SVC (Inductive Operation), lth SVC (Capacitive Operation), jth HVDC pole & nth  HVDC back-to-back block .