CENTRAL ELECTRICITY REGULATORY COMMISSION

Core-3, 5th Floor. SCOPE Complex, Lodi Road, New Delhi – 110 003

Tel: 4364911 Fax: 4360010/4360058

Ref. No.12/2/1/99-CERC				                              Date: 15.9.2000

Sub:  Petition No.4/2000 – Operational Norms for Thermal Generation - Regarding

## Sir

The commission heard the above petition on 09.05.2000 and constituted an expert group under the Chairmanship of Shri V.S.Verma, Chief Engineer CEA with members drawn from NTPC, NLC and Power Grid to review all the norms as already available in the draft, based on the submission made by the respondents and to arrive at agreed recommendations for the consideration of the Commission.  The Chairman, expert group submitted the report on 12th September 2000 without consensus on the various issues involved.   The three members of the expert group representing NTPC, NLC and MSEB (co-opted) submitted a separate report on 8.9.2000.  A comparative statement of norms in the draft circulated by CERC in Jan., 2000, recommendations of Chairman, expert group and recommendations of NTPC, NLC & MSEB members represented in the expert group on the major issues is enclosed.

It is requested that the comments/objections from all parties viz. CPU’s, SEB’s & PSU’s, if any, may be filed immediately.  The original reports referred above may be inspected at CERC office during the office hours.

-Sd-

(K.S.DHINGRA)

Encl.: as above.                                                                                   JT.CHIEF (LEGAL)

## Thermal Operation Norms - Comparative statement amongst Draft circulated by CERC in Jan.,2000, Recommendations of chairman, expert group and Recommendations of NTPC, NLC & MSEB members represented in the expert Group

| Sl.No | Particulars | Draft Operation norms as notified by CERC (January, 2000) | Recommendations as per CEA, (Chairman of Expert Group -September, 2000) | Recommendation of NTPC, NLC, MSEB (Members represented in Expert Group) |
| --- | --- | --- | --- | --- |
| 1. | 2. | 3. | 4. | 5. |
| A. GENERAL |
| 1. | Settlement Period | An hour or any other agreed period which was later clarified as to be 15 minutes to match with ABT recommendations. | Daily basis | Variable charges should be based on single normative heat rate for the tariff period and payable monthly. |
| 2. | Applicability of Norms | To be made applicable to central generating station. | To be made applicable to Central Generating stations. | Norms should be applicable to all generating stations in the country, irrespective of ownership. |
| B. COAL/LIGNITE BASED PLANTS |
| 1. | Margins/ Degradation factor for variation in Operational factors for existing units. | 5.0%(4.5 + 0.5) Based on 4.5% for TG Island and 0.5% for Boiler Island. | Coal Based (Existing Units) 500 MW units = 4.25(3.962 +0.296) 200 MW units = 4.0 (3.712 +0.296) Lignite Based Units 200 MW units = 5.25 (4.397 +0.813) (Existing stage II units with water lancing) | The prevailing norms shall continue for existing stations. |
| 2(a) | Base Turbine Cycle Heat Rate based on GCV of fuel | New Units | New Units | New Units |
|  |  |  | 100% | 80% | 60% | 50% | 100% | 80% | 60% | 50% | -Not furnished on a comparable basis with col(4). - The normative value of Heat Rate shall be the guaranteed,/demonstrated value plus a margin as specified in # B 3. |
|  |  | 170 kg/cm2/ 535/535°C | 2000 | 2040 | 2100 | 2135 | 1990 | 2030 | 2090 | 2125 |  |
|  |  | 150 kg/cm2/ 535/535°C | 2040 | 2080 | 2140 | 2175 | 2025 | 2065 | 2125 | 2160 |  |
|  |  | 130 kg/cm2/ 535/535°C | 2080 | 2120 | 2180 | 2215 | 2065 | 2105 | 2165 | 2200 |  |
| 1. | 2. | 3. | 4. | 5. |
| 2(b) | Boiler efficiency | Boiler efficiency =92.5 – 50A+630(M+9H) GCV | For coal based units Boiler efficiency = 88.7 – 50A + 630M GCV For lignite based units Boiler efficiency =91.3 – 50A+630(M+9H) GCV | For New Units For coal based units Boiler efficiency = 86.15 – 50A + 630M GCV For lignite based units Boiler efficiency =81.339– 50A+630(M) GCV |
| 3. | Degradation Factor formula as per C1. B-1.12.1(a) Of CERC document | Applicable heat rate to be lower of the Following two values:- 1..05X Guaranteed Heat rate Base value as indicated in table above | The factor of 1.05 has been revised as Under :- 1.04 for coal fired units with super heater spray taken before H.P heaters. 1.0375 for other coal fired units 1.0495 for lignite fired units | For New Units, the applicable Heat Rate shall be Guaranteed / Demonstrated Heat Rate at 100% load plus following margins: NTPC – 10.284% including 0.205% for startup and 0.8 % for pipe insulation loss. MSEB – 12.510% NLC - 10.323% |
| 4. | Decrease in GCV value of Coal/lignite From ‘As received basis’ To ‘As fired basis’. | 100kCal/kg | Nil | Calorific Value on as fired basis. |
| 5. | Auxiliary Energy consumption | Different values for various types of plants/ systems. | All values decreased by 0.5%. Further adjustments on part load operations done away with. | To retain existing norms as per GOI notification 30.3.1992 and for lignite fired station 10.5% |
| 6. | COD | As on PG test completion | Completion of trial run. | Completion of trial run. |
| 7. | Secondary fuel Oil consumption | 1 ml/kWh for coal 3 ml/kWh for lignite. | 1 ml/kWh for coal 2 ml/kWh for lignite. | 3.5 ml/kWh for all types of units |

| Sl.No | Particulars | Draft Operation norms as notified by CERC (January, 2000) | Recommendations as per Report submitted by Chairman Expert Group (September, 2000) | Recommendation as NTPC, NLC & MSEB (Members represented in Expert Group) |
| --- | --- | --- | --- | --- |
| 1. | 2. | 3. | 4. | 5. |
| C. GAS/NAPTHA BASED PROJECTS |
| 1. | Margins/ Degradation factor for variation in Operational factors for existing units. | 3.5% for CCGT and 3.25% for SCGT. | 4 % for CCGT as well as for SCGT. Additional margin of 25 kcal /kWh for CCGT and 40 kcal / kWh for SCGT on account of NOx control in the heat rate based on GCV. | The prevailing norms shall continue for existing stations. |
| COMBINED CYCLE OPERATION |
| 2. | Base Heat Rate on LCV basis at ISO | New Units | New Units |  |
|  |  |  | 100% | 80% | 60% | 50% |  | 100% | 80% | 60% | 50% | -Not furnished on a comparable basis with col(4). - The normative value of Heat Rate shall be the guaranteed, demonstrated value plus a margin as specified in # C 6. |
|  |  | Upto 50 MW and Less | 1800 | 1850 | 1980 | 2080 | Upto 30 MW and Less | 1719 | 1771 | 1891 | 1994 |  |
|  |  | More than 50 MW and less than 200 MW. | 1680 | 1730 | 1850 | 1950 | More than 30 MW and Upto 50 MW. | 1792 | 1846 | 1971 | 2079 |  |
|  |  | More than 200 MW and above | 1580 | 1630 | 1740 | 1840 | More than 50 MW and Upto 100MW. | 1672 | 1722 | 1839 | 1940 |  |
|  |  |  |  |  |  |  | More than 100 MW and Upto 150 MW. | 1694 | 1745 | 1863 | 1965 |  |
|  |  |  |  |  |  |  | More than 150 MW and Upto 200 MW. | 1625 | 1674 | 1788 | 1885 |  |
|  |  |  |  |  |  |  | More than 200 MW and Upto 300 MW. | 1533 | 1579 | 1686 | 1778 |  |

| 1. | 2. | 3. | 4. | 5. |
| --- | --- | --- | --- | --- |
| 3 | Capacity Degradation factor | Year of Operation 1. 2. 3. 4. 5. 6. 7. 8. 9. 10. 11. 12. 13. 14. 15. | Natural Gas/Liquefied Natural Gas(LNG) 1.0000 0.9925 0.9850 0.9775 0.9700 0.9950 0.9875 0.9800 0.9725 0.9650 0.9950 0.9875 0.9800 0.9725 0.9650 | Naphtha Natural Gas Liquid(NGL) 1.000 0.990 0.980 0.970 0.960 0.995 0.985 0.975 0.965 0.955 0.995 0.985 0.975 0.965 0.955 | YEAR OF OPERATION | CAPACITY DEGRADATION FACTOR | The degradation factor should be based evaluated operating hours (EOH). |
|  |  |  |  |  |  | NG/LNG | Naphtha/NGL/HSD |  |
|  |  |  |  |  | 1 | 1.000 | 1.000 |  |
|  |  |  |  |  | 2 | 0.9925 | 0.990 |  |
|  |  |  |  |  | 3 | 0.9850 | 0.980 |  |
|  |  |  |  |  | 4 | 0.9775 | 0.970 |  |
|  |  |  |  |  | 5 | 0.9700 | 0.960 |  |
|  |  |  |  |  | After the first major overhaul of the plant and upto second major overhaul, the installed capacity shall be determined by multiplying the first year installed capacity by Capacity Degradation Factors for the corresponding years as given hereunder. |  |
|  |  |  |  |  | YEAR OF OPERATION | CAPACITY DEGRADATION FACTOR |  |
|  |  |  |  |  |  | NG/LNG | Naphtha/NGL/HSD |  |
|  |  |  |  |  | 1 | 0.9950 | 0.995 |  |
|  |  |  |  |  | 2 | 0.9875 | 0.985 |  |
|  |  |  |  |  | 3 | 0.9800 | 0.975 |  |
|  |  |  |  |  | 4 | 0.9725 | 0.965 |  |
|  |  |  |  |  | 5 | 0.9650 | 0.955 |  |
| SIMPLE CYCLE OPERATION |
| 4. | Base Turbine Cycle Heat Rate on LCV basis at ISO | New Units | New Units |
|  |  |  | 100% | 80% | 60% |  | 100% | 80% | 60% | -Not furnished on a comparable basis with col(4). - The normative value of Heat Rate shall be the guaranteed, demonstrated value plus a margin as a specified in item C 6. |
|  |  | Upto 50 MW and Less | 2800 | 2950 | 3175 | Upto 30 MW and Less | 2622 | 2761 | 2973 |  |
|  |  | More than 50 MW and less than 200 MW. | 2600 | 2750 | 2975 | More than 30 MW and upto 50 MW. | 2778 | 2925 | 3150 |  |
|  |  | More than 200 MW and above | 2400 | 2550 | 2775 | More than 50 MW and upto 100MW. | 2597 | 2747 | 2971 |  |
|  |  |  |  |  |  | More than 100 MW and upto 150 MW. | 2622 | 2773 | 3000 |  |
|  |  |  |  |  |  | More than 150 MW and upto 200 MW. | 2533 | 2679 | 2898 |  |
| 1. | 2. | 3. | 4. | 5. |
| 5. | Heat Rate correction for NOx control | CCCT using conventional combustor (other than dry low Nox) and steam/water injection for Nox control, Gross Heat Rate shall be increased as under: Fuel N Gas/LNG Naphta/NGL Nox Emission Level 50 ppm 100 ppm Max. heat rate Degradation, In kCal/kWh,with i) Water injection 100 50 ii) Steam injection 75 35 | DLN combustor specified. For other combustor Nox control effects as per OEM guarantees | As per design/guaranteed demonstrated values. |
|  |  | SCGT using conventional combustor (other than dry low Nox) and steam/water injection for Nox control, Gross Heat Rate shall be increased as under: Fuel N Gas/LNG naphta/NGL Nox Emission Level 50 ppm 100 ppm Max. heat rate Degradation, In kCal/kWh,with i) Water injection 70 50 | -do- | -do- |
| 6. | Degradation Factor formula as per B-2.5.2.1(A&B) Of CERC document | Applicable heat rate to be lower of the following two values:- (1.035 for CCGT and 1.0325 for SCGT)X Guaranteed Heat rate Base value as indicated in table above | Applicable heat rate to be lower of the following two values:- (1.035 for CCGT and 1.0325 for SCGT)X Guaranteed Heat rate Base value as indicated in table above | CCGT Gas firing – 12.45% Naptha firing- 14.95% HSDfiring- 15.95% SCGT Gas firing – 12.28 % |
| 7. | COD | As on PG test completion | Completion of trial run. | Completion of trial run. |