## Annexure-III 1 to 3
Annexure-III
SH 1/3
Pro-forma for furnishing Actual annual performance/operational data for the Hydro Electric generating stations for the 5-year period from 2012-13 to 2016-17
| Particulars |  | Units | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | Name of Company |  |  | NHPC LTD.
2 | Name of Station |  |  | TLDP-III Power Station
3 | Installed Capacity and Configuration |  | (MW) | 132
4 | Station Location |  | Under ground or Surface | Surface
5 | Type of Excitation System |  |  | Static
6 | Live Storage Capacity |  | (Million Cubic) | 7.077 | 7.077 | 7.077 | 7.077 | 7.077
7 | Rated Head |  | Metres | 21.34 M | 21.34 M | 21.34 M | 21.34 M | 21.34 M
8 | Head at Full Reservoir Level (FRL) |  | Metres | 26.2 M | 26.2 M | 26.2 M | 26.2 M | 26.2 M
9 | Head at Minimum Draw down Level (MDDL) |  | Metres | 24.52 M | 24.52 M | 24.52 M | 24.52 M | 24.52 M
10 | MW Capability at FRL |  | MW |  | 132 MW | 132 MW | 132 MW | 132 MW
11 | MW Capability at MDDL |  | MW |  | At present, it is not possible to run Units at EL 203 M
12 | Cost of spares :
12.1 | Cost of spares capitalized in books of accounts |  | (Rs. Lakhs) | - | Nil | Nil | 98.49 | 195.85
12.2 | Cost of spares included in the capital cost for the purpose of tariff |  | (Rs. Lakhs) | - | Nil | Nil | Nil | Nil
Period
13 | Generation :
13.1 | Actual Gross Generation at Generator Terminals |  | (MU) | 3.0484 | 191.54 | 393.7515 | 514.849 | 553.6666
13.2 | Actual Net Generation Ex-bus including free power |  | (MU) | 3.0484 | 188.5841 | 387.2005 | 508.6413 | 547.4983
13.3 | Scheduled generation Ex-bus including free power |  | (MU) |  | 185.8313 | 380.1655 | 496.1957 | 538.0207
14 | Actual Auxiliary Energy Consumption excluding colony consumption |  | (MU) |  | 2.9559 | 7.113 | 7.9925 | 8.8422
15 | Actual Energy supplied to Colony from the station |  | (MU) | - | NIL | NIL | NIL | NIL
16 | Average Declared Capacity (DC) during the year |  | (MW) | - | 33.23 | 72.29 | 88.77 | 89.54
Annexure-III
SH 2/3
| Period |  | Units | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
17 | Weighted Average duration of outages ( Unit-wise details)
17.1 | Scheduled outages |  | (Days) | - | 356.5431 | 179.707 | 60.7896 | 90.425
17.2 | Forced outages |  | (Days) | - | 585.8246 | 81.1279 | 11.4528 | 48.8021
18 | Cost of spares actually consumed |  | (Rs. Lakhs) | - | Nil | Nil | Nil | Nil
19 | Average stock of spares |  | (Rs. Lakhs) | - | Nil | Nil | 49.25 | 147.17
Month wise Design Energy
Month |  | Period | Design Energy as approved by CEA (MU) |  | Month | Period | Design Energy as approved by CEA (MU)
April |  | 1-10 | 6.9136 |  | October | 1-10 | 22.5381
|  | 11-20 | 8.7295 | 8.7295 |  | 11-20 | 23.6895 | 23.6895
|  | 21-30 | 14.4652 | 14.4652 |  | 21-31 | 24.5544 | 24.5544
May |  | 1-10 | 10.3721 | 10.3721 | November | 1-10 | 13.0258 | 13.0258
|  | 11-20 | 10.5934 | 10.5934 |  | 11-20 | 7.2738 | 7.2738
|  | 21-31 | 20.1551 | 20.1551 |  | 21-30 | 6.1975 | 6.1975
June |  | 1-10 | 19.027 | 19.027 | December | 1-10 | 8.7852 | 8.7852
|  | 11-20 | 29.047 | 29.047 |  | 11-20 | 8.0918 | 8.0918
|  | 21-30 | 28.758 | 28.758 |  | 21-31 | 6.349 | 6.349
July |  | 1-10 | 30.096 | 30.096 | January | 1-10 | 8.1288 | 8.1288
|  | 11-20 | 30.096 | 30.096 |  | 11-20 | 7.519 | 7.519
|  | 21-31 | 33.1056 | 33.1056 |  | 21-31 | 7.9196 | 7.9196
August |  | 1-10 | 30.096 | 30.096 | February | 1-10 | 6.0645 | 6.0645
|  | 11-20 | 30.096 | 30.096 |  | 11-20 | 6.0105 | 6.0105
|  | 21-31 | 33.1056 | 33.1056 |  | 21-28 | 4.7005 | 4.7005
September |  | 1-10 | 28.3668 | 28.3668 | March | 1-10 | 7.3595 | 7.3595
|  | 11-20 | 20.6031 | 20.6031 |  | 11-20 | 7.7183 | 7.7183
|  | 21-30 | 25.4967 | 25.4967 |  | 21-31 | 9.0222 | 9.0222
[5 empty] | Total |  | 594.0708
Storage Hydro plants shall also furnish actual monthly average peaking generation in MW achieved during the period 2012-13 to 2016-17 against the monthly average peaking capability approved by CEAas per following format:
Month |  | Expected Avg. of daily 3-hour peaking capacity as approved by CEA |  |  | Actual monthly average of daily 3-hour peaking (MW) for the period 2012-13 to 2016-17
April |  | 130.68 |  |  |  | 117.7403
May |  | 130.68 |  |  |  | 111.4009
June |  | 130.68 |  |  |  | 106.4333
July |  | 130.68 |  |  |  | 64.8937
August |  | 130.68 |  |  |  | 82.3306
September |  | 130.68 |  |  |  | 102.1445
October |  | 130.68 |  |  |  | 107.9463
November |  | 130.68 |  |  |  | 96.3861
December |  | 130.68 |  |  |  | 86.0081
January |  | 130.68 |  |  |  | 63.9717
February |  | 130.68 |  |  |  | 87.6904
March |  | 130.68 |  |  |  | 90.4966
Annexure III
SH 3/3
1 | List of beneficiaries/customers along with allocation by GoI including (allocation of unallocated share) / capacity as contracted should also be furnished separately for each generating station.
2 | Declared Capacity should be as per Regulation 31(3) of CERC Tariff Regulations for the period 2014-19 including month wise information may be furnished.
3 | Any relevant point or a specific fact having bearing on performance or operating parameters may also be highlighted or brought to the notice of the Commission.

## Annexure-IV
Annexure –IV
PLANT AVAILABILITY/SCHEDULED PLANT LOAD FACTOR ACHIEVED Generating company: NHPC LTD. Name of Generating station: TLDP-III Power Station Installed Capacity (MW) : 132 MW Normative Annual Plant Availability Factor (%) approved by Commission : 85%
Plant Availability Factor Achieved (%)
Month | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | Reasons for shortfall in PAF achieved vis-a-vis NAPAF
April | - | 83.7032 | 99.4202 | 97.8642 | 79.4052 | DURING 2013-14: 1. COMPLETE SHUTDOWN OF POWER STATION W.E.F 02-AUG-2013 TO 15-AUG-2013 DUE TO BANDH CALLED BY GJMM. 2. COMPLETE SHUTDOWN OF POWER STATION W.E.F 03-JAN-2014 TO 31-MAR-2014 FOR REPAIR WORKS AT DAM. 3. OUTAGE OF U#4 W.E.F 04-JUL-2013 TO 31-OCT-2013 FOR RECTIFICATION OF SHAFL SEAL LEAKAGE. | 117.7403
May |  | 65.757 | 98.9203 | 94.3576 | 81.9535 |  | 111.4009
June |  | 40.9226 | 94.7436 | 96.1977 | 93.919 |  | 106.4333
July |  | 18.4889 | 39.372 | 49.6616 | 91.1115 |  | 64.8937
August |  | 11.5525 | 54.8989 | 99.06 | 86.4955 |  | 82.3306
September |  | 22.1365 | 100.0026 | 100.5255 | 89.9908 |  | 102.1445
October |  | 40.5983 | 87.524 | 99.3562 | 102.9355 |  | 107.9463
November |  | 55.1347 | 37.1603 | 100.653 | 102.0814 |  | 96.3861
December |  | 72.7954 | 3.2337 | 86.2239 | 101.0101 |  | 86.0081
January |  | 7.3314 | 59.8894 | 74.1284 | 54.4628 |  | 63.9717
February |  | 0 | 97.8581 | 82.9085 | 87.6459 |  | 87.6904
March |  | 1.0861 | 94.4337 | 78.3495 | 103.133 |  | 90.4966
Annual |  | 32.5654 | 71.9624 | 88.2025 | 89.5072
DURING 2014-15: 1. COMPLETE SHUTDOWN OF POWER HOUSE W.E.F 13-JUL-2014 TO 12-AUG-2014. FOR REPAIR WORKS OF THE DAMAGED ROAD IN UPSTREAM SIDE. 2. COMPLETE SHUTDOWN OF POWER HOUSE W.E.F 15-NOV-2014 TO 12-JAN-2015 FOR RECTIFICATION WORKS OF GIS & LINE BREAKER .
Plant Load Factor Achieved (%)
Month | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | Reasons for shortfall in PLF achieved vis-a-vis Target PLF
April
May
June
July
August
September
October
November
December
January
February
March
Annual

## Annexure-XIX (TLDP-III)
Annexure-XIX
Name of the Utility |  | NHPC LTD.
Name of the Generating Station |  | TLDP-III Power Station
Station/ Stage/ Unit |  | 4x33 MW
Fuel Type (Coal/ Lignite/ Gas/ Liquid Fuel/ Nuclear/ Hydro | [7 empty] | Hydro
Capacity of Plant (MW) |  | 132 MW
COD |  | 2013-05-19
|  | 2004-05 | 2005-06 | 2006-07 | 2007-08 | 2008-09 | 2009-10 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | Plant Availability Factor (PAF) (%) | 2013-05-19 2004-05: Not Commissioned; 2013-05-19 2013-14: 32.5411; 2013-05-19 2014-15: 72.9534; 2013-05-19 2015-16: 88.188; 2013-05-19 2016-17: 89.5072
2 | Plant Load Factors (PLF) (%)
3 | Scheduled Energy (MU) | 2013-05-19 2004-05: Not Commissioned; 2013-05-19 2013-14: 185.8313; 2013-05-19 2014-15: 380.1655; 2013-05-19 2015-16: 496.1957; 2013-05-19 2016-17: 538.0207
4 | Scheduled Generation (MU)
5 | Actual Generation (MU) | 2013-05-19 2004-05: Not Commissioned; 2013-05-19 2012-13: 3.0484; 2013-05-19 2013-14: 191.54; 2013-05-19 2014-15: 393.7515; 2013-05-19 2015-16: 514.849; 2013-05-19 2016-17: 553.6666
6 | Quantum of coal consumption (MT) | 2013-05-19 2004-05: Not Applicable
7 | Value of coal (Rs. Lakh)
8 | Specific Coal Consumption (kg/kwh)
9 | Gross Calorific Value of Coal (Kcal/ Kg)
10 | Heat Contribution of Coal (Kcal/ kwh)
11 | Cost Of Specific Coal Consumption (Rs./Kwh) – Finally admitted by CERC
12 | Quantum of Oil Consumption (Lit.)
13 | Value of Oil (Rs. lakh)
14 | Gross calorific value of oil (kcal/lit)
15 | Specific Oil Consumption (ml/ kwh)
16 | Cost Of Specific Oil Consumption (Rs./Kwh) – Finally admitted by CERC
17 | Heat Contribution of Oil (Kcal/ kwh)
18 | Station Heat Rate (kcal/kwh)
19 | Auxiliary Energy Consumption (%) | 2013-05-19 2004-05: Not Commissioned; 2013-05-19 2013-14: 1.5; 2013-05-19 2014-15: 1.8; 2013-05-19 2015-16: 1.55; 2013-05-19 2016-17: 1.6
20 | Debt at the end of the year (Rs. Crore)
21 | Equity (Rs. Crore) | 2013-05-19 2013-14: 559.9291
22 | Working Capital (Rs. Crore) – finally admitted by CERC | 2013-05-19 2013-14: 6.6945
23 | Capital cost (Rs. Crore) – finally admitted by CERC | 2013-05-19 2013-14: 1866.4316
24 | Capacity Charges/ Annual Fixed Cost (AFC)
(a) Return on equity – pre tax (admitted by CERC)
| Absolute value | 2013-05-19 2013-14: 102.555
| Rate (%) | 2013-05-19 2013-14: 18.61%
(b) interest on Loan
| Absolute value | 2013-05-19 2013-14: 107.1195
| Rate (%) – Weighted Average Rate | 2013-05-19 2013-14: 9.509%
(c) Depreciation (finally allowed by CERC)
| Absolute value | 2013-05-19 2013-14: 92.1374
| Rate (%) | 2013-05-19 2013-14: 5.015%
(d) Interest on working Capital
| Absolute value | 2013-05-19 2013-14: 8.8037
| Rate (%) | 2013-05-19 2013-14: 13.2%
(e) Operation and maintenance cost (finally admitted by CERC)
| Absolute value | 2013-05-19 2013-14: 37.3132
Rate (%)
(f) Compensation Allowances | bar: 2013-05-19 2004-05
25 | AFC (Rs. Crore) | 2013-05-19 2013-14: 347.9288 | 582.248
26 | Energy Charge (Rs./Kwh) | 2013-05-19 2013-14: 2.9878
27 | Total tariff (Rs. Kwh) | 2013-05-19 2013-14: 5.9756
28 | Revenue realisation before tax (Rs. Crore) | 2013-05-19 2013-14: 114.0782; 2013-05-19 2014-15: 342.7394; 2013-05-19 2015-16: 343.7606; 2013-05-19 2016-17: 0.5695
29 | Revenue realisation after tax (Rs. Crore) #
30 | Profit/ loss before tax(Rs. Crore) | 2013-05-19 2013-14: -143.8767; 2013-05-19 2014-15: 95.249; 2013-05-19 2015-16: 86.88; 2013-05-19 2016-17: 95.4698
31 | DSM Generation (MU) | 2013-05-19 2013-14: 3.6792; 2013-05-19 2014-15: 7.1784; 2013-05-19 2015-16: 12.614; 2013-05-19 2016-17: 9.4571
32 | DSM Rate (Ps/Kwh)
33 | Revenue from DSM (Rs. Crore) | 2013-05-19 2013-14: 0.20437; 2013-05-19 2014-15: 1.1916; 2013-05-19 2015-16: 2.7465; 2013-05-19 2016-17: 1.6161
1. The data at Sl No. 20 to 27 has been filled based on CERC order dated 22.01.2015
2. The capital cost sl no. 23 & equity at sl no. 21 has been considered as closing equity & capital cost respectively as on 31st March of respective year.
3. The billing for the period 2014-19 is being carried out based on allowed AFC for 2013-14 grossed up with MAT rate.
4. # NHPC calculate Corporate Tax as a whole after considering all the admissible deductions, exemptions etc. as per Income Tax Act. Therefore unitwise calculation has not been made.
Note: Generating Companies are required to submit data for all generating stations.
This is a general format. Plants of different fuel users have to fill the cells as applicable to them. Tariff for the Hydro may be understood as composite tariff.
The data provided for the corresponding years need to mention as Actual or provisional.
Data for each Unit and Stage is required to be submitted in additional sheets as per the format.

## 2012-13 vs 2013-14
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC Ltd
Name of Power Station: TLDP III POWER STATION
Sl. No. | ITEMS | 2012-13 | 2013-14
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares |  | 5838419
0
2 | Repair & Maintenance |  | 0
2.1 | For Dam,Intake,WCS,De-silting chamber |  | 82460854
2.2 | For Power House and all other works |  | 32983410
| Sub-Total (Repair and Maintenance) | 0 | 115444264
0
3 | Insurance |  | 23052840
4 | Security Expenses |  | 31716608
0
5 | Administrative Expenses |  | 0
5.1 | Rent |  | 10653381
5.2 | Electricity charges |  | 19992427
5.3 | Travelling & Conveyance |  | 5432603
5.4 | Telephone, Telex & Postage (Communication) |  | 2954864
5.5 | Advertisement |  | 2608270
5.6 | Donation |  | 0
5.7 | Entertainment |  | 16050
0
| Sub-total (Administrative expenses) | 0 | 41657595
6 | Employee Cost |  | 0
6.1a | Salaries,wages & allow. -Project |  | 205492901
6.2 | Staff welfare expenses |  | 14718217
6.3 | Productivity Linked incentive |  | 3018709
6.4 | VRS-Ex-gratia |  | 9509225
6.5 | Ex-gratia |  | 0
6.6 | Performance related pay (PRP) |  | 8145312
| Sub-total (Employee Cost) | 0 | 240884364
7 | Loss of Store |  | 0
0
0
9.1 | Allocation of CO Office expenses |  | 118106766
0
10 | Others (Specify items) |  | 69370996
11 | Total (1 to 10) | 0 | 646071852
12 | Revenue /Recoveries |  | 12668973
13 | Net Expenses | 0 | 633402879
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 2013-14 vs 2014-15
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC Ltd
Name of Power Station: TLDP III POWER STATION
Sl. No. | ITEMS | 2013-14 | 2014-15 | Variance (%) | Reason
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 5838419 | 26558987 | 354.9% | Due to consumption of various high value spares such as MOOG VALVE, SYNTHETIC HIGH VOLTAGE INSULATING MAT etc which are not regular in nature and rectification of account head as per the various guidelines. | PROVIDE REASONS
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 82460854 | 38593457 | -53.2% | Expendture increased in FY 2013-14 due to rectification of GL Head consequent upon decapitalization of asset | PROVIDE REASONS
2.2 | For Power House and all other works | 32983410 | 49882157 | 51.23% | Expenditure increased in FY 2014-15 with respect to FY 2013-14 due to outsourcing of Preventing Annual Mainteannce of Generating Units and consumption of high value | PROVIDE REASONS
| Sub-Total (Repair and Maintenance) | 115444264 | 88475614
|  | 0 | 0
3 | Insurance | 23052840 | 30834255 | 33.75% | Mega insurance policy has been taken in 2014-15 and therefore expenditure increased.
4 | Security Expenses | 31716608 | 66704799 | 110.3% | Due to Induction of CISF on 01.09.2013 | PROVIDE REASONS
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 10653381 | 11823444 | 10.98% | Increase in Hiring expenses of vehicles in Post Capitalisation period.
5.2 | Electricity charges | 19992427 | 25958525 | 29.84%
5.3 | Travelling & Conveyance | 5432603 | 5791456 | 6.606% | NA
5.4 | Telephone, Telex & Postage (Communication) | 2954864 | 3400010 | 15.06% | Due to increase in Satellite Communication Expenses.
5.5 | Advertisement | 2608270 | 2975375 | 14.07% | Increase in tender Advertisement Cost.
5.6 | Donation | 0 | 0
5.7 | Entertainment | 16050 | 34502 | 115% | Since increase in expenditure in absolute terms is very nominal.
|  | 0 | 0
| Sub-total (Administrative expenses) | 41657595 | 49983312 | 19.99%
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 205492901 | 226297513 | 10.12% | Expenditure increases due to increase in Manpower, effect of annual increment and promotion, etc.
6.2 | Staff welfare expenses | 14718217 | 14849822 | 0.8942% | NA
6.3 | Productivity Linked incentive | 3018709 | 4493306 | 48.85% | Expenditure depend rate of PLI fixed by CO & nos of empolyees in the project
6.4 | VRS-Ex-gratia | 9509225 | 0 |  | No VRS paid in the FY 2014-15
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 8145312 | 13715606 | 68.39% | Expenditure depend upon the rating of NHPC, KPA and nos of empolyees in the project
| Sub-total (Employee Cost) | 240884364 | 259356247 | 7.668%
7 | Loss of Store | 0 | 645748 |  | NA
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 118106766 | 127176799 | 7.68% | NA
|  | 0 | 0
10 | Others (Specify items) | 69370996 | 44049551 | -36.5% | Expenditure decreases due to reduction in Expenditure on Compensatory afforestation / catchment area treatment and foreign exhange loss.
11 | Total (1 to 10) | 646071852 | 693785312
12 | Revenue /Recoveries | 12668973 | 117104341 | 824.3% | Recovery of LD and other penalties from Major Contractor.
13 | Net Expenses | 633402879 | 576680971
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 2014-15 vs 2015-16
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC Ltd
Name of Power Station: TLDP III POWER STATION
Sl. No. | ITEMS | 2014-15 | 2015-16 | Variance 2014-15 & 2015-16 | Reason
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 26558987 | 23862477 | -10.15% | Due to less consumption of spares in FY 2015-16 with respect of FY 2014-15.
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 38593457 | 26687147 | -30.85% | Expendture increased in FY 2014-15 due to additional Rectification works in spillway of Barrage of TLDP-III Power Station which was not in routine nature
2.2 | For Power House and all other works | 49882157 | 58360330 | 17% | Expenditure increased in FY 2015-16 with respect to FY 2014-15 due to various additional work like treatment of A&B Lines Wall at Primary Cooling Floor EL176.5 Mtr, Protection work of Gabion crate wall, construction of officer club cum training hall at Sector-F of TLD-III PS etc and consumption of high value spares which were not in routine nature.
| Sub-Total (Repair and Maintenance) | 88475614 | 85047477
|  | 0 | 0
3 | Insurance | 30834255 | 46094875 | 49.49% | In case of Mega Insurance Police 1. Increase in premium rates on account of deteriorating claim ratio as a result of loss due Fire incident at Uri-II Power Station and submergence of Chutak power Station in November 2014 and June 2015 respectively and other claims during policy period 2014-15 2. Increase in sum-insured due to increase in reinstatement cost of assets on Valuation. 3. Increase in the rate of Service Tax and WCT from 12.36% to 14% and 10.5% to 12.6% respectively. In case of CPM policy, Increase in Sum insured due to valuation of Assets, additional Construction equipment purchased and increase in premium rates & Service Tax/WCT rates as above.
4 | Security Expenses | 66704799 | 66206747 | -0.7467% | NA
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 11823444 | 13614254 | 15.15% | Due to increase in hiring expenses of vehicles.
5.2 | Electricity charges | 25958525 | 24576486 | -5.324% | NA
5.3 | Travelling & Conveyance | 5791456 | 4990438 | -13.83% | It includes the travelling and coveyance expenditure for tour which is based on organisational requirement.
5.4 | Telephone, Telex & Postage (Communication) | 3400010 | 4072449 | 19.78% | Due to increase in Satellite Communication Expenses.
5.5 | Advertisement | 2975375 | 4016449 | 34.99% | Increase in tender Advertisement Cost due to increase in no of R&M contracts in Post Capitalisation Period.
5.6 | Donation | 0 | 0
5.7 | Entertainment | 34502 | 34155 | -1.006%
|  | 0 | 0
| Sub-total (Administrative expenses) | 49983312 | 51304231 | 2.643%
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 226297513 | 233668462 | 3.257%
6.2 | Staff welfare expenses | 14849822 | 17874564 | 20.37% | Increase in Medical Expenditure of Staff has resulted into such a varaince. However, varaince overall employee cost is very less.
6.3 | Productivity Linked incentive | 4493306 | 4790521 | 6.615%
6.4 | VRS-Ex-gratia | 0 | 0
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 13715606 | 14912087 | 8.724%
| Sub-total (Employee Cost) | 259356247 | 271245634 | 4.584%
7 | Loss of Store | 645748 | 41199 | -93.62% | Provision for loss of store was created based on NRV and Cost valuation concepts as per Accounting Standard.
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 127176799 | 136802740 | 7.569%
|  | 0 | 0
10 | Others (Specify items) | 44049551 | 41450547 | -5.9%
11 | Total (1 to 10) | 693785312 | 722055927
12 | Revenue /Recoveries | 117104341 | 11610896 | -90.08% | No major recoveries made in this as per compared to Previous Year where LD was recovered from Major Contractor.
13 | Net Expenses | 576680971 | 710445031
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 2015-16 vs 2016-17
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC Ltd
Name of Power Station: TLDP III POWER STATION
Sl. No. | ITEMS | 2015-16 | 2016-17 | Variance 2015-16 & 2016-17 | Reason
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 23862477 | 19401492 | -18.69% | Due to less consumption of spares in FY 2016-17 with respect of FY 2015-16. | PROVIDE REASONS
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 26687147 | 25051663 | -6.128%
2.2 | For Power House and all other works | 58360330 | 65202440 | 11.72%
| Sub-Total (Repair and Maintenance) | 85047477 | 90254103
|  | 0 | 0
3 | Insurance | 46094875 | 47434220 | 2.906%
4 | Security Expenses | 66206747 | 85888406 | 29.73% | Due to wage revision fo Security Personnel. | PROVIDE REASONS
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 13614254 | 13141191 | -3.475% | Due to decrease in Rent of Land as Railway sidings were now being used by Other Projects. | PROVIDE REASONS
5.2 | Electricity charges | 24576486 | 25582255 | 4.092%
5.3 | Travelling & Conveyance | 4990438 | 6139969 | 23.03% | Due to increase in movement of employees for training programmes and other tours.
5.4 | Telephone, Telex & Postage (Communication) | 4072449 | 4148526 | 1.868%
5.5 | Advertisement | 4016449 | 1367548 | -65.95% | Reduction in Tender Cost due to lees no. of NITs
5.6 | Donation | 0 | 0
5.7 | Entertainment | 34155 | 43515 | 27.4% | Since increase in expenditure in absolute terms is very nominal.
|  | 0 | 0
| Sub-total (Administrative expenses) | 51304231 | 50423004 | -1.718%
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 233668462 | 286608662 | 22.66%
6.2 | Staff welfare expenses | 17874564 | 12458318 | -30.3% | Due to decrease in retired employee medical benefits provisioning as per Acturial Valuation.
6.3 | Productivity Linked incentive | 4790521 | 9512084 | 98.56% | Increase due to payment of arear of PLGI at revised rate from F.Y 2010-11 to F.Y 2013-14 and provision of PLGI for Q4 of FY 2016-17 made on revised pay
6.4 | VRS-Ex-gratia | 0 | 0
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 14912087 | 17892534 | 19.99% | Expenditure depend upon the rating of NHPC, KPA and nos of empolyees in the project
| Sub-total (Employee Cost) | 271245634 | 326471598 | 20.36%
7 | Loss of Store | 41199 | 0
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 136802740 | 276286534 | 102% | Corporate office expenditure is allocated to Units.
|  | 0 | 0
10 | Others (Specify items) | 41450547 | 44806928 | 8.097%
11 | Total (1 to 10) | 722055927 | 940966285
12 | Revenue /Recoveries | 11610896 | 12763320 | 9.925%
13 | Net Expenses | 710445031 | 928202965
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation