## Annexure I (1)
[8 empty] | Annexure –I |  | SH 1/4
Actual annual performance/operational data for the lignite based thermal generating stations for the 5-year period from 2012-13 to 2016-17
Sl.No | Particulars | Units | 2012-13 |  | 2013-14 |  | 2014-15 |  | 2015-16 | 2016-17
1 | Name of Company |  | NLC India Limited
2 | Name of Station/ Pit head or Non- Pit head |  | Barsingsar Thermal Power Station, Barsingsar - 334 402, Rajasthan, Pit Head Power Station
3 | Installed Capacity and Configuration | MW | 250 MW (2 x 125 MW)
4 | Rated Steam Parameters (Also state the type of Steam turbine and Boiler) |  | Main Steam: 126Kg/Cm2, 535°C Reheat Steam: 29.58 Kg/cm2, 535°C TURBINE : Tandem compound, straight condensing ,single reheat with two cylinder - HP/IP combined & double flow LP turbine BOILER : Single Drum,natural circulation,single reheat,radiant,dry bottom,balanced draft CFBC type
5 | Type of BFP |  | Electrical Driven
6 | Circulating water system |  | Closed Cycle
7 | Any other Site specific feature |  | 2 Nos Steam Generators are of Circulating Fluidised Bed Combustion Technology
8 | Fuels :
8.1 | Primary Fuel : |  | Lignite
8.1.1 | Annual Allocation or/and Requirement | Million Ton | 1.3 | 1.55 |  | 1.65 |  | 1.766 |  | 1.69
8.1.2 | Sources of supply/ procurement along with contracted quantity and grade of coal |  | Pit Head Power Station
8.1.2. | FSA | MT | NA | NA |  | NA |  | NA |  | NA
8.1.2. | Imported | MT | NA | NA |  | NA |  | NA |  | NA
8.1.2. | Spot Market/e-auction | MT | NA | NA |  | NA |  | NA |  | NA
8.1.3 | Transportation Distance of the station from the sources of supply | km | Pit Head Power Station
8.1.4 | Mode of Transport |  | Conveyor
8.1.5 | Maximum Station capability to stock primary fuel | Days & MT | 2.5 Lac Tonnes including Mines Storage
8.1.6 | Maximum stock maintained for primary fuel | MT | 95946.18 |  | 136840.22 |  | 137686 |  | 148532.25 | 148985.388
8.1.7 | Minimum Stock maintained for primary fuel | MT | 74390 |  | 74390 |  | 74390 |  | 74390 | 74390
8.1.8 | Average stock maintained for primary fuel | MT | 85168.09 |  | 105615.11 |  | 106038 |  | 111461.125 | 111687.694
8.2 | Secondary Fuel : |  | LDO & HFO
8.2.1 | Annual Allocation / Requirement | KL | 1506.25 |  | 1917.5 |  | 1643 |  | 1752 | 1752
8.2.2 | Sources of supply |  | IOCL, HPCL, New Delhi.
8.2.3 | Transportation Distance of the station from the sources of supply | KM | 1000 KM
8.2.4 | Mode of Transport |  | ROAD
8.2.5 | Maximum Station capability to stock secondary fuels | KL | 1200 (LDO + HFO)
8.2.6 | Maximum Stock of secondary oil actually maintained | KL | LDO : 510.30 |  |  |  | HFO : 540.42
8.2.7 | Minimum Stock of secondary oil actually maintained | KL | LDO : 241.80 |  |  |  | HFO : 471.00
8.2.8 | Average Stock of secondary oil actually maintained | KL | LDO : 361.49 |  |  |  | HFO : 488.38
9 | Cost of Spares :
9.1 | Cost of Spares capitalized in the books of accounts | (Rs. Lakh) | -
9.2 | Cost of spares included in capital cost for the purpose of tariff | (Rs. Lakh) | -

## Annexure I (2)
Annexure –I | [8 empty] | SH 2/4
Actual annual performance/operational data for the lignite based thermal generating stations for the 5-year period from 2012-13 to 2016-17
| Period |  |  |  | 2012-13 | 2013-14 | 2014-15 | 2015-16 |  | 2016-17
10 | Generation :
10.1 | -Actual Gross Generation at generator terminals |  |  | MU | 1280.496 | 1437.923 | 1380.656 | 1285.567 |  | 1463.256
10.2 | -Actual Net Generation Ex-bus |  |  | MU | 1114.074 | 1252.7058 | 1190.2515 | 1102.682 |  | 1271.0437
10.3 | -Scheduled Generation Ex-bus |  |  | MU | 1113.309 | 1253.9138 | 1197.386 | 1115.3992 |  | 1297.5688
11 | Average Declared Capacity (DC) |  |  | MW | 128 | 145 | 137.28 | 127.4 |  | 148.76
12 | Actual Auxiliary Energy Consumption excluding colony consumption |  |  | MU | 162.3678 | 181.2874 | 186.5256 | 179.2154 |  | 188.2565
13 | Actual Energy supplied to Colony from the station |  |  | MU | 2.017 | 2.118 | 2.136 | 1.838 |  | 2.143
14 | Primary Fuel : |  |  | Lignite fed from Barsingsar Pithead mine
14.1 | Consumption : |  |  |  | 1245504 | 1479367.77 | 1351631.101 | 1212757.4741 |  | 1412681.79
2014-01-01 | Domestic coal | From linked mines |  | MT | 1245504 | 1479367.77 | 1351631.101 | 1212757.4741 |  | 1412681.79
|  | Non-linked mines |  | MT | NA | NA | NA | NA |  | NA
2014-01-02 | Imported coal* |  |  | MT | NA | NA | NA | NA |  | NA
2014-01-03 | Spot market/e-auction coal* |  |  | MT | NA | NA | NA | NA |  | NA
14.2 | Gross Calorific Value (GCV) :
2014-02-01 | Domestic Coal (Lignite) |  | (As Billed) | kCal/kg | NA | NA | NA | NA |  | NA
|  |  | (As Received) | kCal/kg | 2668 | 2613.8891 | 2646.9847 | 2706.3591 |  | 2631.4268
|  |  | ( As Fired ) | kCal/kg | NA | NA | NA | NA |  | NA
2014-02-02 | Imported Coal |  | (As Billed) | kCal/kg | NA | NA | NA | NA |  | NA
|  |  | (As Received) | kCal/kg | NA | NA | NA | NA |  | NA
2014-02-03 | Spot market/e- auction coal |  | (As Billed) | kCal/kg | NA | NA | NA | NA |  | NA
|  |  | (As Received) | kCal/kg | NA | NA | NA | NA |  | NA
2014-02-04 | Weighted Average Gross Calorific value (As Billed) |  |  | (kCal /Kg) | NA | NA | NA | NA |  | NA
2014-02-05 | Weighted Average Gross Calorific value (As Received) |  |  | (kCal /Kg) | 2668 | 2613.8891 | 2646.9847 | 2706.3591 |  | 2631.4268
2014-02-06 | Weighted Average Gross Calorific value (As Fired) |  |  | (kCal /Kg) | NA | NA | NA | NA |  | NA
14.3 | Price of coal :
2014-03-01 | Weighted Average Landed price of Domestic coal |  |  | (Rs/MT) | 1039.64 | 941.38 | 1074.3 | 1087.16 |  | 1392.11 | 1039.64 | 941.38 | 1074.3 | 1087.16 | 1392.11
2014-03-02 | Weighted Average Landed Price of Imported coal |  |  | (Rs/MT) | - | - | - | - |  | -
2014-03-03 | Weighted Average Landed Price of Spot market/e-auction coal |  |  | (Rs/MT) | - | - | - | - |  | -
2014-03-04 | Weighted Average Landed Price of all the Coals |  |  | (Rs/MT) | 1039.64 | 941.38 | 1074.3 | 1087.16 |  | 1392.11
14.4 | Blending : |  |  | % and MT ( of the total coal consumed ) | NA | NA | NA | NA |  | NA
2014-04-01 | Blending ratio of imported coal with domestic coal |  |  | Equivalent to domestic coal | NA | NA | NA | NA |  | NA
2014-04-02 | Proportion of e-auction coal in the blending |  |  |  | NA | NA | NA | NA |  | NA
14.5 | Actual Average Coal stock maintained |  |  | Days and MT | 85168.09 | 105615.11 | 106038 | 111461.125 |  | 111687.694
14.5 | Actual Transit & Handling Losses for coal/Lignite |  |  | (%) | NA | NA | NA | NA |  | NA
2014-05-01 | Pit- Head Station
14.5.1.1 | Transit loss from linked mines |  |  |  | NA | NA | NA | NA |  | NA
14.5.1.2 | Transit loss from non-linked mines including e-auction coal mines. |  |  |  | NA | NA | NA | NA |  | NA
14.5.1.3 | Transit loss of imported coal |  |  |  | NA | NA | NA | NA |  | NA
2014-05-02 | Non-Pit Head station
14.5.2.1 | Transit loss from linked mines |  |  |  | NA | NA | NA | NA |  | NA
14.5.2.2 | Transit loss from non-linked mines including e-auction coal mines. |  |  |  | NA | NA | NA | NA |  | NA
14.5.2.3 | Transit loss of imported coal |  |  |  | NA | NA | NA | NA |  | NA
15 | Secondary Fuel Oil : ( If more than one fuel usedthen give details of all the fuels separately)
15.1 | Consumption |  |  | (KL) | 722.23 | 1108.87 | 870.713 | 1269.22 |  | 1130.623
15.2 | Weighted Average Gross Calorific value (As received) |  |  | (kCal/Lit.) | 9156.036 | 9144.3322 | 8922.6409 | 8782.9753 |  | 8913.2562
15.3 | Weighted Average Price |  |  | (Rs per KL) | 60998 | 66726 | 59770 | 43391 |  | 36842
15.4 | Actual Average stock maintained |  |  | ( KL) | 1075.39 | 878.5467 | 877.2739 | 834.6983 |  | 808.9606
15.4.1 | LDO |  |  | (KL) | 457.76 | 372.6783 | 380.2739 | 355.0317 |  | 337.9606
15.4.2 | HFO |  |  | (KL) | 546 | 505.8683 | 497 | 479.6667 |  | 471
16 | Weighted average duration of outages( unit-wise details):
16.1 | Planned Outages |  |  | (Days) | 36.3738 | 72.9783 | 70.0778 | 62.6701 |  | 113.9431
16.2 | Forced Outages |  |  | (Days) | 221.275 | 115.2379 | 93.4792 | 123.4827 |  | 91.2313
16.3 | Number of tripping |  |  | Nos. | 57 | 39 | 25 | 28 |  | 17
16.4 | Number of start-ups:
2016-04-01 | Cold Start-up |  |  | Nos. | 11 | 18 | 16 | 21 |  | 15
2016-04-02 | Warm Start-up |  |  | Nos. | 34 | 17 | 4 | 2 |  | 0
2016-04-03 | Hot start-up |  |  | Nos. | 12 | 4 | 5 | 5 |  | 2
17 | NOx , SOx ,and other particulate matter emission in :
17.1 | Design value of emission control equipment |  |  | mg/Nm3 | 150 | 150 | 150 | 150 |  | 150

## Annexure I (3)
[8 empty] | Annexure –I |  | SH 4/4
Actual annual performance/operational data for the lignite based thermal generating stations for the 5-year period from 2012-13 to 2016-17
|  | Period |  |  | 2012-13 | 2013-14 | 2014-15 |  | 2015-16 | 2016-17
17 |  | NOx , SOx ,and other particulate matter emission in :
17.1 |  | Design value of emission control equipment |  | mg/Nm3 | 150 | 150 | 150 |  | 150 | 150
17.2 |  | Actual emission (SPM) | UNIT - I | mg/Nm3 | 88 | 62 | 50 |  | 86 | 76
|  |  | UNIT - II |  | 88 | 57 | 50 |  | 88 | 69
|  | SOx | UNIT - I | mg/Nm3 | - | 181 | 270 |  | 262 | 348
|  |  | UNIT - II |  | - | 183 | 204 |  | 229 | 247
|  | NOx | UNIT - I | mg/Nm3 | - | 131 | 268 |  | 264 | 325
|  |  | UNIT - II |  | - | 130 | 210 |  | 228 | 232
19 |  | Detail of Ash utilization % of fly ash produced |  | Qty Produced | 198234 | 264312.66 | 220418 |  | 198818.45 | 226682
19.1 |  | Conversion of value added product (Cement & Bricks Industry) |  | (%) | 75.35 | 79.4347 | 86.5274 |  | 80.3981 | 79.8833
19.2 |  | For making roads &embarkment |  | (%) | Nil | Nil | Nil |  | Nil | Nil
19.3 |  | Land filling(Mixed with OB in mines filling) |  | (%) | 24.65 | 20.5653 | 13.4726 |  | 19.6019 | 20.1167
19.4 |  | Used in plant site in one or other form or used in some other site |  | (%) | Nil | Nil | Nil |  | Nil | Nil
19.5 |  | Any other use , Please specify |  | Qty. and Usage | Nil | Nil | Nil |  | Nil | Nil
20 |  | Cost of spares actually consumed |  | ( Rs. Lakh) | 275.47 | 591.02 | 711.8 |  | 615.03 | 1199.46
21 |  | Average stock of spares |  | (Rs. Lakhs) | 382.33 | 596.345 | 1126.81 |  | 1669.11 | 2109.155
22 |  | Number of employees deployed in O&M
22.1 |  | - Executives |  | Nos. | 219 | 194 | 190 |  | 180 | 181
22.2 |  | - Non Executives |  | Nos. | 43 | 38 | 57 |  | 80 | 79
22.3 |  | - Corporate office |  | - | 41 | 28 | 33 |  | 26 | 26
23 |  | Man-MW ratio |  | Man/MW | 1.212 | 1.04 | 1.12 |  | 1.144 | 1.144
Note :- * Not applicable to lignite based thermal power station.
** Due to Royalty rivision from 10/05/2012
Note:
1. BTPS beneficiaries along with allocation - Ajmer Discom - 28 %, Jaipur Discom - 40 %, Jodhpur Discom - 32 % .

## Annexure V(C) (hidden)
Annexure-V (C)
Name of Generating Station …………………… Stage……..
COD of Units/Station ………………………………
Details of expenditure incurred from Compensation Allowance and Special Allowance during Tariff Period 2009-14
FY Year | Add- cap allowed by the Commis sion under the provision of Regulati on 9(2) | Compens atory allowance allowed by the Commission, if any | Special allowance allowed by the Commiss ion, if any | Details of Asset/Work wise Capitalisation based on the Expenditure allowed by the Commission in the tariff period 2009-14 | [5 empty] | Capitali sation done which has not been claimed/ allowed in the tariff | Total Addi tion durin g the year | Total Additi on during the year as per duly audit ed Sche dule of Fixed Asset | Variati on if any to be reconciled /justified.
|  |  |  | Capitalisation out of add cap allowed under Regulation 9(2) |  | Capitalisati on out of Compensati on allowance in the stations wherever applicable |  | Capitalisa tion out of Special Allowance allowed in the stations where applicable
|  |  |  | Asset / work | (Rs.lakh) | Asset/ work | (Rs. lakh) | Asset/ work | (Rs. lakh)
2009 -10
2010 -11
2011 -12
2012 -13
2013 -14
Note :Similar Details shall be furnished for the period 2014-15 to 2016-17 under Tariff Regulations, 2014

## Annexure VIII (hidden)
Annexure-VIII
DETAILS OF O & M EXPENSES (At Corporate Level/Regional Level)
Name of the Company:
( Rs. In Lacs)
Sl.No. | ITEM | unit | 2012-13 | 2013-14 |  | 2014-15 | 2015-16 |  | 2016-17
1 | 2 |  | 3 | 4 |  | 5 | 6 |  | 7
(A) | Breakup of corporate expenses (Aggregate at Company level)
1 | - Employee expenses:
1.1 | -Salaries, wages and allowances
1.2 | -Staff welfare expenses
1.3 | -Productivity linked incentive
1.4 | - Expenditure on VRS
1.5 | -Ex-gratia
1.6 | -Performance related pay( PRP)
2 | Administrative Expenses:
2.1 | - Repair and maintenance
2.2 | - Training and Recruitment
2.3 | - Communication
2.4 | - Traveling & Conveyance
2.5 | - Rent
2.6 | - Others (Specify items)
Sub - Total (Administrative
3 | Security
4 | Donations
5 | Provisions
6 | Others (specify items)
7 | Total (1 to 6)
8 | Less recoveries (if any)
9 | Net Corporate Expenses (Aggregate)
(B) | Allocation of Corporate Expenses to
1 | Power Generation/Transmission O&M
2 | Project management/Projects under Construction
3 | RLDC and ULDC
4 | Consultancy Business
5 | Telecommunication Business
6 | Any other
Note: Heads indicated above are illustrative. Generating companies or the transmission utilities may furnish the allocations in different functional activities suited to their company.
(C) | Allocation of Corporate Expenses relating to functional activity of power Generation or the transmission to various generating stations or the transmission region/systems as the case may be.
1 | Generating station 1 / Transmission Region 1
2 | Generating station 2 / Transmission Region 2 ……..
Note:
Year-wise audited actual O&M expenses submitted for the period 2012-13 to 2016-17 should be clearly indicating the following:
(i)Explanation / Justification for year to year variation of more than (±) 10% in any head of O&M expenses.
(ii) Details of expenditure under the head "Others".
(iii) Details of the amount indicated under the head "Revenues/Recoveries".
(iv) Details of arrears and prior period adjustments included in the data for the period 2012-13 to 2016-17, if
any, pertaining to period prior to the year 2012-13 should be mentioned separately in the following format:
Sl. No. | Year during the period 2012-17 in which arrear/ prior period adjustments have been made | Year to which this arrear and prior period adjustment pertains |  |  | Amount of arrear/ prior period adjustment (Rs. in lakh)
(v) Separately furnish the details of abnormal expenses, if any.
(vi) Future provisions pertaining to period beyond 2016-17 made in the employee cost or any other head during
2012-13 to 2016-17 towards wage revision/arrears or for any other reason shall be provided separately.
(vii) Details of Regional level expenses to be provided separately giving methodology of allocation of Regional
expenses.

## Annexure XVI(A) (hidden)
Annexure XVI A
Details of Incidental Expenses during Construction (IDEC) with break-up for the
Generating stations for which COD is declared after 1.4.2014
Sl. No. | Item-wise details of expenditure with break-up | Expenditure as on SCOD | Expenditure as on actual COD of unit/ station | Time Overrun

## ANNEXURE IV
Annexure –IV
PLANT AVAILABILITY/SCHEDULED PLANT LOAD FACTOR ACHIEVED Generating company: NLC INDIA LIMITED Name of Generating station: Installed Capacity (MW) :Barsingsar Thermal Power Station (250 MW) Normative Annual Plant Availability Factor (%) approved by Commission : First 3 years from COD 75 % and 80 % for following years.
Plant Availability Factor Achieved (%)
Month | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | Reasons for shortfall in PAF achieved vis-a-vis NAPAF
April | 47.6177 | 37.8797 | 49.4428 | 75.1765 | 40.7062 | Forced Outages & Partial loading in both Units. Consequent to the modification carried out in both the Boilers in F.Y. 2016-17 planned outages, PAF % has improved.
May | 40.4637 | 77.5558 | 53.7672 | 54.1549 | 24.3256
June | 71.9433 | 70.2009 | 53.8573 | 32.5763 | 48.254
July | 61.7927 | 57.7126 | 43.6892 | 50.3675 | 34.5107
August | 34.8718 | 39.2642 | 64.3109 | 56.2541 | 72.6086
September | 18.6339 | 47.8576 | 64.5829 | 67.245 | 91.1779
October | 68.9488 | 54.8308 | 74.0518 | 66.9521 | 86.6533
November | 58.6249 | 77.4949 | 62.6196 | 66.1681 | 83.8776
December | 77.0084 | 97.7101 | 77.075 | 60.918 | 62.2208
January | 63.4858 | 83.7909 | 74.593 | 56.5253 | 97.1894
February | 85.8711 | 87.5213 | 64.4858 | 63.7313 | 98.8603
March | 80.0704 | 73.6729 | 78.6352 | 57.4021 | 87.6321
Annual | 58.9997 | 67.0527 | 63.4807 | 58.9152 | 68.7888
Scheduled Plant Load Factor Achieved (%)
Month | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | Reasons for shortfall in PLF achieved vis-a-vis Target PLF
April | 47.6177 | 37.7169 | 49.4428 | 74.7945 | 40.693 | Forced Outages & Partial loading in both Units. Consequent to the modification carried out in both the Boilers in F.Y. 2016-17 planned outages, Scheduled PLF % has improved.
May | 40.4637 | 75.0355 | 53.7672 | 54.0239 | 24.1888
June | 71.9433 | 66.9879 | 53.8573 | 32.4804 | 48.254
July | 61.7927 | 55.2056 | 43.6892 | 49.8403 | 34.3368
August | 34.8718 | 39.2568 | 63.2644 | 55.4453 | 72.6086
September | 18.6339 | 47.2338 | 63.278 | 67.245 | 91.1779
October | 68.9488 | 54.8308 | 74.0518 | 66.6494 | 86.6533
November | 58.6249 | 77.4949 | 62.6196 | 66.1681 | 83.8776
December | 77.0084 | 97.0696 | 77.075 | 60.918 | 62.1558
January | 63.4858 | 83.6236 | 74.593 | 56.5253 | 95.2963
February | 82.9175 | 87.4383 | 64.0883 | 63.7313 | 98.6856
March | 79.9865 | 73.3302 | 78.0954 | 57.3226 | 86.6329
Annual | 58.7659 | 66.1923 | 63.2083 | 58.7194 | 68.4968

## ANNEXURE VC
Annexure-V (C)
Name of Generating Station : BTPS 250 MW
COD of Units/Station:
Details of expenditure incurred from Compensation Allowance and Special Allowance during Tariff Period 2009-14
FY Year | Add- cap allowed by the Commis sion under the provisio n of Regulati on 9(2) | Compens atory allowance allowed by the Commissi on, if any | Special allowanc e allowed by the Commiss ion, if any | Details of Asset/Work wise Capitalisation based on the Expenditure allowed by the Commission in the tariff period 2009-14 | [5 empty] | Capitali sation done which has not been claime d/ allowed in the tariff | Total Addi tion during the year | Total Additi on durin g the year as per duly audit ed Sche dule of Fixed Asset | Variati on if any to be recon ciled /justifi ed.
|  |  |  | Capitalisation out of add cap allowed under Regulation 9(2) |  | Capitalisation out of Compensati on allowance in the stations wherever applicable |  | Capitalisa tion out of Special Allowanc e allowed in the stations where applicable
|  |  |  | Asset / work | (Rs.la kh) | Asset /work | (Rs. lak h) | Ass et/ wo rk | (Rs. lak h)
2009-10
2010-11
2011-12 |  |  |  | Asset comm. Prior to COD = 1873.15 Laks and Asst. Addn allow =137.38 Laks | 2010.53 |  |  |  |  | 0 | 2010.53 | 2010.53
2012-13 |  |  |  | Discharge of Liab | 0 |  |  |  |  | 2082.15 | 2082.15 | 2082.15
2013-14 |  |  |  | Asst allw Rs 324.84 Laks and discharge of Lia 6465.63Lak | 324.84 |  |  |  |  | 1028.86 | 1353.7 | 1353.7
2014-15 | [9 empty] | 0 | - | -
2015-16 | [9 empty] | 0 | - | -
2016-17 | [9 empty] | 0 | - | -
Note :Similar Details shall be furnished for the period 2014-15 to 2016-17 under Tariff Regulations, 2014
For the years 2014-17, audited schedule for assets will be furnished in due course.

## ANNEXURE VIA
Annexure VI(A)
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
(To be filled for each of the Thermal /Hydro Generating Station)
Name of the Company: NLC India Limited
Name of the Power Station : BARSINGSAR TPS
(Rs. In Lakhs)
Sl.No. | ITEM | MIS | CTB | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | 2 |  |  | 3 | 4 | 5 | 6 | 7
(A) | Breakup of O&M expenses :
1 | Consumption of Stores and Spares | Stores & Spares |  | 275.4696 | 591.0232 | 1053.3234 | 718.0334 | 1565.3779
2 | Repair and Maintenance | Outside Services |  | 1005.6369 | 1753.381 | 1375.9121 | 1328.3772 | 2016.3188
3 | Insurance | Other Expenditure | Insurance | 39.6809 | 48.2145 | 76.7931 | 61.8007 | 39.0721
4 | Security (normal)
4.1 | Additional Security it any on the advise of Govt. Agency/ Statutory Authorityf |  |  | 548.75 | 570.6458 | 625.2907 | 669.8678 | 834.9827
5 | Water Charges | Internal Services |  | 185.8251 | 151.0276 | 341.5262 | 103.0034 | 149.7739
6 | Administrative Expenses : | Other Expenditure
6.1 | - Rent | Other Expenditure
6.2 | - Electricity Charges | Other Expenditure
6.3 | - Traveling and conveyance | Other Expenditure |  | 64.8768 | 84.8086 | 79.7866 | 122.5223 | 53.2966
6.4 | - Communication expenses | Other Expenditure |  | 0.49721 | 0.74179 | 0.76029 | 0.36748 | 0.3163
6.5 | - Advertising | Other Expenditure
6.6 | - Foundation laying and inauguration | Other Expenditure
6.7 | - Donations | Other Expenditure
6.8 | - Entertainment | Other Expenditure |  | 7.42 | 7.665 | 9.13 | 7.5 | 1.38
6.9 | -Filing Fees | Other Expenditure
| Sub-Total (Administrative Expenses) | Other Expenditure |  | 72.794 | 93.2154 | 89.6769 | 130.3897 | 54.9929
7 | Employee Cost | Remuneration & Benefits
7.1 | -Salaries, wages and allowances | Remuneration & Benefits | Emp. Remuneration | 3424.3816 | 3028.3601 | 3568.9672 | 2964.0717 | 3538.0491
7.2 | -Staff welfare expenses | Remuneration & Benefits | Welfare Expenses | 111.4164 | 60.8672 | 48.8109 | 51.0578 | 91.9882
7.3 | -Productivity linked incentive | Remuneration & Benefits | Bonus & Incentives | 284.4972 | 172.5916 | 203.4329 | 599.3177 | 261.9952
7.4 | - Expenditure on VRS | Remuneration & Benefits |  | 0 |  |  |  | 0.46
7.5 | -Ex-gratia | Remuneration & Benefits | Superannuation Benefits ,CPF & Gratuity | 513.7629 | 593.3374 | 702.6244 | 647.7421 | 758.4433
7.6 | -Performance related pay (PRP) | Remuneration & Benefits
| Sub-Total (Employee Cost) | Remuneration & Benefits |  | 4334.0581 | 3855.1563 | 4523.8354 | 4262.1892 | 4650.9357
8 | Loss of store
9 | Provisions | Other Expenditure | Provisions
10 | Prior Period Adjustment , if any
11 | Corporate office expenses allocation | Common Charges | Common Charges | 338.9115 | 336.9169 | 405.7534 | 399.921 | 444.4478
12 | - Others (Specify items) |  |  | 276.6161 | 237.6251 | 228.8012 | 218.5699 | 28.4945
14 | Total (1 to 12) |  |  | 7077.7422 | 7637.2058 | 8720.9123 | 7892.1523 | 9784.3964
14.1 | Revenue/ Recoveries, if any | Recovery -Others | Recovery | 36.0067 | 61.9139 | 32.133 | 68.8891 | 1744.2414
15 | Net Expenses |  |  | 7041.7355 | 7575.2919 | 8688.7793 | 7823.2632 | 8040.155
16 | Capital spares consumed not included in (A) (1) above and not claimed /allowed by Commission for
Notes:
NOTES TO ANNEXURE VIA
1. Corporate expenses have been allocated as furnished in Annexure VIII
2. Reasons for variation in excess of 10%: Increase of 1. Salary & Wages 2.Stores and Spares 3.Repir & Maintenance Expenditure
3.O & M Expenses, which includes Lignite Handling System expenditure have been reconciled with audited Balance Sheet.
4.Break up of employees expenditure furnished below
5.Break up of Staff welfare expenses furnished
6.No.Abnormal expenses
7.No of Employees for VRS: NIL
8.Details of water charges furnished in Annexure VIC
|  |  |  | 7041.7355 | 7575.2919 | 8688.7793 | 7823.2632 | 8040.155
|  |  |  | 0 | 0 | 0 | 0 | 0
| Other Expenses-Breakup |  |  | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
| Internal Services |  |  | 0 | 0 | 0 | 0 | 0
| Canteen Expenses | [5 empty] | 23.283 | 93.6987
| Entry Tax |  |  | 18.5623 | 30.2178 | 55.8898 | 26.0598 | 24.9899
| Inland Tours |  |  | 12.5441 | 10.1247 | 5.0679 | 4.6054 | 8.0391
| Licence Fees |  |  | 8.7619 | 11.4724 | 10.5732 | 9.8664 | 14.4167
| Tender Advertisement |  |  | 25.7199 | 29.9603 | 34.4171 | 48.5895 | 78.0398
| Personnel-Stipends |  |  | 16.7632 | 29.58 | 38.3229 | 29.6516 | 23.6188
| Official Language |  |  | 7.6158 | 1.0729 | 0.53784 | 0.65379 | 0.79333
| National Festival |  |  | 1.5053 | 1.5745 | 1.3447 | 1.5515 | 1.5194
| Lorry Freight |  |  | 10.6393 | 0.34779 | 0.017 | 0 | 0
| Arbitration Charges |  |  |  |  | 31.385 | 2.48 | 14.5989
| DRE -Others |  |  |  | 87.7776 | 0 | 0 | 0
| Barsingsar Expansion Transferred | [6 empty] | -306.0941
| Pheripheral Expenses |  |  | 64.9043 | 0 | 0 | 0 | 0
| Miscellaneous Expenses |  |  | 109.6 | 35.4971 | 51.2458 | 71.8289 | 74.874
| Total |  |  | 276.6161 | 237.6251 | 228.8012 | 218.5699 | 28.4945
| Check |  |  | 0 | 0 | 0 | 0 | 8.5265e-14
| Ex-Gratia Breakup |  |  | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
| Gratuity |  |  | 105.5761 | 59.1159 | 73.2542 | 0.97235 | 95.984
| CPF |  |  | 249.8775 | 250.235 | 294.9744 | 303.9237 | 314.5293
| Superannuation Benefits |  |  | 158.3093 | 283.9866 | 334.3957 | 342.846 | 347.93
| Total |  |  | 513.7629 | 593.3374 | 702.6244 | 647.7421 | 758.4433
|  |  |  | 0 | 0 | 0 | 0 | 0
| IUSS-Canteen |  |  | 0
| EL Encashment |  |  | 66.0789 | 145.9499 | 146.4292 | 222.2861 | 94.8074

## Welfare Expenses
STAFF WELFARE EXPENSES BTPS
Rs. In Lakh
Gl Code | DETAILS | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
4326 | T.A.SUPERANNUATION. | 0.9844 |  |  | 1.0709 | 8.2279
4325 | T.A.MEDICAL | 0.09984 | 0.13819 | 0.0324
4313 | SCHOLARSHIPS TO WARD | 0 | 0 | 0 | 0 | 0
4314 | SAFETY PERSONAL PROT |  |  | 1.1016
4308 | REIMBURSMENT OF MEMB | 0.015 | 0.038 |  | 0.025 | 0.05
5514 | MISC EXPENSES-CULTUR | 0.12 | 0.35138 | 0.3987 | 3.7816 | 0.67591
4302 | MEDICAL REFERRAL PAY | 88.1853 | 34.6339 | 22.5611 | 16.4551 | 6.8906
4306 | EMPLOYEES WELFARE EX |  |  | 0.97848
3257 | MEDICINES |  |  |  | 0.29352
3258 | LOCAL PURCHASE-MEDIC |  | 1.1674 | 5.42 | 6.6167 | 14.8566
4310 | L T A | 0.00849
4315 | EMPLOYEES WELFARE EX | 0.327 |  | 0.00335 | 0.00335 | 2.4466
4311 | EMPLOYEES WELFARE EX | 5.686 | 13.2462 | 6.3 | 13.56 | 5.7
4303 | EMPLOYEES WELFARE EX | 15.9404 | 11.2921 | 12.0152 | 9.2517 | 53.0915
4321 | EMP. WELFARE EXP. PA | 0.05 |  |  |  | 0.05
|  | 111.4164 | 60.8672 | 48.8109 | 51.0578 | 91.9891
|  | 111.4164 | 60.8672 | 48.8109 | 51.0578 | 91.9882
|  |  | 0 | 0 | 0 | -0.001

## ANNEXURE VI C
Annexure-VI (C)
DETAILS OF WATER CHARGES
Name of the Company: NLC INDIA LIMITED
Name of the Power Station and Stage/Phase : Barsingsar Thermal Power Station
Sl.No. | ITEM | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | 2 | 3 | 4 | 5 | 6 | 7
(A) | Plant
1 | Type of Plant | Thermal Power Station / Lignite fired
2 | Type of Cooling Tower | Induced Draft
3 | Type of Cooling Water System | Closed Circuit Circulating Water System
4 | Any Special Features which may increase/reduce water consumption | - | - | - | - | -
(B) | Quantum of Water : ( Cubic Meter)
5 | Contracted Quantum | - | - | - | - | -
6 | Allocation of Water | 45 cusec | 45 cusec | 45 cusec | 45 cusec | 45 cusec
7 | Actual water Consumption in M3 (ft3/35.315) | 4787174.2885 | 5758041.5687 | 5478752.9945 | 5935690.4998 | 6026954.8351
8 | Actual water Consumption in Cu. ft. | 169059060 | 203345238 | 193482162 | 209618910 | 212841910
8 | Rate of Water Charges per 1000 ft3 in ` | 20 | 20 | 20 | 20 | 20
9 | Water Charges paid in ` | 3381181 | 4066905 | 3869643 | 4192378 | 4256838
10 | Other charges/Fees , if paid as part of Water Charges - Water cess in ` | 513238 | 584859 | 619104 | 613384 | 650537
11 | Total water Charges Paid ` | 3894419 | 4651764 | 4488747 | 4805762 | 4907375
Note on E18: Author: Mar'12-Feb'13
Note on E19: Author: May'12-Mar'13
Note on F18: Author: Mar'13-Feb'14
Note on F19: Author: Apr'13-Mar'14
Note on G18: Author: Mar'14-Feb'15
Note on G19: Author: Apr'14-Mar'15
Note on H18: Author: Mar'15-Feb'16
Note on H19: Author: Apr'15-Mar'16
Note on I18: Author: Mar'16-Feb'17
Note on I19: Author: Apr'17-Mar'17

## ANNEXURE VID
Annexure VI (D)
DETAILS OF CAPITAL SPARES
Name of the Company: NLC INDIA LIMITED
Name of the Power Station :Barsingsar Thermal Power Station (250 MW)
( In Rs.)
Sl.No. | ITEM | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | 2 | 3 | 4 | 5 | 6 | 7
(A) | Details of Capital Spares in opening Stock
1 | Non metallic expansion joint for Cyclone and flue gas duct | 0 | 909450.39 | 1956324.5 | 582961 | 582961
2 | Non metallic expansion joint for Flue gas duct and and back pass | 0 | 586846.01 | 586846.01 | 586846.01 | 586846.01
3 | SERVO VALVE ST 10-4 | 0 | 176311.28 | 176311.28 | 176311.28 | 0
4 | HP Element for service air compressor ZR 500 | 0 | 1387994 | 1387994 | 1387994 | 1387994
5 | Input Shaft for Intermediate conveyor Gear box | 0 | 289993 | 289993 | 289993 | 289993
6 | ASH INTAKE VALVE COMPLETE ASSEMBLY. | 0 | 133965.63 | 133965.63 | 133965.62 | 979910.5
7 | FRP Blades for CT Fan | 0 | 0 | 563739 | 0 | 1441034.38
8 | Fluid Coupling 500 SDFC | 0 | 0 | 140058 | 140058 | 140058
9 | Gear Box (B2SF-160) for Belt Feeder of Stacker Cum Reclaimer | 0 | 0 | 1172124 | 1172124 | 1172124
10 | Intermediate conveyor gearbox for SCR | 0 | 0 | 2460762 | 2460762 | 2460762
11 | Oil cooler for GA200W compressor- 7.5bar | 0 | 0 | 481343.08 | 240671.54 | 240671.54
12 | After cooler for GA200W compressor- 7.5bar | 0 | 0 | 361006.92 | 361006.92 | 361006.92
13 | Oil gun assembly for start up burner. | 0 | 0 | 197738.31 | 197738.31 | 0
14 | Complete set of chain assembly for TRC. | 0 | 0 | 0 | 1980582 | 0
15 | Complete set of chain assembly for Lignite Extraction feeder. | 0 | 0 | 0 | 1895734 | 0
16 | Non metallic expansion joint for Between combustor and cyclone | 0 | 0 | 0 | 1557999 | 1686745
17 | Cartridge assembly for HFO pressurising pump model no:T3ST 70/46. | 0 | 0 | 0 | 434861 | 434861
18 | Cartridge Assembly for LDO Pressurising pump model no:T3S T45/46. | 0 | 0 | 0 | 237832.4 | 0
19 | MOT Centrifuge- Major service kit | 0 | 0 | 0 | 203969.98 | 203969.98
20 | MOT Centrifuge-Inlet pipe with parting disc | 0 | 0 | 0 | 471241.91 | 471241.91
21 | Rexroth Axial Piston Pump-Control Oil Tank. | 0 | 0 | 0 | 178453.76 | 178453.76
22 | HP BYPASS QUICK STROKING DEVICE SSB 10. | 0 | 0 | 0 | 244697.72 | 244698
23 | HP BY PASS SYSTEM SERVO VALVE (MAIN -BP) ST 10 -63. | 0 | 0 | 0 | 207213 | 414426.4
24 | HP BYPASS SPARE- AXIAL PISTON | 0 | 0 | 0 | 173400 | 173400
25 | DMCW . BOOSTER PUMP(Hor. Split Case Pump).PUMP SHAFT. | 0 | 0 | 0 | 109001.54 | 109001.54
26 | Top Shaft sleeve for Circulating Water Pump | 0 | 0 | 0 | 112901.79 | 112901.79
27 | Imp.shaft sleeve for Circulating Water Pump | 0 | 0 | 0 | 118592.29 | 118592.29
28 | Rubber Bearing for Circulating Water Pump | 0 | 0 | 0 | 107972.91 | 107972.91
29 | Main oil pump- EBFP | 0 | 0 | 0 | 356028 | 356028
30 | Auxiliary Lub Oil Pump for EBFP | 0 | 0 | 0 | 383836 | 383836
31 | EBFP SPARE- BALANCE DRUM BUSHING | 0 | 0 | 0 | 100580.85 | 100580.85
32 | Resilient coupling 127S GBM Make or equivalent for BCN-18A/B | 0 | 0 | 0 | 269279.9 | 269279.9
33 | Resilient coupling 126S GBM Make or equivalent for BCN-1A,BCN-7A/B | 0 | 0 | 0 | 182784 | 182784
34 | Resilient coupling 125S GBM Make or equivalent for BCN-11A/B,BCN-19A/B,BCNLS-1 | 0 | 0 | 0 | 140760 | 140760
35 | Resilient coupling 125S GBM Make or equivalent for BCN-4A/B | 0 | 0 | 0 | 140760 | 140760
36 | Roller Shaft Assembly for Roller Screen | 0 | 0 | 0 | 2063765 | 2063765
37 | DRIVE PULLEY OF SIZE: DIA 1024 X 1200MM X16T | 0 | 0 | 0 | 327930 | 327930
38 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 824 X 1400MM X16T | 0 | 0 | 0 | 560280 | 560280
39 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 824 X 1200MM X16T | 0 | 0 | 0 | 372394.48 | 372394.48
40 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 524 X 1400MM X12T | 0 | 0 | 0 | 262926.52 | 262926.52
41 | TAKE-UP PULLEY OF SIZE : DIA 824 X 1400MM X16 MM T | 0 | 0 | 0 | 414359.69 | 414359.69
42 | TAKE-UP PULLEY OF SIZE: DIA 654 X 1200MM X 12MM T | 0 | 0 | 0 | 205773.47 | 205773.47
43 | TAKE-UP PULLEY OF SIZE: DIA 824 X 1200MM X12 MM T | 0 | 0 | 0 | 255838.64 | 255838.64
44 | TAKE-UP PULLEY OF SIZE: DIA 524 X 1200MM X12 MM T | 0 | 0 | 0 | 191260.2 | 191260.2
45 | SDFC 450 Fluid coupling assembly | 0 | 0 | 0 | 125491 | 125491
46 | HAND OPERATED 4 INCH CCS WCB 2500 CLASS GATE VALVE. | 0 | 0 | 0 | 139067.86 | 0
47 | NRV SIZE: 4" CCS VALVE WCB SWING CHECK TYPE CLASS RATING 2500. | 0 | 0 | 0 | 218754.14 | 0
48 | Oil Separator for GA 200 W | 0 | 0 | 0 | 140692.15 | 140692.15
49 | Mechanical seal Ebil make,Type:H75/65 (Pump 45KW) | 0 | 0 | 0 | 389025.74 | 389025.74
50 | Mechanical seal Ebil make,Type:H75/40 (Pump 22KW) | 0 | 0 | 0 | 110896.07 | 110896.07
51 | Complete set of chain assembly for DCC | 0 | 0 | 0 | 0 | 1112262
52 | Screw set (AISI 410) of LDO decanting pump . | 0 | 0 | 0 | 0 | 351436.22
53 | Safety Relief Valve for jack oil system size 3/4"X 1". | 0 | 0 | 0 | 0 | 182106
54 | AUXILIARY LUB OIL PUMP FOR BOILER FEED PUMP | 0 | 0 | 0 | 0 | 323830
55 | Complete Mechanical Seal for Boiler Feed Pump DE | 0 | 0 | 0 | 0 | 181444.01
56 | Complete Mechanical Seal for Main Boiler Feed Pump NDE | 0 | 0 | 0 | 0 | 186261.71
57 | Complete Mechanical Seal for Booster Pump DE of Feed Pump | 0 | 0 | 0 | 0 | 101358.8
58 | Complete Mechanical Seal for Booster Pump NDE of Feed Pump | 0 | 0 | 0 | 0 | 101358.8
59 | Thrust Pad set for Bearing 5 SLT of CEP Model EN7H32 | 0 | 0 | 0 | 0 | 397500.5
60 | Journal pad set for Bearing 5 SLT of CEP Model EN7H32 | 0 | 0 | 0 | 0 | 358919.5
61 | Butterfly Valve 800 NB | 0 | 0 | 0 | 0 | 276206
62 | Bevel Gear Pair for Cooling Tower Fan Gear Box. | 0 | 0 | 0 | 0 | 541711.8
63 | Second Stage Wheel for Cooling Tower Fan Gear Box. | 0 | 0 | 0 | 0 | 135645.98
64 | Drive Sheave for Toothed Double Roll Crusher | 0 | 0 | 0 | 0 | 366265.52
65 | Roller Shaft for Primary Roller Screen | 0 | 0 | 0 | 0 | 973446.12
66 | Main Drive Shaft for Flip Flow Screen | 0 | 0 | 0 | 0 | 217281.75
67 | Thrust Rod System for Flip Flow Screen | 0 | 0 | 0 | 0 | 118517.21
68 | Hydraulic Pump Complete P6S-2R1C-9A2-B00-0A1-M2-07704 | 0 | 0 | 0 | 0 | 1373848
69 | Non- Magnetic DRIVE PULLEY OF SIZE: DIA 824 X 1200MM X16T | 0 | 0 | 0 | 0 | 353735.8
70 | Non magnetic DRIVE PULLEY OF SIZE: DIA 1024 X 1200X16MM T | 0 | 0 | 0 | 0 | 586500
71 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 654 X 1200MM X12T | 0 | 0 | 0 | 0 | 242066
72 | TAIL PULLEY (MOUNTED ON BEARINGS )OF SIZE:DIA 524X1400MMX16T(SCR) | 0 | 0 | 0 | 0 | 130305
73 | TAKE PULLEY OF SIZE: DIA 524 X 1200MM X16T(SCR) | 0 | 0 | 0 | 0 | 138363
74 | DISCHARGE PULLEY(MOUNTED ON BEARINGS)OF SIZE: DIA1024X1200MMX20T | 0 | 0 | 0 | 0 | 445944
75 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 654 X 1200MMX20T | 0 | 0 | 0 | 0 | 214607.6
76 | DRIVE PULLEY OF SIZE: DIA 654 X 1200MMX20T(SCR) | 0 | 0 | 0 | 0 | 183600
77 | DRIVE PULLEY OF SIZE: DIA 524 X 1400MM X16T(SCR) | 0 | 0 | 0 | 0 | 127131.78
78 | TAIL PULLEY (MOUNTED ON BEARINGS )OF SIZE:DIA654X1200MMX16T(SCR) | 0 | 0 | 0 | 0 | 191821.2
79 | BEND PULLEY (MOUNTED ON BEARINGS)OF SIZE:DIA824X1200MMX20T(SCR) | 0 | 0 | 0 | 0 | 344056.2
80 | SNUB PULLEY(MOUNTED ON BEARINGS)OF SIZE:DIA424X1200MMX16.7T(SCR) | 0 | 0 | 0 | 0 | 138536.4
81 | BEND PULLEY (MOUNTED ON BEARINGS)OF SIZE:DIA524X1200MMX16T(SCR) | 0 | 0 | 0 | 0 | 164464.8
82 | Input shaft with pinion & key for H3-280 Ratio 23.016:1 | 0 | 0 | 0 | 0 | 133489.27
83 | Input shaft with pinion & key for H3-280 Ratio 34.984:1 | 0 | 0 | 0 | 0 | 133489.27
84 | Input shaft with pinion & key for H3-315 Ratio 22.433:1 | 0 | 0 | 0 | 0 | 197900
85 | Input shaft with pinion & key for H3-400 Ratio 28.4:1 | 0 | 0 | 0 | 0 | 326096
86 | Input shaft with pinion & key for H3-500 Ratio 28.4:1 | 0 | 0 | 0 | 0 | 540282.46
87 | 570 PST Coupling Set With Essential accessories | 0 | 0 | 0 | 0 | 688207.99
88 | Fluid coupling SDFC 410 assembly | 0 | 0 | 0 | 0 | 102483
89 | Horizontal centrifugal pump for transferring Degassed water. | 0 | 0 | 0 | 0 | 267220.39
90 | Top Shaft with sleeve for Raw water Pump | 0 | 0 | 0 | 0 | 147779.93
91 | Line Shaft with its sleeve for Raw water Pump. | 0 | 0 | 0 | 0 | 414234.52
92 | Bearing sealing ring, Part No: HY11390131083 | 0 | 0 | 0 | 0 | 0
93 | Labyrinth ring for bearing shell Part No: HY31390131116 | 0 | 0 | 0 | 0 | 0
94 | Generator fan blades TE, Part No: HY9316103002 | 0 | 0 | 0 | 0 | 0
95 | Generator fan blades EE, Part No: HY9316103010 | 0 | 0 | 0 | 0 | 0
96 | Adjusting steel for bearing pedestal, Part No: HY31390131118 | 0 | 0 | 0 | 0 | 0
97 | Generator Bearing insulation. Part No: HY1390131020 | 0 | 0 | 0 | 0 | 0
98 | Rotork Actuator Type K30G0A | 0 | 0 | 0 | 0 | 0
99 | Rotork Actuator Type K150F10A | 0 | 0 | 0 | 0 | 0
100 | Make:E/R ,Num.Dir.IDMTL 3O/C+1E/F Highset Relay,Type:ARGUS 2 | 0 | 0 | 0 | 0 | 0
101 | Motor Protection Relay,Type:AMV2-1A, P&B MAKE | 0 | 0 | 0 | 0 | 0
102 | Feeder Protection Relay, Type -AFV2-1A, P&B MAKE | 0 | 0 | 0 | 0 | 0
103 | ABT Energy meter for feeders | 0 | 0 | 0 | 0 | 0
104 | L&T Make:CN-CS-1250H type Breaker. | 0 | 0 | 0 | 0 | 0
105 | Out door radio modem unit for 25Mbps | 0 | 0 | 0 | 0 | 0
106 | PACKAGE PROJECT FOR SUPPLY, ERECTION, COMMISSION AND OPERATION OF CAAQMS | 0 | 0 | 0 | 0 | 0
107 | DM Transmitter Model: 1056-01-20-32-AN+PH+Conductivity sensor | 0 | 0 | 0 | 0 | 0
108 | Guided Wave Radar Level Transmitter for Measuring SILO LEVEL. | 0 | 0 | 0 | 0 | 0
109 | Single acting smart positioner for drain valves as per spec | 0 | 0 | 0 | 0 | 0
110 | DPU 4F Primary Module- MODULE NO: 69230D401B, TYPE: PDP401 | 0 | 0 | 0 | 0 | 0
111 | Prop. Directional Valve, Type: G631-XXXXX-H-75-J-O-F-M-4-V-B-Q | 0 | 0 | 0 | 0 | 0
112 | DUAL SIESMIC MONITOR MAKE:SHINKAWA, MODEL: VM-5U-221110-000-001-0 | 0 | 0 | 0 | 0 | 0
113 | Communication between IAC/SAC and main DCS. | 0 | 0 | 0 | 0 | 0
114 | 415 V,145 KW,TEFC SQUIRREL CAGE INDUCTION MOTOR . | 0 | 0 | 0 | 0 | 375232
115 | AUMA Actuator Model SA30A90. | 0 | 0 | 0 | 0 | 155254.5
116 | Fan Transformer 3-phase 500-690VAC | 0 | 0 | 0 | 0 | 120104.85
117 | Fan for framesize g,h and j, Part for Siemens Make VFD Unit. | 0 | 0 | 0 | 0 | 162659.28
118 | ABT METER READING INSTRUMENT FOR L&T ABT METERS | 0 | 0 | 0 | 0 | 0
119 | Fan Transformer 3 phase 380-480 VAC, 50/60 Hz | 0 | 0 | 0 | 0 | 103061.14
120 | 400Volts, 75KW, Frame 280S, 4P, Motor for Bucket Wheel of SCR | 0 | 0 | 0 | 0 | 453079.99
121 | 400Volts, 22KW, Frame 180L, 4P, Motor for Slew of SCR | 0 | 0 | 0 | 0 | 112782.03
122 | 400Volts, 55KW, Frame 250M, 4P, Motor for Boom Conveyor of SCR | 0 | 0 | 0 | 0 | 377196.98
123 | Commulating Choke for SCR | 0 | 0 | 0 | 0 | 160051.5
124 | Convertor for SCR | 0 | 0 | 0 | 0 | 976518.04
125 | VACCUME CONTACTOR ,3TF69 44-0C,110V AC,make:Siemens. | 0 | 0 | 0 | 0 | 204750.15
126 | 415Volts, 75kW, 6pole, Frame 315S motor for RWP | 0 | 0 | 0 | 0 | 259781
127 | 110KW,415V,4 Pole,ND315S,Delta connection,Hydrant pump Motor. | 0 | 0 | 0 | 0 | 476410
128 | ID FanMotor, 690 V, 800 KW, 8 Pole Horizondal mounted Cage motor | 0 | 0 | 0 | 0 | 0
129 | 37Kw Motor,415V,2Pole,Conn:Delta,Fr:200L-Fire BoosterPump Motor | 0 | 0 | 0 | 0 | 118489
130 | Out door radio modem unit for 50Mbps | 0 | 0 | 0 | 0 | 0
131 | ONLINE OXYGEN ANALYSER AS PER TECHNICAL SPECIFICATIONS | 0 | 0 | 0 | 0 | 0
132 | Nafion dryer Make Perma pure Model: PD-100T-24MKA as per spec | 0 | 0 | 0 | 0 | 0
133 | DCS Engineer Work Station as per spec. | 0 | 0 | 0 | 0 | 0
134 | Main PC Control circut Card for Spider Control,ver 4.2.1,rev:R2D | 0 | 0 | 0 | 0 | 0
135 | Combox(Gateway MK5),Part no: 2230006800 | 0 | 0 | 0 | 0 | 0
136 | Housing Vibration Module, MODEL NO: 3500/42-01-00 | 0 | 0 | 0 | 0 | 576872.78
137 | DUAL SIESMIC MONITOR MAKE:SHINKAWA, MODEL: VM-5U-921110-000-001-0 | 0 | 0 | 0 | 0 | 0
138 | VM-5 SERIES INSTRUMENT RACK MAKE: SHINKAWA, MODEL: VM-5W1-0 | 0 | 0 | 0 | 0 | 0
139 | HYDRAULIC DEAD WEIGHT TESTER AS PER SPECIFICATIONS | 0 | 0 | 0 | 0 | 0
140 | Electronic Water Drain for SAC part no. 8102042630 | 0 | 0 | 227139.97 | 0 | 0
141 | LIGNITE BUNKER WEIGHT CALIBRATION UNIT AS PER SPEC | 0 | 0 | 0 | 0 | 0
142 | LIGNITE BUNKER WEIGHING INDICATORS AS PER SPEC | 0 | 0 | 0 | 0 | 0
143 | Flexible connector for Equipment complete set-2500A | 0 | 0 | 0 | 179485.05 | 179485.05
144 | Flexible connector for Equipment complete set-1600A | 0 | 0 | 0 | 116743.47 | 116743.47
145 | MOP/LOP(AC) 37KW Motor | 0 | 0 | 0 | 125766 | 125766
146 | AUMA Actuator Model No SAR12B45 | 0 | 0 | 0 | 0 | 0
147 | AUMA Actuator whole assembly Type SA15AF32+Epac . | 0 | 0 | 0 | 0 | 0
148 | Auma actuator whole assembly model SA12E125+TBG. | 0 | 0 | 0 | 0 | 0
149 | AUMA Actuator model SA50-E-90 . | 0 | 0 | 0 | 140019.57 | 140019.57
150 | Gear Box for actuator SA50-E-90 . | 0 | 0 | 0 | 148318.16 | 148318.16
151 | LIMITORQUE MAKE ELECTICAL ACTUATOR MODEL NO. SMB-2-60/4 | 0 | 0 | 0 | 1389073 | 1389073
152 | 245 KV,triple pole, Centre Post Rotating Double Break Isolators | 0 | 0 | 0 | 244794.03 | 244794.03
153 | Snubber Board | 0 | 0 | 0 | 0 | 0
154 | ARECA CONTROLLER WITH FIRING CARD | 0 | 0 | 0 | 0 | 0
155 | 6.6kV 415kW 3Phase Squirrel Cage Induction Motor Frame TS500L2. | 0 | 1876679 | 0 | 1650000 | 1650000
156 | Stall Torque motor; SBS -125B4 ; Torque: 9.7NM for SCR | 0 | 0 | 0 | 571898.83 | 571898.83
157 | Stall Torque motor; SBS -100B4 ; Torque: 4.3NM | 0 | 0 | 0 | 397728.18 | 397728.18
158 | 6.6KV Grade Slip Ring Assembly for PCRD | 0 | 0 | 0 | 116259.01 | 116259.01
159 | 1.1KV Grade Slip Ring Assembly for CCRD | 0 | 0 | 0 | 177447.96 | 177447.96
160 | BTS2000 BUS TRANSFER SYSTEM MAIN MODULE | 0 | 0 | 0 | 0 | 0
161 | 760KW,6.6KV CWP MOTOR | 0 | 0 | 0 | 0 | 0
162 | 55 kW motor,415v,4Pole, Fr:D280S - CT Fan motor | 0 | 0 | 0 | 219000 | 219000
163 | Quantar Repeater | 0 | 0 | 0 | 0 | 0
164 | 415V, 160KW, 315L, 4Pole, Motor for Fly Ash/Bed Ash Compressor | 0 | 0 | 0 | 449553 | 449553
165 | 6.6KV, 185KW, 315F, 4Pole Motor for Fly Ash Stg 2 Compressor | 0 | 0 | 0 | 1325600 | 1325600
166 | RA#5 SIEMENS SITRANS probe LU Transmitter 7M5221-2BA11 | 0 | 0 | 0 | 171232.39 | 171232.39
167 | GUIDED WAVE RADAR LEVEL TR. | 0 | 0 | 0 | 0 | 0
168 | Flow meter for Circulating water forebay makeup water. | 0 | 0 | 0 | 0 | 0
169 | Flow meter for Boiler blow down (Intermediate blow down). | 0 | 0 | 0 | 0 | 0
170 | DM Conductivity Transmitter Model: 1056-01-22-30-AN +P/N 23820-00 | 0 | 0 | 0 | 0 | 0
171 | LPG Pilot Gas Ignitor ZA1- 150 P/K0K5M | 0 | 0 | 0 | 1423421 | 0
172 | RA#3 compressor Local opertor panel for ZR-37,GA160W,GA200W. | 0 | 0 | 0 | 0 | 0
173 | CPU 360 MODULE MAKE :GE MODEL NO: IC693CPU360 | 0 | 0 | 0 | 131080.34 | 131080.34
174 | GENIUS BUS CONTROLLER MAKE:GE,MODEL NO: IC693BEM331 | 0 | 0 | 0 | 126113.82 | 126113.82
175 | Siemens PLC, MONOMODE PROFIBUS OLM G12-1300 | 0 | 0 | 0 | 302919.37 | 302919.37
176 | Siemens PLC,CP1613 FOR Industrial Ethernet Communication | 0 | 0 | 0 | 208324.63 | 208324.63
177 | Siemens PLC,Communication processor CP 341-1,(POINT TO POINT LINK) | 0 | 0 | 0 | 110808.74 | 110808.74
178 | Siemens PLC, Y-LINK | 0 | 0 | 0 | 0 | 0
179 | Siemens PLC - Function Module , FM350-2 COUNTER in JNT & screen | 0 | 0 | 0 | 118079.31 | 118079.31
180 | PLC HMI Operator\Engineer work station(OWS\EWS) as per spec. | 0 | 0 | 0 | 0 | 0
181 | LIMITORQUE MAKE ELECTICAL ACTUATOR MODEL NO. SMB-3-150/4 | 0 | 0 | 1829321 | 1829321 | 1829321
182 | BFP SCOOP MOTOR ACTUATOR ABB MAKE MODEL -RHD250 | 0 | 0 | 0 | 0 | 0
183 | BFP SCOOP CONTROL SUPPLY UNIT ABB MAKE MODEL -EBN853 | 0 | 0 | 0 | 0 | 0
184 | Current Transformer for Inter Bus Transformers | 0 | 0 | 1382399.17 | 1382399.17 | 1382399.17
185 | Current Transformer for GTs and Feeders. | 0 | 0 | 1164802.83 | 1164802.83 | 1164802.83
186 | ED7470400311 DIGITAL AVR DC-DC SUPPLY MODULE | 0 | 0 | 0 | 0 | 0
187 | ED7470400141 AVR FIRING &CONTROL MODULE | 0 | 0 | 0 | 0 | 0
188 | ED7470400133 AVR CPU MODULE | 0 | 0 | 0 | 0 | 0
189 | CN 9090389300 PULSE FINAL STAGE | 0 | 0 | 0 | 0 | 0
190 | ED7470400290 16 CHANNEL BINARY OUT PUT MODULE | 0 | 0 | 0 | 0 | 0
191 | ED7470400168 DAVR INT GEN MODULE | 0 | 0 | 356983.95 | 356983.95 | 356983.95
192 | ED7470400281 DAVR I/O MODULE | 0 | 0 | 359682.65 | 359682.65 | 359682.65
193 | CN9090433503 PULSE COUP STAGE MODULE | 0 | 0 | 200773.52 | 200773.52 | 200773.52
194 | ED9090334114,AC/DC-DC CONVERTOR MODULE | 0 | 0 | 0 | 0 | 0
195 | CN9090110704 PULSE SUPERVISION MODULE | 0 | 0 | 156809.39 | 0 | 0
196 | ED7470400206 DAVR 16 CHANNEL O/P MDL | 0 | 0 | 124824.59 | 124824.59 | 124824.59
197 | SA0653980205,AC ISOLATOR 3 POLE WITH MICRO SWITCH | 0 | 0 | 234195.85 | 234195.85 | 234195.85
198 | 3 PH, 6.6 KV, 180 KW, B3, 4 P, S1, IP 55, S.C. IND. MOTOR | 0 | 0 | 954678 | 954678 | 954678
199 | 415kV, 75kW 3Phase Squirrel Cage Induction Motor, Frame 280M | 0 | 0 | 226936.5 | 226936.5 | 226936.5
200 | 415kV,90kW, 3Phase Squirrel Cage Induction Motor, Frame 315S | 0 | 0 | 278654.25 | 278654.25 | 278654.25
201 | 415kV, 55kW 3Phase Squirrel Cage Induction Motor, Frame 280S | 0 | 0 | 195405 | 195405 | 195405
202 | 415kV,160 kW, 3Phase Squirrel Cage Induction Motor, Frame 355L | 0 | 0 | 509528.25 | 509528.25 | 509528.25
203 | Siemens make ACB 800amps for stacker cum reclaimer. | 0 | 0 | 178205.41 | 178205.41 | 178205.41
204 | GE 800 A Spectronic ACB with LMZ7 | 0 | 0 | 232316 | 232316 | 232316
205 | Durag Make Flame Scanner Unit, Model: D-LE-603-UA-P. | 0 | 160541 | 0 | 0 | 0
206 | Durag Make Flame Control Unit, Model-D-UG 660 -115A-420 | 0 | 0 | 0 | 0 | 0
207 | KELTRON Pneumatic Actuator Model No.C0608 252239 for SUB SA | 0 | 0 | 179050.99 | 179050.99 | 179050.99
208 | KELTRON Pneumatic Actuator Model No.C0816 352239 for CombustorSAD | 0 | 0 | 195529.01 | 195529.01 | 195529.01
209 | Pneumatic Actuator for Sec. Air IGV, Keltron, C1216442239 | 0 | 0 | 218646.71 | 218646.71 | 218646.71
210 | PFT ,Indigenous Equivalent to CCI ,make:MASS ModelMG-10+4K | 0 | 0 | 0 | 0 | 0
211 | BFP SCOOP PFT ABB MAKE PART NO 764975 | 0 | 0 | 219114.67 | 219114.67 | 219114.67
212 | MID VALUE SELECTOR MODULE ED69229S901A | 0 | 0 | 429578.68 | 429578.68 | 429578.68
213 | 1 OF 3 I/P SELECTION MODULE ED69229S902A FOR TURBINE-DCS | 0 | 0 | 515111.06 | 515111.06 | 515111.06
214 | POSITION MEASUREMENT MODULE ED69229S910A FOR TURBINE-DCS | 0 | 0 | 461024.7 | 461024.7 | 461024.7
215 | POSITION CONTROL MODULE ED69229S914A FOR TURBINE DCS | 0 | 0 | 396036.56 | 396036.56 | 396036.56
216 | Antivirus server for DCS network | 0 | 0 | 0 | 0 | 0
217 | GE PLC Series 90-30 ETHERNET INTERFACE TCP/IP MODULE, IC693CMM321 | 0 | 0 | 0 | 0 | 0
218 | GE PLC Series 90-30 Genius Bus Controller,IC693BEM331. | 0 | 0 | 122274.51 | 122274.51 | 122274.51
219 | GE PLC Rx3i Ethernet Module IC695ETM001,used at AHS PLC,SILO. | 0 | 0 | 111951.83 | 111951.83 | 111951.83
220 | Regulator ELECTRONIKON IIID for SAC 1900071032. | 0 | 0 | 151002.94 | 0 | 0
221 | REGULATOR for SAC part no. 1900071082 | 0 | 0 | 134135.55 | 134135.55 | 134135.55
222 | ALARM UNIT for SAC part no. 1089045770 | 0 | 0 | 235998.78 | 235998.78 | 235998.78
223 | Regulator ELECTRONIKON IIID for IAC 1900071032 | 0 | 0 | 149537.92 | 0 | 0
224 | Rotork Actuator Type K1000F16A | 0 | 174301.41 | 174301.41 | 174301.41 | 174301.41
225 | Rotork Actuator type K300F14E | 0 | 0 | 0 | 0 | 0
226 | Rotork Actuator type K600F14A | 0 | 328445.73 | 328445.73 | 328445.73 | 328445.73
227 | Rotork Actuator type K300F14A | 0 | 0 | 0 | 0 | 0
228 | Rotork Actuator type K500G3A | 0 | 162694.63 | 162694.63 | 162694.63 | 162694.63
229 | E+H Liquicap Level Transmitter for Turbine Main Oil Tank | 0 | 101120.5 | 101120.5 | 101120.5 | 101120.5
230 | Level control unit for Bunker Level, Endress+Hauser Make | 0 | 109250.55 | 0 | 0 | 0
231 | Ultrosonic Level Probe for Bunker Level, Make: Endress+Hauser | 0 | 213361.45 | 0 | 0 | 0
232 | DVC-6010 AD, Smart Positioner: Thum Adapter, Make Fisher | 0 | 258794 | 258794 | 258794 | 0
233 | SMART POSITIONER FOR MASONEILAN CONTROL VALVE | 0 | 0 | 0 | 0 | 0
234 | PI servo amplifier, Make: MOOG,Model G122-829-001 | 0 | 346800 | 346800 | 346800 | 346800
(B) | Details of Capital Spares procured during the year
1 | Non metallic expansion joint for Between combustor and cyclone | 1319060.41 | 2666857.96 | 1557999 | 1720623.96 | 0
2 | Non metallic expansion joint for Cyclone and flue gas duct | 1208560.39 | 0 | 610253.98 | 0 | 0
3 | Non metallic expansion joint for Flue gas duct and and back pass | 586846.01 | 0 | 0 | 0 | 0
4 | SERVO VALVE ST10-63 | 172675.8 | 0 | 0 | 0 | 0
5 | SERVO VALVE ST 10-4 | 176311.28 | 0 | 0 | 0 | 0
6 | HP Element for service air compressor ZR 500 | 1391185.95 | 0 | 0 | 0 | 0
7 | Input Shaft for Intermediate conveyor Gear box | 289993 | 0 | 0 | 0 | 0
8 | ASH INTAKE VALVE COMPLETE ASSEMBLY. | 282466.52 | 0 | 0 | 1164701.5 | 0
10 | Oil gun assembly for start up burner. | 0 | 221649.3 | 0 | 0 | 312923.26
11 | FRP Blades for CT Fan | 0 | 1127478 | 1903862.7 | 1790691.36 | 0
12 | Fluid Coupling 500 SDFC | 0 | 140058 | 0 | 0 | 0
13 | 570 PST Fluild Coupling for Hammer Mill | 0 | 1041725 | 0 | 0 | 0
14 | Gear Box for MBCN-1A | 0 | 3848039 | 0 | 0 | 0
15 | Gear box (H3-400) for BCN-1A | 0 | 2040625 | 0 | 0 | 0
16 | Gear Box (B2SF-160) for Belt Feeder of Stacker Cum Reclaimer | 0 | 1204078.72 | 0 | 0 | 0
17 | Intermediate conveyor gearbox for SCR | 0 | 2460762 | 0 | 0 | 0
18 | Oil cooler for GA200W compressor- 7.5bar | 0 | 481343.08 | 0 | 0 | 0
19 | After cooler for GA200W compressor- 7.5bar | 0 | 361006.92 | 0 | 0 | 0
20 | Screw element of GA160W, 5.0/7.5 Bar Atlas Copco air compressor | 0 | 1852001 | 0 | 0 | 0
21 | Horizontal centrifugal pump with motor | 0 | 217675 | 0 | 0 | 0
22 | Complete set of chain assembly for TRC. | 0 | 0 | 1983507.06 | 2353553.69 | 2357397.38
23 | Complete set of chain assembly for Lignite Extraction feeder. | 0 | 0 | 1946369.4 | 4206673.76 | 1633010.2
26 | Cartridge assembly for HFO pressurising pump model no:T3ST 70/46. | 0 | 0 | 434861 | 0 | 0
27 | Cartridge Assembly for LDO Pressurising pump model no:T3S T45/46. | 0 | 0 | 241551.44 | 0 | 0
28 | MOT Centrifuge- Major service kit | 0 | 0 | 203969.98 | 0 | 0
29 | MOT Centrifuge-Inlet pipe with parting disc | 0 | 0 | 492330.02 | 0 | 0
30 | Rexroth Axial Piston Pump-Control Oil Tank. | 0 | 0 | 181213.88 | 0 | 0
31 | Turbine oil system- Jack Oil Pump Model: T 3SA 38/36. | 0 | 0 | 1993158.34 | 0 | 0
32 | HP BYPASS QUICK STROKING DEVICE SSB 10. | 0 | 0 | 244698 | 244698 | 0
33 | HP BYPASS OSU PRV MANIFOLD. | 0 | 0 | 166994.4 | 0 | 0
34 | HP BY PASS SYSTEM SERVO VALVE (MAIN -BP) ST 10 -63. | 0 | 0 | 207213 | 414426.4 | 0
35 | HP BY PASS SYSTEM SERVO VALVE (BPE) ST 10-4 | 0 | 0 | 207213 | 0 | 0
36 | HP BYPASS SPARE- AXIAL PISTON | 0 | 0 | 173400 | 0 | 0
37 | Wear ring casing for ACW pump | 0 | 0 | 266303.42 | 0 | 0
38 | DMCW . BOOSTER PUMP(Hor. Split Case Pump).PUMP SHAFT. | 0 | 0 | 109001.54 | 0 | 0
39 | Top Shaft sleeve for Circulating Water Pump | 0 | 0 | 112901.79 | 0 | 0
40 | Imp.shaft sleeve for Circulating Water Pump | 0 | 0 | 118592.29 | 0 | 0
41 | Rubber Bearing for Circulating Water Pump | 0 | 0 | 107972.91 | 0 | 0
42 | COMPLETE DRIVE SHAFT ASSEMBLY FOR CT FAN. | 0 | 0 | 773551.64 | 0 | 0
43 | Main oil pump- EBFP | 0 | 0 | 356028.51 | 0 | 0
44 | Auxiliary Lub Oil Pump for EBFP | 0 | 0 | 383836 | 0 | 0
45 | EBFP SPARE- BALANCE DRUM BUSHING | 0 | 0 | 100580.85 | 0 | 0
46 | Resilient coupling 129S GBM Make or equivalent | 0 | 0 | 465460 | 0 | 0
47 | Resilient coupling 127S GBM Make or equivalent for BCN-18A/B | 0 | 0 | 269280 | 0 | 0
49 | Resilient coupling 126S GBM Make or equivalent for BCN-1A,BCN-7A/B | 0 | 0 | 182784 | 0 | 0
50 | Resilient coupling 125S GBM Make or equivalent for BCN-11A/B,BCN-19A/B,BCNLS-1 | 0 | 0 | 140760 | 0 | 0
51 | Resilient coupling 125S GBM Make or equivalent for BCN-4A/B | 0 | 0 | 140760 | 0 | 0
52 | Roller Shaft Assembly for Roller Screen | 0 | 0 | 2084402.94 | 0 | 0
53 | DRIVE PULLEY OF SIZE: DIA 1024 X 1200MM X16T | 0 | 0 | 327930 | 0 | 0
54 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 824 X 1400MM X16T | 0 | 0 | 560280 | 0 | 0
55 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 824 X 1200MM X16T | 0 | 0 | 372394.86 | 0 | 0
56 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 524 X 1400MM X12T | 0 | 0 | 262926.52 | 0 | 0
57 | TAKE-UP PULLEY OF SIZE : DIA 824 X 1400MM X16 MM T | 0 | 0 | 414359.69 | 0 | 0
58 | TAKE-UP PULLEY OF SIZE: DIA 654 X 1200MM X 12MM T | 0 | 0 | 205773.47 | 0 | 0
59 | TAKE-UP PULLEY OF SIZE: DIA 824 X 1200MM X12 MM T | 0 | 0 | 255838.64 | 0 | 0
60 | TAKE-UP PULLEY OF SIZE: DIA 524 X 1200MM X12 MM T | 0 | 0 | 191260.2 | 0 | 0
61 | Bevel gear pair for B-3 180 ratio 21.750 | 0 | 0 | 174969.66 | 0 | 0
62 | SDFC 450 Fluid coupling assembly | 0 | 0 | 125491 | 0 | 0
63 | Runner for 570 PST fluid coupling | 0 | 0 | 162161.62 | 0 | 0
64 | HAND OPERATED 4 INCH CCS WCB 2500 CLASS GATE VALVE. | 0 | 0 | 139067.86 | 0 | 0
65 | NRV SIZE: 4" CCS VALVE WCB SWING CHECK TYPE CLASS RATING 2500. | 0 | 0 | 222456.66 | 0 | 0
66 | Oil Separator for GA 200 W | 0 | 0 | 281384.3 | 0 | 0
67 | BWT L1500 Pump 50HZ with Start Kit for IAC-Model ZR 37 | 0 | 0 | 196785.95 | 0 | 0
68 | Mechanical seal Ebil make,Type:H75/65 (Pump 45KW) | 0 | 0 | 389025.74 | 0 | 0
69 | Mechanical seal Ebil make,Type:H75/40 (Pump 22KW) | 0 | 0 | 451084.94 | 0 | 0
70 | Complete set of chain assembly for DCC | 0 | 0 | 0 | 1114101.65 | 0
71 | Mechanical Seal Set (04 No.s) of LDO decanting pump. | 0 | 0 | 0 | 240242.64 | 0
72 | Screw set (AISI 410) of LDO decanting pump . | 0 | 0 | 0 | 358851.52 | 0
73 | Safety Relief Valve for jack oil system size 3/4"X 1". | 0 | 0 | 0 | 183184.41 | 0
74 | AUXILIARY LUB OIL PUMP FOR BOILER FEED PUMP | 0 | 0 | 0 | 335421.16 | 0
75 | Complete Mechanical Seal for Boiler Feed Pump DE | 0 | 0 | 0 | 372523.42 | 0
76 | Complete Mechanical Seal for Main Boiler Feed Pump NDE | 0 | 0 | 0 | 372523.42 | 0
77 | Complete Mechanical Seal for Booster Pump DE of Feed Pump | 0 | 0 | 0 | 101358.8 | 0
78 | Complete Mechanical Seal for Booster Pump NDE of Feed Pump | 0 | 0 | 0 | 101358.8 | 0
79 | Thrust Pad set for Bearing 5 SLT of CEP Model EN7H32 | 0 | 0 | 0 | 817694.14 | 0
80 | Journal pad set for Bearing 5 SLT of CEP Model EN7H32 | 0 | 0 | 0 | 717839 | 0
81 | Thrust and Guide Bearing Assembly 5SLT for CEP Model EN7H32 | 0 | 0 | 0 | 1534093 | 0
82 | SAC Spare- Maint. kit for drier MD 1000/ 1300 W | 0 | 0 | 0 | 152342.03 | 177045.48
83 | IAC Spare- 16000 H Maintenance kit ZR/ZT 110-145+IMD | 0 | 0 | 0 | 325878.2 | 382329.84
84 | IAC Spare- HP Discharge silencer kit ZR/ZT 110-145 | 0 | 0 | 0 | 115836.15 | 135902.24
85 | SAC Spare- 16000 H Maintenance kit ZR 500 VSD | 0 | 0 | 0 | 466043.53 | 546774.73
86 | SAC Spare- HP Silencer kit ZR 300-425 | 0 | 0 | 0 | 241427.15 | 270134.28
87 | SAC Spare-Cooler cleaning kit ZR 300-425 | 0 | 0 | 0 | 169877.58 | 0
88 | Gear Box Assembly for Cooling Tower Fan. | 0 | 0 | 0 | 1005437.23 | 2140768.76
89 | Butterfly Valve 800 NB | 0 | 0 | 0 | 276206 | 0
90 | Bevel Gear Pair for Cooling Tower Fan Gear Box. | 0 | 0 | 0 | 541711.8 | 0
91 | Second Stage Wheel for Cooling Tower Fan Gear Box. | 0 | 0 | 0 | 135645.98 | 145674.24
92 | Drive Sheave for Toothed Double Roll Crusher | 0 | 0 | 0 | 366265.52 | 0
93 | Roller Shaft for Primary Roller Screen | 0 | 0 | 0 | 973446.12 | 0
94 | Main Drive Shaft for Flip Flow Screen | 0 | 0 | 0 | 217281.75 | 0
95 | Thrust Rod System for Flip Flow Screen | 0 | 0 | 0 | 118517.21 | 0
96 | Hydraulic Pump Complete P6S-2R1C-9A2-B00-0A1-M2-07704 | 0 | 0 | 0 | 1373848.2 | 0
97 | Non- Magnetic DRIVE PULLEY OF SIZE: DIA 824 X 1200MM X16T | 0 | 0 | 0 | 353736 | 0
98 | Non magnetic DRIVE PULLEY OF SIZE: DIA 1024 X 1200X16MM T | 0 | 0 | 0 | 586500 | 0
99 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 654 X 1200MM X12T | 0 | 0 | 0 | 242066.4 | 0
100 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 524 X 1200MM X12T | 0 | 0 | 0 | 206202.69 | 0
101 | TAIL PULLEY (MOUNTED ON BEARINGS )OF SIZE:DIA 524X1400MMX16T(SCR) | 0 | 0 | 0 | 130305 | 0
102 | TAKE PULLEY OF SIZE: DIA 524 X 1200MM X16T(SCR) | 0 | 0 | 0 | 138363 | 0
103 | DISCHARGE PULLEY(MOUNTED ON BEARINGS)OF SIZE: DIA1024X1200MMX20T | 0 | 0 | 0 | 445944 | 0
104 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 654 X 1200MMX20T | 0 | 0 | 0 | 214608 | 0
105 | DRIVE PULLEY OF SIZE: DIA 654 X 1200MMX20T(SCR) | 0 | 0 | 0 | 183600 | 0
106 | DRIVE PULLEY OF SIZE: DIA 524 X 1400MM X16T(SCR) | 0 | 0 | 0 | 127131.78 | 0
107 | TAIL PULLEY (MOUNTED ON BEARINGS )OF SIZE:DIA654X1200MMX16T(SCR) | 0 | 0 | 0 | 191821.2 | 0
108 | BEND PULLEY (MOUNTED ON BEARINGS)OF SIZE:DIA824X1200MMX20T(SCR) | 0 | 0 | 0 | 344056.2 | 0
109 | SNUB PULLEY(MOUNTED ON BEARINGS)OF SIZE:DIA424X1200MMX16.7T(SCR) | 0 | 0 | 0 | 138536.4 | 0
110 | BEND PULLEY (MOUNTED ON BEARINGS)OF SIZE:DIA524X1200MMX16T(SCR) | 0 | 0 | 0 | 164464.8 | 0
111 | Input shaft with pinion & key for H3-280 Ratio 23.016:1 | 0 | 0 | 0 | 133489.27 | 0
112 | Input shaft with pinion & key for H3-280 Ratio 34.984:1 | 0 | 0 | 0 | 133489.27 | 0
113 | Input shaft with pinion & key for H3-315 Ratio 22.433:1 | 0 | 0 | 0 | 204926.31 | 0
114 | Input shaft with pinion & key for H3-400 Ratio 28.4:1 | 0 | 0 | 0 | 336570.72 | 0
115 | Input shaft with pinion & key for H3-500 Ratio 28.4:1 | 0 | 0 | 0 | 571280.6 | 0
116 | 570 PST Coupling Set With Essential accessories | 0 | 0 | 0 | 688207.99 | 0
117 | 500 PST Coupling (Bi-directional) Set With All accessories | 0 | 0 | 0 | 919095.25 | 0
118 | Fluid coupling SDFC 410 assembly | 0 | 0 | 0 | 102483 | 0
119 | Horizontal centrifugal pump for transferring Degassed water. | 0 | 0 | 0 | 267445.3 | 0
120 | SCW roof of back pass & fin with O/L header as per referal drg. | 0 | 0 | 0 | 0 | 19000000
121 | COMBUSTOR SPIESS VALVE LANCE TIP | 0 | 0 | 0 | 0 | 787185
122 | LANCE TIP FOR SEALPOT SPIESS VALVE. | 0 | 0 | 0 | 0 | 2276089.2
123 | Elecon make complete gear box for Transport feeder. | 0 | 0 | 0 | 0 | 458816.4
124 | Triplex sprocket forLignite transport conveyor drive shaft. | 0 | 0 | 0 | 0 | 485990.68
125 | Elecon make complete gear box for extraction feeder. | 0 | 0 | 0 | 0 | 458816.6
126 | Triplex sprocket for lignite extraction conveyor. | 0 | 0 | 0 | 0 | 1457972.04
127 | DRIVING SIDE LINER ASSEMBLY FOR SECONDARY AIR FAN. | 0 | 0 | 0 | 0 | 1219631.82
128 | THURST PLATE KIT FOR DODGE SLEEVOIL BEARING RTL 5*7/16 . | 0 | 0 | 0 | 0 | 137275.54
129 | MODULAR HOUSING FOR DRIVE END DODGE SLEEVOIL BEARING RTL 5*7/16 . | 0 | 0 | 0 | 0 | 872458.59
130 | THURST PLATE KIT FOR DODGE SLEEVOIL BEARING RTL 4*7/16 . | 0 | 0 | 0 | 0 | 117006
131 | Bed ash Bare rotary Air lock feeder without drive. | 0 | 0 | 0 | 0 | 594408.97
132 | Triplex sprocket for DCC drive shaft. | 0 | 0 | 0 | 0 | 699078.88
133 | Bed material Bare rotary Air lock feeder without drive. | 0 | 0 | 0 | 0 | 500871.09
134 | Bare Pump without motor of LDO decanting pump. | 0 | 0 | 0 | 0 | 798633.15
135 | Set of lobe with shaft (1 set =2 nos) bed ash conveying blower. | 0 | 0 | 0 | 0 | 142668.53
136 | Set of gear ( 1 set = 2 nos) for bed ash conveying blower . | 0 | 0 | 0 | 0 | 112096.71
137 | Lifting oil to turning gear, Solenoid valve assembly. | 0 | 0 | 0 | 0 | 804300.88
138 | HP bypass system , Stem for BP VALVE , Type: ARS 80. | 0 | 0 | 0 | 0 | 269688
139 | HP bypass system , Jet cage for BP Valve , Type: ARS 80. | 0 | 0 | 0 | 0 | 189720
140 | HP bypass system ,Seat for BPE VALVE (Spray valve), Type: E 32 S. | 0 | 0 | 0 | 0 | 193800
141 | BFP Recirculation Valve Model 87-78124 with Actuator | 0 | 0 | 0 | 0 | 523156.51
142 | Thrust bearing for boiler feed pump FK6D30 | 0 | 0 | 0 | 0 | 295111.9
143 | Lower Shaft for condensate extraction pump EN7H32 | 0 | 0 | 0 | 0 | 298740.33
144 | Upper Shaft for condensate extraction pump EN7H32 | 0 | 0 | 0 | 0 | 310835.08
145 | Hotwell make up pump assembly without motor. | 0 | 0 | 0 | 0 | 1079916.36
146 | Impeller Guide piece for Circulating Water Pump | 0 | 0 | 0 | 0 | 601814.78
147 | HEAD SHAFT, T5 ANT | 0 | 0 | 0 | 0 | 319894.39
148 | Head Shaft for Fire Hydrant Pump | 0 | 0 | 0 | 0 | 132295.07
149 | INTERMEDIATE SHAFT for Hydrant Fire Pump(KBL pump,Type:BHR 28-30) | 0 | 0 | 0 | 0 | 259931.52
150 | IMPELLER SHAFT for Hydrant Fire Pump (KBL pump, Type:BHR 28-30) | 0 | 0 | 0 | 0 | 117470.03
151 | Flange with internal spline for Turbine Shaft Turning Gear | 0 | 0 | 0 | 0 | 276516.54
152 | Flange between hydromotor&over running clutch for STG | 0 | 0 | 0 | 0 | 355226.47
153 | Shaft of hydraulic motor for Turbine Shaft Turning Gear | 0 | 0 | 0 | 0 | 147868.55
154 | Shaft of Over Running Clutch for Turbine Shaft Turning Gear | 0 | 0 | 0 | 0 | 736394.79
155 | Long Travel Gearbox for SCR | 0 | 0 | 0 | 0 | 2140354.22
156 | Grinding Jip carrier | 0 | 0 | 0 | 0 | 1322534.37
157 | Hydraulic Pump Complete P11S-7R1C-9A2-B00-0A1-M2-08037 | 0 | 0 | 0 | 0 | 2492170.32
158 | Shaft Seal Kit, HD Item no : 478 2277 -964 | 0 | 0 | 0 | 0 | 376159.5
159 | Seal Kit Pump Complete, HD Item no: 478 3233 -146 | 0 | 0 | 0 | 0 | 161668.47
160 | Hydraulic cylinder 80X45X1600 | 0 | 0 | 0 | 0 | 509324.08
161 | Hydraulic Motor CA 210 210 CB0NHC0200 with brake | 0 | 0 | 0 | 0 | 5978456.64
162 | DRIVE PULLEY OF SIZE: DIA 824 X 1200MMX20T(SCR) | 0 | 0 | 0 | 0 | 473813
163 | Bevel pinion shaft assembly for B3-180 & bevel wheel | 0 | 0 | 0 | 0 | 448455.88
164 | Bevel pinion shaft assembly for B3-180 ratio 31.103:1 | 0 | 0 | 0 | 0 | 224227.94
165 | Bevel pinion shaft assembly for B3-200 gear box | 0 | 0 | 0 | 0 | 263784.46
166 | Bevel pinion shaft assembly for B3-160 gear box | 0 | 0 | 0 | 0 | 201492.42
167 | Bevel pinion shaft assembly for B3-140 gear box | 0 | 0 | 0 | 0 | 182406.96
168 | Bevel pinion shaft assembly for B3-280 gear box | 0 | 0 | 0 | 0 | 463865.76
169 | Bearing sealing ring, Part No: HY11390131083 | 0 | 0 | 0 | 0 | 2056591.28
170 | Labyrinth ring for bearing shell Part No: HY31390131116 | 0 | 0 | 0 | 0 | 1144163.36
171 | Generator fan blades TE, Part No: HY9316103002 | 0 | 0 | 0 | 0 | 1048010.1
172 | Generator fan blades EE, Part No: HY9316103010 | 0 | 0 | 0 | 0 | 1048010.1
173 | Adjusting steel for bearing pedestal, Part No: HY31390131118 | 0 | 0 | 0 | 0 | 652190.2
174 | Generator Bearing insulation. Part No: HY1390131020 | 0 | 0 | 0 | 0 | 1255557.12
175 | Rotork Actuator Type K30G0A | 0 | 0 | 0 | 0 | 108712.89
176 | Rotork Actuator Type K150F10A | 0 | 0 | 0 | 0 | 120563.94
177 | Make:E/R ,Num.Dir.IDMTL 3O/C+1E/F Highset Relay,Type:ARGUS 2 | 0 | 0 | 0 | 0 | 108896.94
178 | Motor Protection Relay,Type:AMV2-1A, P&B MAKE | 0 | 0 | 0 | 0 | 152210.13
179 | Feeder Protection Relay, Type -AFV2-1A, P&B MAKE | 0 | 0 | 0 | 0 | 162707.38
180 | ABT Energy meter for feeders | 0 | 0 | 0 | 0 | 843684
181 | L&T Make:CN-CS-1250H type Breaker. | 0 | 0 | 0 | 0 | 151793.4
182 | Out door radio modem unit for 25Mbps | 0 | 0 | 0 | 253215 | 235620
183 | PACKAGE PROJECT FOR SUPPLY, ERECTION, COMMISSION AND OPERATION OF CAAQMS | 0 | 0 | 0 | 0 | 12641317.5
184 | DM Transmitter Model: 1056-01-20-32-AN+PH+Conductivity sensor | 0 | 0 | 0 | 0 | 176495.26
185 | Guided Wave Radar Level Transmitter for Measuring SILO LEVEL. | 0 | 0 | 0 | 0 | 222787
186 | Single acting smart positioner for drain valves as per spec | 0 | 0 | 0 | 0 | 553248.32
187 | DPU 4F Primary Module- MODULE NO: 69230D401B, TYPE: PDP401 | 0 | 0 | 0 | 0 | 2004264.56
188 | Prop. Directional Valve, Type: G631-XXXXX-H-75-J-O-F-M-4-V-B-Q | 0 | 0 | 0 | 0 | 260000
189 | DUAL SIESMIC MONITOR MAKE:SHINKAWA, MODEL: VM-5U-221110-000-001-0 | 0 | 0 | 0 | 0 | 1572671.2
190 | Communication between IAC/SAC and main DCS. | 0 | 0 | 0 | 0 | 239631.3
191 | 415 V,145 KW,TEFC SQUIRREL CAGE INDUCTION MOTOR . | 0 | 0 | 0 | 375232 | 0
192 | AUMA Actuator Model SA30A90. | 0 | 0 | 0 | 396524.04 | 0
193 | Fan Transformer 3-phase 500-690VAC | 0 | 0 | 0 | 141795.54 | 0
194 | Fan for framesize g,h and j, Part for Siemens Make VFD Unit. | 0 | 0 | 0 | 192035.22 | 0
195 | ABT METER READING INSTRUMENT FOR L&T ABT METERS | 0 | 0 | 0 | 118125 | 0
196 | Fan Transformer 3 phase 380-480 VAC, 50/60 Hz | 0 | 0 | 0 | 121673.78 | 0
197 | 400Volts, 75KW, Frame 280S, 4P, Motor for Bucket Wheel of SCR | 0 | 0 | 0 | 515868.48 | 0
198 | 400Volts, 22KW, Frame 180L, 4P, Motor for Slew of SCR | 0 | 0 | 0 | 128411.53 | 0
199 | 400Volts, 55KW, Frame 250M, 4P, Motor for Boom Conveyor of SCR | 0 | 0 | 0 | 429469.49 | 0
200 | Commulating Choke for SCR | 0 | 0 | 0 | 160051.5 | 0
201 | Convertor for SCR | 0 | 0 | 0 | 995214.01 | 0
202 | VACCUME CONTACTOR ,3TF69 44-0C,110V AC,make:Siemens. | 0 | 0 | 0 | 204750.15 | 0
203 | 415Volts, 75kW, 6pole, Frame 315S motor for RWP | 0 | 0 | 0 | 259781 | 0
204 | 110KW,415V,4 Pole,ND315S,Delta connection,Hydrant pump Motor. | 0 | 0 | 0 | 543107.81 | 0
205 | ID FanMotor, 690 V, 800 KW, 8 Pole Horizondal mounted Cage motor | 0 | 0 | 0 | 6742297.56 | 0
206 | 37Kw Motor,415V,2Pole,Conn:Delta,Fr:200L-Fire BoosterPump Motor | 0 | 0 | 0 | 135077.37 | 0
207 | Out door radio modem unit for 50Mbps | 0 | 0 | 0 | 133875 | 0
208 | ONLINE OXYGEN ANALYSER AS PER TECHNICAL SPECIFICATIONS | 0 | 0 | 0 | 626063 | 0
209 | Nafion dryer Make Perma pure Model: PD-100T-24MKA as per spec | 0 | 0 | 0 | 533058 | 0
210 | DCS Engineer Work Station as per spec. | 0 | 0 | 0 | 563337.5 | 0
211 | Main PC Control circut Card for Spider Control,ver 4.2.1,rev:R2D | 0 | 0 | 0 | 601536.42 | 0
212 | Combox(Gateway MK5),Part no: 2230006800 | 0 | 0 | 0 | 138680.1 | 0
213 | Housing Vibration Module, MODEL NO: 3500/42-01-00 | 0 | 0 | 0 | 657762.38 | 0
214 | DUAL SIESMIC MONITOR MAKE:SHINKAWA, MODEL: VM-5U-921110-000-001-0 | 0 | 0 | 0 | 1397930.08 | 0
215 | VM-5 SERIES INSTRUMENT RACK MAKE: SHINKAWA, MODEL: VM-5W1-0 | 0 | 0 | 0 | 226746 | 0
216 | HYDRAULIC DEAD WEIGHT TESTER AS PER SPECIFICATIONS | 0 | 0 | 0 | 205491 | 0
217 | Electronic Water Drain for SAC part no. 8102042630 | 0 | 454280.24 | 0 | 144507.46 | 0
218 | LIGNITE BUNKER WEIGHT CALIBRATION UNIT AS PER SPEC | 0 | 0 | 0 | 551775 | 0
219 | LIGNITE BUNKER WEIGHING INDICATORS AS PER SPEC | 0 | 0 | 0 | 323400 | 0
220 | Flexible connector for Equipment complete set-2500A | 0 | 0 | 179485.05 | 0 | 0
221 | Flexible connector for Equipment complete set-1600A | 0 | 0 | 116743.47 | 0 | 0
222 | MOP/LOP(AC) 37KW Motor | 0 | 0 | 125766 | 0 | 0
223 | AUMA Actuator Model No SAR12B45 | 0 | 343857.22 | 361583.45 | 0 | 0
224 | AUMA Actuator whole assembly Type SA15AF32+Epac . | 0 | 0 | 198179.22 | 0 | 0
225 | Auma actuator whole assembly model SA12E125+TBG. | 0 | 0 | 144635.15 | 0 | 0
226 | AUMA Actuator model SA50-E-90 . | 0 | 0 | 140019.57 | 0 | 0
227 | Gear Box for actuator SA50-E-90 . | 0 | 0 | 148318.16 | 0 | 0
228 | LIMITORQUE MAKE ELECTICAL ACTUATOR MODEL NO. SMB-2-60/4 | 0 | 0 | 1415568.97 | 0 | 0
229 | 245 KV,triple pole, Centre Post Rotating Double Break Isolators | 0 | 0 | 244794.03 | 0 | 0
230 | Snubber Board | 0 | 0 | 101322.9 | 0 | 0
231 | ARECA CONTROLLER WITH FIRING CARD | 0 | 0 | 619682.57 | 0 | 0
232 | 6.6kV 415kW 3Phase Squirrel Cage Induction Motor Frame TS500L2. | 1914134.13 | 0 | 1881000 | 0 | 0
233 | Stall Torque motor; SBS -125B4 ; Torque: 9.7NM for SCR | 0 | 0 | 611889.51 | 0 | 0
234 | Stall Torque motor; SBS -100B4 ; Torque: 4.3NM | 0 | 0 | 397728.18 | 0 | 0
235 | 6.6KV Grade Slip Ring Assembly for PCRD | 0 | 0 | 116259.01 | 0 | 0
236 | 1.1KV Grade Slip Ring Assembly for CCRD | 0 | 0 | 177447.96 | 0 | 0
237 | BTS2000 BUS TRANSFER SYSTEM MAIN MODULE | 0 | 0 | 1388520 | 0 | 0
238 | 760KW,6.6KV CWP MOTOR | 0 | 0 | 2985613.4 | 0 | 0
239 | 55 kW motor,415v,4Pole, Fr:D280S - CT Fan motor | 0 | 0 | 219000 | 0 | 0
240 | Quantar Repeater | 0 | 0 | 1799280 | 0 | 0
241 | 415V, 160KW, 315L, 4Pole, Motor for Fly Ash/Bed Ash Compressor | 0 | 0 | 449553 | 0 | 0
242 | 6.6KV, 185KW, 315F, 4Pole Motor for Fly Ash Stg 2 Compressor | 0 | 0 | 1460076.8 | 0 | 0
243 | RA#5 SIEMENS SITRANS probe LU Transmitter 7M5221-2BA11 | 0 | 0 | 192396.84 | 0 | 0
244 | GUIDED WAVE RADAR LEVEL TR. | 0 | 0 | 211017.2 | 0 | 0
245 | Flow meter for Circulating water forebay makeup water. | 0 | 0 | 261816.78 | 0 | 0
246 | Flow meter for Boiler blow down (Intermediate blow down). | 0 | 0 | 682914.26 | 0 | 0
247 | DM Conductivity Transmitter Model: 1056-01-22-30-AN +P/N 23820-00 | 0 | 0 | 385716.02 | 0 | 0
248 | LPG Pilot Gas Ignitor ZA1- 150 P/K0K5M | 1087163 | 790473.24 | 2228445.65 | 0 | 0
249 | RA#3 compressor Local opertor panel for ZR-37,GA160W,GA200W. | 0 | 0 | 526146.66 | 0 | 0
250 | CPU 360 MODULE MAKE :GE MODEL NO: IC693CPU360 | 0 | 0 | 131080.34 | 0 | 0
251 | GENIUS BUS CONTROLLER MAKE:GE,MODEL NO: IC693BEM331 | 0 | 0 | 126113.82 | 0 | 0
252 | Siemens PLC, MONOMODE PROFIBUS OLM G12-1300 | 0 | 0 | 343764.07 | 0 | 0
253 | Siemens PLC,CP1613 FOR Industrial Ethernet Communication | 0 | 0 | 236414.48 | 0 | 0
254 | Siemens PLC,Communication processor CP 341-1,(POINT TO POINT LINK) | 0 | 0 | 125749.72 | 0 | 0
255 | Siemens PLC, Y-LINK | 0 | 0 | 190706.28 | 0 | 0
256 | Siemens PLC - Function Module , FM350-2 COUNTER in JNT & screen | 0 | 0 | 134000.62 | 0 | 0
257 | PLC HMI Operator\Engineer work station(OWS\EWS) as per spec. | 0 | 0 | 696250 | 0 | 0
258 | LIMITORQUE MAKE ELECTICAL ACTUATOR MODEL NO. SMB-3-150/4 | 0 | 1895978.83 | 0 | 0 | 0
259 | BFP SCOOP MOTOR ACTUATOR ABB MAKE MODEL -RHD250 | 0 | 1064852.22 | 0 | 0 | 0
260 | BFP SCOOP CONTROL SUPPLY UNIT ABB MAKE MODEL -EBN853 | 0 | 765698.69 | 0 | 0 | 0
261 | Current Transformer for Inter Bus Transformers | 0 | 1382399.17 | 0 | 0 | 0
262 | Current Transformer for GTs and Feeders. | 0 | 1164802.83 | 0 | 0 | 0
263 | ED7470400311 DIGITAL AVR DC-DC SUPPLY MODULE | 0 | 455428.34 | 0 | 0 | 0
264 | ED7470400141 AVR FIRING &CONTROL MODULE | 0 | 578332.46 | 0 | 0 | 0
265 | ED7470400133 AVR CPU MODULE | 0 | 469562.32 | 0 | 0 | 0
266 | CN 9090389300 PULSE FINAL STAGE | 0 | 105219.65 | 0 | 0 | 0
267 | ED7470400290 16 CHANNEL BINARY OUT PUT MODULE | 0 | 170332.61 | 0 | 0 | 0
268 | ED7470400168 DAVR INT GEN MODULE | 0 | 356983.95 | 0 | 0 | 0
269 | ED7470400281 DAVR I/O MODULE | 0 | 433771.44 | 0 | 0 | 0
270 | CN9090433503 PULSE COUP STAGE MODULE | 0 | 200773.52 | 0 | 0 | 0
271 | ED9090334114,AC/DC-DC CONVERTOR MODULE | 0 | 326796.05 | 0 | 0 | 0
272 | CN9090110704 PULSE SUPERVISION MODULE | 0 | 156809.39 | 0 | 0 | 0
273 | ED7470400206 DAVR 16 CHANNEL O/P MDL | 0 | 124824.59 | 0 | 0 | 0
274 | SA0653980205,AC ISOLATOR 3 POLE WITH MICRO SWITCH | 0 | 234195.85 | 0 | 0 | 0
275 | 3 PH, 6.6 KV, 180 KW, B3, 4 P, S1, IP 55, S.C. IND. MOTOR | 0 | 964224.76 | 0 | 0 | 0
276 | 415kV, 75kW 3Phase Squirrel Cage Induction Motor, Frame 280M | 0 | 226936.5 | 0 | 0 | 0
277 | 415kV,90kW, 3Phase Squirrel Cage Induction Motor, Frame 315S | 0 | 278654.25 | 0 | 0 | 0
278 | 415kV, 55kW 3Phase Squirrel Cage Induction Motor, Frame 280S | 0 | 195405 | 0 | 0 | 0
279 | 415kV,160 kW, 3Phase Squirrel Cage Induction Motor, Frame 355L | 0 | 509528.25 | 0 | 0 | 0
280 | Siemens make ACB 800amps for stacker cum reclaimer. | 0 | 183719 | 0 | 0 | 0
281 | GE 800 A Spectronic ACB with LMZ7 | 0 | 232316 | 0 | 0 | 0
282 | Durag Make Flame Scanner Unit, Model: D-LE-603-UA-P. | 160541 | 320900.16 | 0 | 0 | 0
283 | Durag Make Flame Control Unit, Model-D-UG 660 -115A-420 | 165268 | 355282.68 | 0 | 0 | 0
284 | KELTRON Pneumatic Actuator Model No.C0608 252239 for SUB SA | 0 | 179050.99 | 0 | 0 | 0
285 | KELTRON Pneumatic Actuator Model No.C0816 352239 for CombustorSAD | 0 | 200950.2 | 0 | 0 | 0
286 | Pneumatic Actuator for Sec. Air IGV, Keltron, C1216442239 | 0 | 237643.5 | 0 | 0 | 0
287 | PFT ,Indigenous Equivalent to CCI ,make:MASS ModelMG-10+4K | 0 | 367200 | 0 | 0 | 0
288 | BFP SCOOP PFT ABB MAKE PART NO 764975 | 0 | 438019.68 | 0 | 0 | 0
289 | MID VALUE SELECTOR MODULE ED69229S901A | 0 | 429578.68 | 0 | 0 | 0
290 | 1 OF 3 I/P SELECTION MODULE ED69229S902A FOR TURBINE-DCS | 0 | 515111.06 | 0 | 0 | 0
291 | POSITION MEASUREMENT MODULE ED69229S910A FOR TURBINE-DCS | 0 | 533080.06 | 0 | 0 | 0
292 | POSITION CONTROL MODULE ED69229S914A FOR TURBINE DCS | 0 | 396036.56 | 0 | 0 | 0
293 | Antivirus server for DCS network | 0 | 663211.18 | 0 | 0 | 0
294 | GE PLC Series 90-30 ETHERNET INTERFACE TCP/IP MODULE, IC693CMM321 | 0 | 213169.4 | 0 | 0 | 0
295 | GE PLC Series 90-30 Genius Bus Controller,IC693BEM331. | 0 | 132795.36 | 0 | 0 | 0
296 | GE PLC Rx3i Ethernet Module IC695ETM001,used at AHS PLC,SILO. | 0 | 121584.49 | 0 | 0 | 0
297 | Regulator ELECTRONIKON IIID for SAC 1900071032. | 0 | 151002.94 | 0 | 0 | 0
298 | REGULATOR for SAC part no. 1900071082 | 0 | 134135.55 | 0 | 0 | 0
299 | ALARM UNIT for SAC part no. 1089045770 | 0 | 235998.78 | 0 | 0 | 0
300 | Regulator ELECTRONIKON IIID for IAC 1900071032 | 0 | 149537.92 | 0 | 0 | 0
301 | Rotork Actuator Type K1000F16A | 174301.41 | 0 | 0 | 0 | 0
302 | Rotork Actuator type K300F14E | 119669.73 | 0 | 0 | 0 | 0
303 | Rotork Actuator type K600F14A | 328445.73 | 0 | 0 | 0 | 0
304 | Rotork Actuator type K300F14A | 121158.5 | 0 | 0 | 0 | 0
305 | Rotork Actuator type K500G3A | 162694.63 | 0 | 0 | 0 | 0
306 | E+H Liquicap Level Transmitter for Turbine Main Oil Tank | 202241 | 0 | 0 | 0 | 0
307 | Level control unit for Bunker Level, Endress+Hauser Make | 109250.55 | 0 | 0 | 0 | 0
308 | Ultrosonic Level Probe for Bunker Level, Make: Endress+Hauser | 213362.94 | 0 | 0 | 0 | 0
309 | DVC-6010 AD, Smart Positioner: Thum Adapter, Make Fisher | 407403 | 0 | 0 | 0 | 0
310 | SMART POSITIONER FOR MASONEILAN CONTROL VALVE | 177826.9 | 0 | 0 | 0 | 0
311 | PI servo amplifier, Make: MOOG,Model G122-829-001 | 346800 | 0 | 0 | 0 | 0
(C) | Details of capital spares consumed during the year
1 | Non metallic expansion joint for Between combustor and cyclone | 1319060.42 | 710533.46 | 1956324.49 | 1591877.96 | 1686745
2 | Non metallic expansion joint for Cyclone and flue gas duct | 299110 | 909450.39 | 27292.98 | 0 | 291480.5
3 | SERVO VALVE ST10-63 | 172675.8 | 0 | 0 | 0 | 0
4 | ASH INTAKE VALVE COMPLETE ASSEMBLY. | 148500.9 | 0 | 0 | 318756.62 | 0
5 | FRP Blades for CT Fan | 0 | 563739 | 2467601.7 | 30900.36 | 0
6 | 570 PST Fluild Coupling for Hammer Mill | 0 | 1041725 | 0 | 0 | 0
7 | Gear Box (B2SF-160) for Belt Feeder of Stacker Cum Reclaimer | 0 | 31954.72 | 0 | 0 | 0
8 | Gear Box for MBCN-1A | 0 | 3848039 | 0 | 0 | 0
9 | Gear box (H3-400) for BCN-1A | 0 | 2040625 | 0 | 0 | 0
10 | Screw element of GA160W, 5.0/7.5 Bar Atlas Copco air compressor | 0 | 1852001 | 0 | 0 | 0
11 | Horizontal centrifugal pump with motor | 0 | 217675 | 0 | 0 | 0
12 | Oil gun assembly for start up burner. | 0 | 23910.99 | 0 | 0 | 0
15 | Turbine oil system- Jack Oil Pump Model: T 3SA 38/36. | 0 | 0 | 1993158.34 | 0 | 0
16 | HP BYPASS OSU PRV MANIFOLD. | 0 | 0 | 166994.4 | 0 | 0
17 | HP BY PASS SYSTEM SERVO VALVE (BPE) ST 10-4 | 0 | 0 | 207213 | 0 | 0
18 | COMPLETE DRIVE SHAFT ASSEMBLY FOR CT FAN. | 0 | 0 | 773551.64 | 0 | 0
19 | Resilient coupling 129S GBM Make or equivalent | 0 | 0 | 465460 | 0 | 0
20 | Bevel gear pair for B-3 180 ratio 21.750 | 0 | 0 | 174969.66 | 0 | 0
21 | Runner for 570 PST fluid coupling | 0 | 0 | 162161.62 | 0 | 0
22 | Oil Separator for GA 200 W | 0 | 0 | 325731.47 | 0 | 0
23 | Oil cooler for GA200W compressor- 7.5bar | 0 | 0 | 240671.54 | 0 | 0
24 | BWT L1500 Pump 50HZ with Start Kit for IAC-Model ZR 37 | 0 | 0 | 196785.95 | 0 | 0
25 | Mechanical seal Ebil make,Type:H75/40 (Pump 22KW) | 0 | 0 | 340188.87 | 0 | 0
26 | Complete set of chain assembly for Lignite Extraction feeder. | 0 | 0 | 50635.4 | 6102407.76 | 1633010.2
27 | Wear ring casing for ACW pump | 0 | 0 | 80148.1 | 0 | 0
28 | DMCW . BOOSTER PUMP(Hor. Split Case Pump).PUMP SHAFT. | 0 | 0 | 1030.9 | 0 | 0
29 | Roller Shaft Assembly for Roller Screen | 0 | 0 | 20637.94 | 0 | 343960.83
30 | Complete set of chain assembly for TRC. | 0 | 0 | 2925.06 | 4334135.69 | 2357397.38
31 | Cartridge Assembly for LDO Pressurising pump model no:T3S T45/46. | 0 | 0 | 3719.04 | 237832.4 | 0
32 | MOT Centrifuge-Inlet pipe with parting disc | 0 | 0 | 21088.11 | 0 | 0
33 | Rexroth Axial Piston Pump-Control Oil Tank. | 0 | 0 | 2760.12 | 0 | 0
34 | NRV SIZE: 4" CCS VALVE WCB SWING CHECK TYPE CLASS RATING 2500. | 0 | 0 | 3788.91 | 218754.14 | 0
35 | Mechanical Seal Set (04 No.s) of LDO decanting pump. | 0 | 0 | 0 | 240242.64 | 0
36 | SERVO VALVE ST 10-4 | 0 | 0 | 0 | 176311.28 | 0
37 | HP BYPASS QUICK STROKING DEVICE SSB 10. | 0 | 0 | 0 | 244697.72 | 244698
38 | HP BY PASS SYSTEM SERVO VALVE (MAIN -BP) ST 10 -63. | 0 | 0 | 0 | 207213 | 414426.4
39 | Complete Mechanical Seal for Boiler Feed Pump DE | 0 | 0 | 0 | 191079.41 | 181444.01
40 | Complete Mechanical Seal for Main Boiler Feed Pump NDE | 0 | 0 | 0 | 186261.71 | 186261.71
41 | Thrust Pad set for Bearing 5 SLT of CEP Model EN7H32 | 0 | 0 | 0 | 420193.64 | 0
42 | Journal pad set for Bearing 5 SLT of CEP Model EN7H32 | 0 | 0 | 0 | 358919.5 | 0
43 | Thrust and Guide Bearing Assembly 5SLT for CEP Model EN7H32 | 0 | 0 | 0 | 1534093 | 0
44 | SAC Spare- Maint. kit for drier MD 1000/ 1300 W | 0 | 0 | 0 | 152342.03 | 177045.48
45 | IAC Spare- 16000 H Maintenance kit ZR/ZT 110-145+IMD | 0 | 0 | 0 | 325878.2 | 382329.84
46 | IAC Spare- HP Discharge silencer kit ZR/ZT 110-145 | 0 | 0 | 0 | 115836.15 | 135902.24
47 | SAC Spare- 16000 H Maintenance kit ZR 500 VSD | 0 | 0 | 0 | 466043.53 | 546774.73
48 | SAC Spare- HP Silencer kit ZR 300-425 | 0 | 0 | 0 | 241427.15 | 270134.28
49 | SAC Spare-Cooler cleaning kit ZR 300-425 | 0 | 0 | 0 | 169877.58 | 0
50 | Gear Box Assembly for Cooling Tower Fan. | 0 | 0 | 0 | 1005437.23 | 0
51 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 524 X 1200MM X12T | 0 | 0 | 0 | 206202.69 | 0
52 | 500 PST Coupling (Bi-directional) Set With All accessories | 0 | 0 | 0 | 919095.25 | 0
53 | HAND OPERATED 4 INCH CCS WCB 2500 CLASS GATE VALVE. | 0 | 0 | 0 | 139067.86 | 0
54 | Screw set (AISI 410) of LDO decanting pump . | 0 | 0 | 0 | 7415.3 | 0
55 | Complete set of chain assembly for DCC | 0 | 0 | 0 | 1839.65 | 0
56 | Safety Relief Valve for jack oil system size 3/4"X 1". | 0 | 0 | 0 | 1078.41 | 0
57 | Auxiliary Lub Oil Pump for boiler feed pump | 0 | 0 | 0 | 11591.16 | 0
58 | Input shaft with pinion & key for H3-315 Ratio 22.433:1 | 0 | 0 | 0 | 3205.76 | 0
59 | SCW roof of back pass & fin with O/L header as per referal drg. | 0 | 0 | 0 | 0 | 19000000
60 | COMBUSTOR SPIESS VALVE LANCE TIP | 0 | 0 | 0 | 0 | 393592.5
61 | LANCE TIP FOR SEALPOT SPIESS VALVE. | 0 | 0 | 0 | 0 | 2276089.2
62 | Elecon make complete gear box for Transport feeder. | 0 | 0 | 0 | 0 | 458816.4
63 | Triplex sprocket forLignite transport conveyor drive shaft. | 0 | 0 | 0 | 0 | 121497.67
64 | Elecon make complete gear box for extraction feeder. | 0 | 0 | 0 | 0 | 458816.6
65 | DRIVING SIDE LINER ASSEMBLY FOR SECONDARY AIR FAN. | 0 | 0 | 0 | 0 | 612849.82
66 | THURST PLATE KIT FOR DODGE SLEEVOIL BEARING RTL 5*7/16 . | 0 | 0 | 0 | 0 | 137275.54
67 | MODULAR HOUSING FOR DRIVE END DODGE SLEEVOIL BEARING RTL 5*7/16 . | 0 | 0 | 0 | 0 | 438399.59
68 | Bed ash Bare rotary Air lock feeder without drive. | 0 | 0 | 0 | 0 | 594408.97
69 | Triplex sprocket for DCC drive shaft. | 0 | 0 | 0 | 0 | 174769.72
70 | HP BYPASS SPARE- AXIAL PISTON | 0 | 0 | 0 | 0 | 173400
71 | BFP Recirculation Valve Model 87-78124 with Actuator | 0 | 0 | 0 | 0 | 523156.51
72 | Complete Mechanical Seal for Booster Pump DE of Feed Pump | 0 | 0 | 0 | 0 | 101358.8
73 | Imp.shaft sleeve for Circulating Water Pump | 0 | 0 | 0 | 0 | 118592.29
74 | Rubber Bearing for Circulating Water Pump | 0 | 0 | 0 | 0 | 107972.91
75 | Impeller Guide piece for Circulating Water Pump | 0 | 0 | 0 | 0 | 601814.78
76 | HEAD SHAFT, T5 ANT | 0 | 0 | 0 | 0 | 319894.39
77 | Bevel Gear Pair for Cooling Tower Fan Gear Box. | 0 | 0 | 0 | 0 | 180570.6
78 | INTERMEDIATE SHAFT for Hydrant Fire Pump(KBL pump,Type:BHR 28-30) | 0 | 0 | 0 | 0 | 129965.76
79 | IMPELLER SHAFT for Hydrant Fire Pump (KBL pump, Type:BHR 28-30) | 0 | 0 | 0 | 0 | 117470.03
80 | Over Running Clutch for Turbine Shaft Turning Gear | 0 | 0 | 0 | 0 | 103173
81 | Long Travel Gearbox for SCR | 0 | 0 | 0 | 0 | 2140354.22
82 | Hydraulic Pump Complete P11S-7R1C-9A2-B00-0A1-M2-08037 | 0 | 0 | 0 | 0 | 2492170.32
83 | Hydraulic Pump Complete P6S-2R1C-9A2-B00-0A1-M2-07704 | 0 | 0 | 0 | 0 | 1373848
84 | Hydraulic cylinder 80X45X1600 | 0 | 0 | 0 | 0 | 509324.08
85 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 824 X 1400MM X16T | 0 | 0 | 0 | 0 | 560280
86 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 524 X 1400MM X12T | 0 | 0 | 0 | 0 | 262926.52
87 | TAIL PULLEY (MOUNTED ON BEARINGS )OF SIZE:DIA654X1200MMX16T(SCR) | 0 | 0 | 0 | 0 | 191821.2
88 | TAKE-UP PULLEY OF SIZE : DIA 824 X 1400MM X16 MM T | 0 | 0 | 0 | 0 | 414359.69
89 | 570 PST Coupling Set With Essential accessories | 0 | 0 | 0 | 0 | 688207.99
90 | Triplex sprocket for lignite extraction conveyor. | 0 | 0 | 0 | 0 | 96656.78
91 | Bare Pump without motor of LDO decanting pump. | 0 | 0 | 0 | 0 | 4636.15
92 | Set of lobe with shaft (1 set =2 nos) bed ash conveying blower. | 0 | 0 | 0 | 0 | 7122.21
93 | Lifting oil to turning gear, Solenoid valve assembly. | 0 | 0 | 0 | 0 | 41213.27
94 | HP bypass system , Stem for BP VALVE , Type: ARS 80. | 0 | 0 | 0 | 0 | 0.2
95 | Thrust bearing for boiler feed pump FK6D30 | 0 | 0 | 0 | 0 | 15121.78
96 | Lower Shaft for condensate extraction pump EN7H32 | 0 | 0 | 0 | 0 | 15307.83
97 | Upper Shaft for condensate extraction pump EN7H32 | 0 | 0 | 0 | 0 | 15927.58
98 | Hotwell make up pump assembly without motor. | 0 | 0 | 0 | 0 | 0.36
99 | Gear Box Assembly for Cooling Tower Fan. | 0 | 0 | 0 | 0 | 73028.97
100 | Head Shaft for Fire Hydrant Pump | 0 | 0 | 0 | 0 | 22265.07
101 | Shaft of Over Running Clutch for Turbine Shaft Turning Gear | 0 | 0 | 0 | 0 | 40723.35
102 | Grinding Jip carrier | 0 | 0 | 0 | 0 | 42298.56
103 | Shaft Seal Kit, HD Item no : 478 2277 -964 | 0 | 0 | 0 | 0 | 16339.5
104 | Hydraulic Motor CA 210 210 CB0NHC0200 with brake | 0 | 0 | 0 | 0 | 104524.64
105 | Bevel pinion shaft assembly for B3-180 & bevel wheel | 0 | 0 | 0 | 0 | 6898.94
106 | Bevel pinion shaft assembly for B3-280 gear box | 0 | 0 | 0 | 0 | 51820.45
107 | Thrust stand assembly (Part No:34) for Raw water pump | 0 | 0 | 0 | 0 | 66712.94
108 | Thrust bearing housing assembly. | 0 | 0 | 0 | 0 | 26547.37
109 | Thrust bearing housing assembly. | 0 | 0 | 0 | 0 | 24288.1
110 | Bearing sealing ring, Part No: HY11390131083 | 0 | 0 | 0 | 0 | 105382.24
111 | Labyrinth ring for bearing shell Part No: HY31390131116 | 0 | 0 | 0 | 0 | 58628.13
112 | Generator fan blades TE, Part No: HY9316103002 | 0 | 0 | 0 | 0 | 53701.2
113 | Generator fan blades EE, Part No: HY9316103010 | 0 | 0 | 0 | 0 | 53701.2
114 | Adjusting steel for bearing pedestal, Part No: HY31390131118 | 0 | 0 | 0 | 0 | 652190.2
115 | Generator Bearing insulation. Part No: HY1390131020 | 0 | 0 | 0 | 0 | 1255557.12
116 | Rotork Actuator Type K30G0A | 0 | 0 | 0 | 0 | 7476.78
117 | Rotork Actuator Type K150F10A | 0 | 0 | 0 | 0 | 8291.84
118 | Make:E/R ,Num.Dir.IDMTL 3O/C+1E/F Highset Relay,Type:ARGUS 2 | 0 | 0 | 0 | 0 | 0
119 | Motor Protection Relay,Type:AMV2-1A, P&B MAKE | 0 | 0 | 0 | 0 | 0.13
120 | Feeder Protection Relay, Type -AFV2-1A, P&B MAKE | 0 | 0 | 0 | 0 | 0.38
121 | ABT Energy meter for feeders | 0 | 0 | 0 | 0 | 522752.86
122 | L&T Make:CN-CS-1250H type Breaker. | 0 | 0 | 0 | 0 | 0.4
123 | Out door radio modem unit for 25Mbps | 0 | 0 | 0 | 253215 | 0
124 | PACKAGE PROJECT FOR SUPPLY, ERECTION, COMMISSION AND OPERATION OF CAAQMS | 0 | 0 | 0 | 0 | 12641317.5
125 | DM Transmitter Model: 1056-01-20-32-AN+PH+Conductivity sensor | 0 | 0 | 0 | 0 | 7541.26
126 | Guided Wave Radar Level Transmitter for Measuring SILO LEVEL. | 0 | 0 | 0 | 0 | 0
127 | Single acting smart positioner for drain valves as per spec | 0 | 0 | 0 | 0 | 154848.32
128 | DPU 4F Primary Module- MODULE NO: 69230D401B, TYPE: PDP401 | 0 | 0 | 0 | 0 | 175837.56
129 | Prop. Directional Valve, Type: G631-XXXXX-H-75-J-O-F-M-4-V-B-Q | 0 | 0 | 0 | 0 | 0
130 | DUAL SIESMIC MONITOR MAKE:SHINKAWA, MODEL: VM-5U-221110-000-001-0 | 0 | 0 | 0 | 0 | 1572671.2
131 | Communication between IAC/SAC and main DCS. | 0 | 0 | 0 | 0 | 9313.3
132 | 415 V,145 KW,TEFC SQUIRREL CAGE INDUCTION MOTOR . | 0 | 0 | 0 | 0 | 0
133 | AUMA Actuator Model SA30A90. | 0 | 0 | 0 | 241269.54 | 0
134 | Fan Transformer 3-phase 500-690VAC | 0 | 0 | 0 | 21690.69 | 0
135 | Fan for framesize g,h and j, Part for Siemens Make VFD Unit. | 0 | 0 | 0 | 29375.94 | 0
136 | ABT METER READING INSTRUMENT FOR L&T ABT METERS | 0 | 0 | 0 | 118125 | 0
137 | Fan Transformer 3 phase 380-480 VAC, 50/60 Hz | 0 | 0 | 0 | 18612.64 | 0
138 | 400Volts, 75KW, Frame 280S, 4P, Motor for Bucket Wheel of SCR | 0 | 0 | 0 | 62788.49 | 0
139 | 400Volts, 22KW, Frame 180L, 4P, Motor for Slew of SCR | 0 | 0 | 0 | 15629.5 | 0
140 | 400Volts, 55KW, Frame 250M, 4P, Motor for Boom Conveyor of SCR | 0 | 0 | 0 | 52272.51 | 0
141 | Commulating Choke for SCR | 0 | 0 | 0 | 0 | 0
142 | Convertor for SCR | 0 | 0 | 0 | 18695.97 | 0
143 | VACCUME CONTACTOR ,3TF69 44-0C,110V AC,make:Siemens. | 0 | 0 | 0 | 0 | 0
144 | 415Volts, 75kW, 6pole, Frame 315S motor for RWP | 0 | 0 | 0 | 0 | 0
145 | 110KW,415V,4 Pole,ND315S,Delta connection,Hydrant pump Motor. | 0 | 0 | 0 | 66697.81 | 0
146 | ID FanMotor, 690 V, 800 KW, 8 Pole Horizondal mounted Cage motor | 0 | 0 | 0 | 6742297.56 | 0
147 | 37Kw Motor,415V,2Pole,Conn:Delta,Fr:200L-Fire BoosterPump Motor | 0 | 0 | 0 | 16588.37 | 0
148 | Out door radio modem unit for 50Mbps | 0 | 0 | 0 | 133875 | 0
149 | ONLINE OXYGEN ANALYSER AS PER TECHNICAL SPECIFICATIONS | 0 | 0 | 0 | 626063 | 0
150 | Nafion dryer Make Perma pure Model: PD-100T-24MKA as per spec | 0 | 0 | 0 | 533058 | 0
151 | DCS Engineer Work Station as per spec. | 0 | 0 | 0 | 563337.5 | 0
152 | Main PC Control circut Card for Spider Control,ver 4.2.1,rev:R2D | 0 | 0 | 0 | 601536.42 | 0
153 | Combox(Gateway MK5),Part no: 2230006800 | 0 | 0 | 0 | 138680.1 | 0
154 | Housing Vibration Module, MODEL NO: 3500/42-01-00 | 0 | 0 | 0 | 80889.6 | 0
155 | DUAL SIESMIC MONITOR MAKE:SHINKAWA, MODEL: VM-5U-921110-000-001-0 | 0 | 0 | 0 | 1397930.08 | 0
156 | VM-5 SERIES INSTRUMENT RACK MAKE: SHINKAWA, MODEL: VM-5W1-0 | 0 | 0 | 0 | 226746 | 0
157 | HYDRAULIC DEAD WEIGHT TESTER AS PER SPECIFICATIONS | 0 | 0 | 0 | 205491 | 0
158 | Electronic Water Drain for SAC part no. 8102042630 | 0 | 227140.27 | 227139.98 | 144507.46 | 0
159 | LIGNITE BUNKER WEIGHT CALIBRATION UNIT AS PER SPEC | 0 | 0 | 0 | 551775 | 0
160 | LIGNITE BUNKER WEIGHING INDICATORS AS PER SPEC | 0 | 0 | 0 | 323400 | 0
161 | Flexible connector for Equipment complete set-2500A | 0 | 0 | 0 | 0 | 0
162 | Flexible connector for Equipment complete set-1600A | 0 | 0 | 0 | 0 | 0
163 | MOP/LOP(AC) 37KW Motor | 0 | 0 | 0 | 0 | 125766
164 | AUMA Actuator Model No SAR12B45 | 0 | 343857.22 | 361583.45 | 0 | 0
165 | AUMA Actuator whole assembly Type SA15AF32+Epac . | 0 | 0 | 198179.22 | 0 | 0
166 | Auma actuator whole assembly model SA12E125+TBG. | 0 | 0 | 144635.15 | 0 | 0
167 | AUMA Actuator model SA50-E-90 . | 0 | 0 | 0 | 0 | 0
168 | Gear Box for actuator SA50-E-90 . | 0 | 0 | 0 | 0 | 0
169 | LIMITORQUE MAKE ELECTICAL ACTUATOR MODEL NO. SMB-2-60/4 | 0 | 0 | 26495.97 | 0 | 0
170 | 245 KV,triple pole, Centre Post Rotating Double Break Isolators | 0 | 0 | 0 | 0 | 0
171 | Snubber Board | 0 | 0 | 101322.9 | 0 | 0
172 | ARECA CONTROLLER WITH FIRING CARD | 0 | 0 | 619682.57 | 0 | 0
173 | 6.6kV 415kW 3Phase Squirrel Cage Induction Motor Frame TS500L2. | 37455.13 | 1876679 | 231000 | 0 | 0
174 | Stall Torque motor; SBS -125B4 ; Torque: 9.7NM for SCR | 0 | 0 | 39990.68 | 0 | 0
175 | Stall Torque motor; SBS -100B4 ; Torque: 4.3NM | 0 | 0 | 0 | 0 | 0
176 | 6.6KV Grade Slip Ring Assembly for PCRD | 0 | 0 | 0 | 0 | 0
177 | 1.1KV Grade Slip Ring Assembly for CCRD | 0 | 0 | 0 | 0 | 0
178 | BTS2000 BUS TRANSFER SYSTEM MAIN MODULE | 0 | 0 | 1388520 | 0 | 0
179 | 760KW,6.6KV CWP MOTOR | 0 | 0 | 2985613.4 | 0 | 0
180 | 55 kW motor,415v,4Pole, Fr:D280S - CT Fan motor | 0 | 0 | 0 | 0 | 219000
181 | Quantar Repeater | 0 | 0 | 1799280 | 0 | 0
182 | 415V, 160KW, 315L, 4Pole, Motor for Fly Ash/Bed Ash Compressor | 0 | 0 | 0 | 0 | 0
183 | 6.6KV, 185KW, 315F, 4Pole Motor for Fly Ash Stg 2 Compressor | 0 | 0 | 134476.8 | 0 | 0
184 | RA#5 SIEMENS SITRANS probe LU Transmitter 7M5221-2BA11 | 0 | 0 | 21164.45 | 0 | 0
185 | GUIDED WAVE RADAR LEVEL TR. | 0 | 0 | 211017.2 | 0 | 0
186 | Flow meter for Circulating water forebay makeup water. | 0 | 0 | 261816.78 | 0 | 0
187 | Flow meter for Boiler blow down (Intermediate blow down). | 0 | 0 | 682914.26 | 0 | 0
188 | DM Conductivity Transmitter Model: 1056-01-22-30-AN +P/N 23820-00 | 0 | 0 | 385716.02 | 0 | 0
189 | LPG Pilot Gas Ignitor ZA1- 150 P/K0K5M | 1087163 | 790473.24 | 805024.65 | 1423421 | 0
190 | RA#3 compressor Local opertor panel for ZR-37,GA160W,GA200W. | 0 | 0 | 526146.66 | 0 | 0
191 | CPU 360 MODULE MAKE :GE MODEL NO: IC693CPU360 | 0 | 0 | 0 | 0 | 0
192 | GENIUS BUS CONTROLLER MAKE:GE,MODEL NO: IC693BEM331 | 0 | 0 | 0 | 0 | 0
193 | Siemens PLC, MONOMODE PROFIBUS OLM G12-1300 | 0 | 0 | 40844.7 | 0 | 0
194 | Siemens PLC,CP1613 FOR Industrial Ethernet Communication | 0 | 0 | 28089.85 | 0 | 0
195 | Siemens PLC,Communication processor CP 341-1,(POINT TO POINT LINK) | 0 | 0 | 14940.98 | 0 | 0
196 | Siemens PLC, Y-LINK | 0 | 0 | 190706.28 | 0 | 0
197 | Siemens PLC - Function Module , FM350-2 COUNTER in JNT & screen | 0 | 0 | 0 | 0 | 118079.31
198 | PLC HMI Operator\Engineer work station(OWS\EWS) as per spec. | 0 | 0 | 696250 | 0 | 0
199 | LIMITORQUE MAKE ELECTICAL ACTUATOR MODEL NO. SMB-3-150/4 | 0 | 66657.83 | 0 | 0 | 0
200 | BFP SCOOP MOTOR ACTUATOR ABB MAKE MODEL -RHD250 | 0 | 1064852.22 | 0 | 0 | 0
201 | BFP SCOOP CONTROL SUPPLY UNIT ABB MAKE MODEL -EBN853 | 0 | 765698.69 | 0 | 0 | 0
202 | Current Transformer for Inter Bus Transformers | 0 | 0 | 0 | 0 | 0
203 | Current Transformer for GTs and Feeders. | 0 | 0 | 0 | 0 | 0
204 | ED7470400311 DIGITAL AVR DC-DC SUPPLY MODULE | 0 | 455428.34 | 0 | 0 | 0
205 | ED7470400141 AVR FIRING &CONTROL MODULE | 0 | 578332.46 | 0 | 0 | 0
206 | ED7470400133 AVR CPU MODULE | 0 | 469562.32 | 0 | 0 | 0
207 | CN 9090389300 PULSE FINAL STAGE | 0 | 105219.65 | 0 | 0 | 0
208 | ED7470400290 16 CHANNEL BINARY OUT PUT MODULE | 0 | 170332.61 | 0 | 0 | 0
209 | ED7470400168 DAVR INT GEN MODULE | 0 | 0 | 0 | 0 | 0
210 | ED7470400281 DAVR I/O MODULE | 0 | 74088.79 | 0 | 0 | 0
211 | CN9090433503 PULSE COUP STAGE MODULE | 0 | 0 | 0 | 0 | 0
212 | ED9090334114,AC/DC-DC CONVERTOR MODULE | 0 | 326796.05 | 0 | 0 | 0
213 | CN9090110704 PULSE SUPERVISION MODULE | 0 | 0 | 156809.39 | 0 | 0
214 | ED7470400206 DAVR 16 CHANNEL O/P MDL | 0 | 0 | 0 | 0 | 0
215 | SA0653980205,AC ISOLATOR 3 POLE WITH MICRO SWITCH | 0 | 0 | 0 | 0 | 0
216 | 3 PH, 6.6 KV, 180 KW, B3, 4 P, S1, IP 55, S.C. IND. MOTOR | 0 | 9546.76 | 0 | 0 | 0
217 | 415kV, 75kW 3Phase Squirrel Cage Induction Motor, Frame 280M | 0 | 0 | 0 | 0 | 0
218 | 415kV,90kW, 3Phase Squirrel Cage Induction Motor, Frame 315S | 0 | 0 | 0 | 0 | 0
219 | 415kV, 55kW 3Phase Squirrel Cage Induction Motor, Frame 280S | 0 | 0 | 0 | 0 | 0
220 | 415kV,160 kW, 3Phase Squirrel Cage Induction Motor, Frame 355L | 0 | 0 | 0 | 0 | 0
221 | Siemens make ACB 800amps for stacker cum reclaimer. | 0 | 5513.59 | 0 | 0 | 0
222 | GE 800 A Spectronic ACB with LMZ7 | 0 | 0 | 0 | 0 | 0
223 | Durag Make Flame Scanner Unit, Model: D-LE-603-UA-P. | 0 | 481441.16 | 0 | 0 | 0
224 | Durag Make Flame Control Unit, Model-D-UG 660 -115A-420 | 165268 | 355282.68 | 0 | 0 | 0
225 | KELTRON Pneumatic Actuator Model No.C0608 252239 for SUB SA | 0 | 0 | 0 | 0 | 0
226 | KELTRON Pneumatic Actuator Model No.C0816 352239 for CombustorSAD | 0 | 5421.19 | 0 | 0 | 0
227 | Pneumatic Actuator for Sec. Air IGV, Keltron, C1216442239 | 0 | 18996.79 | 0 | 0 | 0
228 | PFT ,Indigenous Equivalent to CCI ,make:MASS ModelMG-10+4K | 0 | 367200 | 0 | 0 | 0
229 | BFP SCOOP PFT ABB MAKE PART NO 764975 | 0 | 218905.01 | 0 | 0 | 0
230 | MID VALUE SELECTOR MODULE ED69229S901A | 0 | 0 | 0 | 0 | 0
231 | 1 OF 3 I/P SELECTION MODULE ED69229S902A FOR TURBINE-DCS | 0 | 0 | 0 | 0 | 0
232 | POSITION MEASUREMENT MODULE ED69229S910A FOR TURBINE-DCS | 0 | 72055.36 | 0 | 0 | 0
233 | POSITION CONTROL MODULE ED69229S914A FOR TURBINE DCS | 0 | 0 | 0 | 0 | 0
234 | Antivirus server for DCS network | 0 | 663211.18 | 0 | 0 | 0
235 | GE PLC Series 90-30 ETHERNET INTERFACE TCP/IP MODULE, IC693CMM321 | 0 | 16888.56 | 0 | 0 | 0
236 | GE PLC Series 90-30 Genius Bus Controller,IC693BEM331. | 0 | 10520.85 | 0 | 0 | 0
237 | GE PLC Rx3i Ethernet Module IC695ETM001,used at AHS PLC,SILO. | 0 | 9632.66 | 0 | 0 | 0
238 | Regulator ELECTRONIKON IIID for SAC 1900071032. | 0 | 0 | 151002.94 | 0 | 0
239 | REGULATOR for SAC part no. 1900071082 | 0 | 0 | 0 | 0 | 134135.55
240 | ALARM UNIT for SAC part no. 1089045770 | 0 | 0 | 0 | 0 | 117999.39
241 | Regulator ELECTRONIKON IIID for IAC 1900071032 | 0 | 0 | 149537.92 | 0 | 0
242 | Rotork Actuator Type K1000F16A | 0 | 0 | 0 | 0 | 0
243 | Rotork Actuator type K300F14E | 119669.73 | 0 | 0 | 0 | 0
244 | Rotork Actuator type K600F14A | 0 | 0 | 0 | 0 | 0
245 | Rotork Actuator type K300F14A | 121158.5 | 0 | 0 | 0 | 0
246 | Rotork Actuator type K500G3A | 0 | 0 | 0 | 0 | 0
247 | E+H Liquicap Level Transmitter for Turbine Main Oil Tank | 101120.5 | 0 | 0 | 0 | 0
248 | Level control unit for Bunker Level, Endress+Hauser Make | 0 | 109250.55 | 0 | 0 | 0
249 | Ultrosonic Level Probe for Bunker Level, Make: Endress+Hauser | 0 | 213361.45 | 0 | 0 | 0
250 | DVC-6010 AD, Smart Positioner: Thum Adapter, Make Fisher | 148609 | 0 | 0 | 258794 | 0
251 | SMART POSITIONER FOR MASONEILAN CONTROL VALVE | 177826.9 | 0 | 0 | 0 | 0
252 | PI servo amplifier, Make: MOOG,Model G122-829-001 | 0 | 0 | 0 | 0 | 0
(D) | Details of capital spares closing at the end of the year
1 | Non metallic expansion joint for Cyclone and flue gas duct | 909450.39 | 1956324.5 | 582961 | 582961 | 291480.5
2 | Non metallic expansion joint for Flue gas duct and and back pass | 586846.01 | 586846.01 | 586846.01 | 586846.01 | 586846.01
3 | SERVO VALVE ST 10-4 | 176311.28 | 176311.28 | 176311.28 | 0 | 0
4 | HP Element for service air compressor ZR 500 | 1387994 | 1387994 | 1387994 | 1387994 | 1387994
5 | Input Shaft for Intermediate conveyor Gear box | 289993 | 289993 | 289993 | 289993 | 289993
6 | ASH INTAKE VALVE COMPLETE ASSEMBLY. | 133965.63 | 133965.63 | 133965.62 | 979910.5 | 0
7 | FRP Blades for CT Fan | 0 | 563739 | 0 | 1441034.38 | 1759791
8 | Fluid Coupling 500 SDFC | 0 | 140058 | 140058 | 140058 | 140058
9 | Gear Box (B2SF-160) for Belt Feeder of Stacker Cum Reclaimer | 0 | 1172124 | 1172124 | 1172124 | 1172124
10 | Intermediate conveyor gearbox for SCR | 0 | 2460762 | 2460762 | 2460762 | 2460762
11 | Oil cooler for GA200W compressor- 7.5bar | 0 | 481343.08 | 240671.54 | 240671.54 | 0
12 | After cooler for GA200W compressor- 7.5bar | 0 | 361006.92 | 361006.92 | 361006.92 | 0
13 | Oil gun assembly for start up burner. | 0 | 197738.31 | 197738.31 | 0 | 312923.26
14 | Complete set of chain assembly for TRC. | 0 | 0 | 1980582 | 0 | 0
15 | Complete set of chain assembly for Lignite Extraction feeder. | 0 | 0 | 1895734 | 0 | 0
16 | Non metallic expansion joint for Between combustor and cyclone | 0 | 0 | 1557999 | 1686745 | 0
17 | Cartridge assembly for HFO pressurising pump model no:T3ST 70/46. | 0 | 0 | 434861 | 434861 | 434861
18 | Cartridge Assembly for LDO Pressurising pump model no:T3S T45/46. | 0 | 0 | 237832.4 | 0 | 0
19 | MOT Centrifuge- Major service kit | 0 | 0 | 203969.98 | 203969.98 | 203969.98
20 | MOT Centrifuge-Inlet pipe with parting disc | 0 | 0 | 471241.91 | 471241.91 | 471241.91
21 | Rexroth Axial Piston Pump-Control Oil Tank. | 0 | 0 | 178453.76 | 178453.76 | 178453.76
22 | HP BYPASS QUICK STROKING DEVICE SSB 10. | 0 | 0 | 244697.72 | 244698 | 0
23 | HP BY PASS SYSTEM SERVO VALVE (MAIN -BP) ST 10 -63. | 0 | 0 | 207213 | 414426.4 | 0
24 | HP BYPASS SPARE- AXIAL PISTON | 0 | 0 | 173400 | 173400 | 0
25 | DMCW . BOOSTER PUMP(Hor. Split Case Pump).PUMP SHAFT. | 0 | 0 | 109001.54 | 109001.54 | 109001.54
26 | Top Shaft sleeve for Circulating Water Pump | 0 | 0 | 112901.79 | 112901.79 | 112901.79
27 | Imp.shaft sleeve for Circulating Water Pump | 0 | 0 | 118592.29 | 118592.29 | 0
28 | Rubber Bearing for Circulating Water Pump | 0 | 0 | 107972.91 | 107972.91 | 0
29 | Main oil pump- EBFP | 0 | 0 | 356028 | 356028 | 356028
30 | Auxiliary Lub Oil Pump for EBFP | 0 | 0 | 383836 | 383836 | 383836
31 | EBFP SPARE- BALANCE DRUM BUSHING | 0 | 0 | 100580.85 | 100580.85 | 100580.85
32 | Resilient coupling 127S GBM Make or equivalent for BCN-18A/B | 0 | 0 | 269279.9 | 269279.9 | 269279.9
33 | Resilient coupling 126S GBM Make or equivalent for BCN-1A,BCN-7A/B | 0 | 0 | 182784 | 182784 | 182784
34 | Resilient coupling 125S GBM Make or equivalent for BCN-11A/B,BCN-19A/B,BCNLS-1 | 0 | 0 | 140760 | 140760 | 140760
35 | Resilient coupling 125S GBM Make or equivalent for BCN-4A/B | 0 | 0 | 140760 | 140760 | 140760
36 | Roller Shaft Assembly for Roller Screen | 0 | 0 | 2063765 | 2063765 | 1719804.17
37 | DRIVE PULLEY OF SIZE: DIA 1024 X 1200MM X16T | 0 | 0 | 327930 | 327930 | 327930
38 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 824 X 1400MM X16T | 0 | 0 | 560280 | 560280 | 0
39 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 824 X 1200MM X16T | 0 | 0 | 372394.48 | 372394.48 | 372394.48
40 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 524 X 1400MM X12T | 0 | 0 | 262926.52 | 262926.52 | 0
41 | TAKE-UP PULLEY OF SIZE : DIA 824 X 1400MM X16 MM T | 0 | 0 | 414359.69 | 414359.69 | 0
42 | TAKE-UP PULLEY OF SIZE: DIA 654 X 1200MM X 12MM T | 0 | 0 | 205773.47 | 205773.47 | 205773.47
43 | TAKE-UP PULLEY OF SIZE: DIA 824 X 1200MM X12 MM T | 0 | 0 | 255838.64 | 255838.64 | 255838.64
44 | TAKE-UP PULLEY OF SIZE: DIA 524 X 1200MM X12 MM T | 0 | 0 | 191260.2 | 191260.2 | 191260.2
45 | SDFC 450 Fluid coupling assembly | 0 | 0 | 125491 | 125491 | 125491
46 | HAND OPERATED 4 INCH CCS WCB 2500 CLASS GATE VALVE. | 0 | 0 | 139067.86 | 0 | 0
47 | NRV SIZE: 4" CCS VALVE WCB SWING CHECK TYPE CLASS RATING 2500. | 0 | 0 | 218754.14 | 0 | 0
48 | Oil Separator for GA 200 W | 0 | 0 | 140692.15 | 140692.15 | 0
49 | Mechanical seal Ebil make,Type:H75/65 (Pump 45KW) | 0 | 0 | 389025.74 | 389025.74 | 0
50 | Mechanical seal Ebil make,Type:H75/40 (Pump 22KW) | 0 | 0 | 110896.07 | 110896.07 | 0
51 | Complete set of chain assembly for DCC | 0 | 0 | 0 | 1112262 | 1112262
52 | Screw set (AISI 410) of LDO decanting pump . | 0 | 0 | 0 | 351436.22 | 351436.22
53 | Safety Relief Valve for jack oil system size 3/4"X 1". | 0 | 0 | 0 | 182106 | 182106
54 | AUXILIARY LUB OIL PUMP FOR BOILER FEED PUMP | 0 | 0 | 0 | 323830 | 323830
55 | Complete Mechanical Seal for Boiler Feed Pump DE | 0 | 0 | 0 | 181444.01 | 0
56 | Complete Mechanical Seal for Main Boiler Feed Pump NDE | 0 | 0 | 0 | 186261.71 | 0
57 | Complete Mechanical Seal for Booster Pump DE of Feed Pump | 0 | 0 | 0 | 101358.8 | 0
58 | Complete Mechanical Seal for Booster Pump NDE of Feed Pump | 0 | 0 | 0 | 101358.8 | 101358.8
59 | Thrust Pad set for Bearing 5 SLT of CEP Model EN7H32 | 0 | 0 | 0 | 397500.5 | 397500.5
60 | Journal pad set for Bearing 5 SLT of CEP Model EN7H32 | 0 | 0 | 0 | 358919.5 | 358919.5
61 | Butterfly Valve 800 NB | 0 | 0 | 0 | 276206 | 276206
62 | Bevel Gear Pair for Cooling Tower Fan Gear Box. | 0 | 0 | 0 | 541711.8 | 361141.2
63 | Second Stage Wheel for Cooling Tower Fan Gear Box. | 0 | 0 | 0 | 135645.98 | 281320.22
64 | Drive Sheave for Toothed Double Roll Crusher | 0 | 0 | 0 | 366265.52 | 366265.52
65 | Roller Shaft for Primary Roller Screen | 0 | 0 | 0 | 973446.12 | 973446.12
66 | Main Drive Shaft for Flip Flow Screen | 0 | 0 | 0 | 217281.75 | 217281.75
67 | Thrust Rod System for Flip Flow Screen | 0 | 0 | 0 | 118517.21 | 118517.21
68 | Hydraulic Pump Complete P6S-2R1C-9A2-B00-0A1-M2-07704 | 0 | 0 | 0 | 1373848 | 0
69 | Non- Magnetic DRIVE PULLEY OF SIZE: DIA 824 X 1200MM X16T | 0 | 0 | 0 | 353735.8 | 353735.8
70 | Non magnetic DRIVE PULLEY OF SIZE: DIA 1024 X 1200X16MM T | 0 | 0 | 0 | 586500 | 586500
71 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 654 X 1200MM X12T | 0 | 0 | 0 | 242066 | 242066
72 | TAIL PULLEY (MOUNTED ON BEARINGS )OF SIZE:DIA 524X1400MMX16T(SCR) | 0 | 0 | 0 | 130305 | 130305
73 | TAKE PULLEY OF SIZE: DIA 524 X 1200MM X16T(SCR) | 0 | 0 | 0 | 138363 | 138363
74 | DISCHARGE PULLEY(MOUNTED ON BEARINGS)OF SIZE: DIA1024X1200MMX20T | 0 | 0 | 0 | 445944 | 445944
75 | TAIL PULLEY (MOUNTED ON BEARINGS ) OF SIZE: DIA 654 X 1200MMX20T | 0 | 0 | 0 | 214607.6 | 214607.6
76 | DRIVE PULLEY OF SIZE: DIA 654 X 1200MMX20T(SCR) | 0 | 0 | 0 | 183600 | 183600
77 | DRIVE PULLEY OF SIZE: DIA 524 X 1400MM X16T(SCR) | 0 | 0 | 0 | 127131.78 | 127131.78
78 | TAIL PULLEY (MOUNTED ON BEARINGS )OF SIZE:DIA654X1200MMX16T(SCR) | 0 | 0 | 0 | 191821.2 | 0
79 | BEND PULLEY (MOUNTED ON BEARINGS)OF SIZE:DIA824X1200MMX20T(SCR) | 0 | 0 | 0 | 344056.2 | 344056.2
80 | SNUB PULLEY(MOUNTED ON BEARINGS)OF SIZE:DIA424X1200MMX16.7T(SCR) | 0 | 0 | 0 | 138536.4 | 138536.4
81 | BEND PULLEY (MOUNTED ON BEARINGS)OF SIZE:DIA524X1200MMX16T(SCR) | 0 | 0 | 0 | 164464.8 | 164464.8
82 | Input shaft with pinion & key for H3-280 Ratio 23.016:1 | 0 | 0 | 0 | 133489.27 | 133489.27
83 | Input shaft with pinion & key for H3-280 Ratio 34.984:1 | 0 | 0 | 0 | 133489.27 | 133489.27
84 | Input shaft with pinion & key for H3-315 Ratio 22.433:1 | 0 | 0 | 0 | 197900 | 197900
85 | Input shaft with pinion & key for H3-400 Ratio 28.4:1 | 0 | 0 | 0 | 326096 | 326096
86 | Input shaft with pinion & key for H3-500 Ratio 28.4:1 | 0 | 0 | 0 | 540282.46 | 540282.46
87 | 570 PST Coupling Set With Essential accessories | 0 | 0 | 0 | 688207.99 | 0
88 | Fluid coupling SDFC 410 assembly | 0 | 0 | 0 | 102483 | 102483
89 | Horizontal centrifugal pump for transferring Degassed water. | 0 | 0 | 0 | 267220.39 | 0
90 | Top Shaft with sleeve for Raw water Pump | 0 | 0 | 0 | 147779.93 | 0
91 | Line Shaft with its sleeve for Raw water Pump. | 0 | 0 | 0 | 414234.52 | 0
92 | COMBUSTOR SPIESS VALVE LANCE TIP | 0 | 0 | 0 | 0 | 393592.5
93 | Triplex sprocket forLignite transport conveyor drive shaft. | 0 | 0 | 0 | 0 | 364493.01
94 | Triplex sprocket for lignite extraction conveyor. | 0 | 0 | 0 | 0 | 1361315.26
95 | DRIVING SIDE LINER ASSEMBLY FOR SECONDARY AIR FAN. | 0 | 0 | 0 | 0 | 606782
96 | MODULAR HOUSING FOR DRIVE END DODGE SLEEVOIL BEARING RTL 5*7/16 . | 0 | 0 | 0 | 0 | 434059
97 | THURST PLATE KIT FOR DODGE SLEEVOIL BEARING RTL 4*7/16 . | 0 | 0 | 0 | 0 | 117006
98 | Triplex sprocket for DCC drive shaft. | 0 | 0 | 0 | 0 | 524309.16
99 | Bed material Bare rotary Air lock feeder without drive. | 0 | 0 | 0 | 0 | 500871.09
100 | Bare Pump without motor of LDO decanting pump. | 0 | 0 | 0 | 0 | 793997
101 | Set of lobe with shaft (1 set =2 nos) bed ash conveying blower. | 0 | 0 | 0 | 0 | 135546.32
102 | Set of gear ( 1 set = 2 nos) for bed ash conveying blower . | 0 | 0 | 0 | 0 | 112096.71
103 | Lifting oil to turning gear, Solenoid valve assembly. | 0 | 0 | 0 | 0 | 763087.61
104 | HP bypass system , Stem for BP VALVE , Type: ARS 80. | 0 | 0 | 0 | 0 | 269687.8
105 | HP bypass system , Jet cage for BP Valve , Type: ARS 80. | 0 | 0 | 0 | 0 | 189720
106 | HP bypass system ,Seat for BPE VALVE (Spray valve), Type: E 32 S. | 0 | 0 | 0 | 0 | 193800
107 | Thrust bearing for boiler feed pump FK6D30 | 0 | 0 | 0 | 0 | 279990.12
108 | Lower Shaft for condensate extraction pump EN7H32 | 0 | 0 | 0 | 0 | 283432.5
109 | Upper Shaft for condensate extraction pump EN7H32 | 0 | 0 | 0 | 0 | 294907.5
110 | Hotwell make up pump assembly without motor. | 0 | 0 | 0 | 0 | 1079916
111 | Gear Box Assembly for Cooling Tower Fan. | 0 | 0 | 0 | 0 | 2067739.79
112 | Head Shaft for Fire Hydrant Pump | 0 | 0 | 0 | 0 | 110030
113 | INTERMEDIATE SHAFT for Hydrant Fire Pump(KBL pump,Type:BHR 28-30) | 0 | 0 | 0 | 0 | 129965.76
114 | Flange with internal spline for Turbine Shaft Turning Gear | 0 | 0 | 0 | 0 | 276516.54
115 | Flange between hydromotor&over running clutch for STG | 0 | 0 | 0 | 0 | 355226.47
116 | Shaft of hydraulic motor for Turbine Shaft Turning Gear | 0 | 0 | 0 | 0 | 147868.55
117 | Shaft of Over Running Clutch for Turbine Shaft Turning Gear | 0 | 0 | 0 | 0 | 695671.44
118 | Grinding Jip carrier | 0 | 0 | 0 | 0 | 1280235.81
119 | Shaft Seal Kit, HD Item no : 478 2277 -964 | 0 | 0 | 0 | 0 | 359820
120 | Seal Kit Pump Complete, HD Item no: 478 3233 -146 | 0 | 0 | 0 | 0 | 161668.47
121 | Hydraulic Motor CA 210 210 CB0NHC0200 with brake | 0 | 0 | 0 | 0 | 5873932
122 | DRIVE PULLEY OF SIZE: DIA 824 X 1200MMX20T(SCR) | 0 | 0 | 0 | 0 | 473813
123 | Bevel pinion shaft assembly for B3-180 & bevel wheel | 0 | 0 | 0 | 0 | 441556.94
124 | Bevel pinion shaft assembly for B3-180 ratio 31.103:1 | 0 | 0 | 0 | 0 | 224227.94
125 | Bevel pinion shaft assembly for B3-200 gear box | 0 | 0 | 0 | 0 | 263784.46
126 | Bevel pinion shaft assembly for B3-160 gear box | 0 | 0 | 0 | 0 | 201492.42
127 | Bevel pinion shaft assembly for B3-140 gear box | 0 | 0 | 0 | 0 | 182406.96
128 | Bevel pinion shaft assembly for B3-280 gear box | 0 | 0 | 0 | 0 | 408480.28
129 | Thrust stand assembly (Part No:34) for Raw water pump | 0 | 0 | 0 | 0 | 1692204.7
130 | Thrust bearing housing assembly. | 0 | 0 | 0 | 0 | 318582.37
131 | Thrust bearing housing assembly. | 0 | 0 | 0 | 0 | 318582.37
132 | Wear ring casing for ACW pump | 0 | 0 | 0 | 0 | 186155.32
133 | Bearing sealing ring, Part No: HY11390131083 | 0 | 0 | 0 | 0 | 1951209.04
134 | Labyrinth ring for bearing shell Part No: HY31390131116 | 0 | 0 | 0 | 0 | 1085535.23
135 | Generator fan blades TE, Part No: HY9316103002 | 0 | 0 | 0 | 0 | 994308.9
136 | Generator fan blades EE, Part No: HY9316103010 | 0 | 0 | 0 | 0 | 994308.9
137 | Adjusting steel for bearing pedestal, Part No: HY31390131118 | 0 | 0 | 0 | 0 | 0
138 | Generator Bearing insulation. Part No: HY1390131020 | 0 | 0 | 0 | 0 | 0
139 | Rotork Actuator Type K30G0A | 0 | 0 | 0 | 0 | 101236.11
140 | Rotork Actuator Type K150F10A | 0 | 0 | 0 | 0 | 112272.1
141 | Make:E/R ,Num.Dir.IDMTL 3O/C+1E/F Highset Relay,Type:ARGUS 2 | 0 | 0 | 0 | 0 | 108896.94
142 | Motor Protection Relay,Type:AMV2-1A, P&B MAKE | 0 | 0 | 0 | 0 | 152210
143 | Feeder Protection Relay, Type -AFV2-1A, P&B MAKE | 0 | 0 | 0 | 0 | 162707
144 | ABT Energy meter for feeders | 0 | 0 | 0 | 0 | 320931.14
145 | L&T Make:CN-CS-1250H type Breaker. | 0 | 0 | 0 | 0 | 151793
146 | Out door radio modem unit for 25Mbps | 0 | 0 | 0 | 0 | 235620
147 | PACKAGE PROJECT FOR SUPPLY, ERECTION, COMMISSION AND OPERATION OF CAAQMS | 0 | 0 | 0 | 0 | 0
148 | DM Transmitter Model: 1056-01-20-32-AN+PH+Conductivity sensor | 0 | 0 | 0 | 0 | 168954
149 | Guided Wave Radar Level Transmitter for Measuring SILO LEVEL. | 0 | 0 | 0 | 0 | 222787
150 | Single acting smart positioner for drain valves as per spec | 0 | 0 | 0 | 0 | 398400
151 | DPU 4F Primary Module- MODULE NO: 69230D401B, TYPE: PDP401 | 0 | 0 | 0 | 0 | 1828427
152 | Prop. Directional Valve, Type: G631-XXXXX-H-75-J-O-F-M-4-V-B-Q | 0 | 0 | 0 | 0 | 260000
153 | DUAL SIESMIC MONITOR MAKE:SHINKAWA, MODEL: VM-5U-221110-000-001-0 | 0 | 0 | 0 | 0 | 0
154 | Communication between IAC/SAC and main DCS. | 0 | 0 | 0 | 0 | 230318
155 | 415 V,145 KW,TEFC SQUIRREL CAGE INDUCTION MOTOR . | 0 | 0 | 0 | 375232 | 375232
156 | AUMA Actuator Model SA30A90. | 0 | 0 | 0 | 155254.5 | 155254.5
157 | Fan Transformer 3-phase 500-690VAC | 0 | 0 | 0 | 120104.85 | 120104.85
158 | Fan for framesize g,h and j, Part for Siemens Make VFD Unit. | 0 | 0 | 0 | 162659.28 | 162659.28
159 | ABT METER READING INSTRUMENT FOR L&T ABT METERS | 0 | 0 | 0 | 0 | 0
160 | Fan Transformer 3 phase 380-480 VAC, 50/60 Hz | 0 | 0 | 0 | 103061.14 | 103061.14
161 | 400Volts, 75KW, Frame 280S, 4P, Motor for Bucket Wheel of SCR | 0 | 0 | 0 | 453079.99 | 453079.99
162 | 400Volts, 22KW, Frame 180L, 4P, Motor for Slew of SCR | 0 | 0 | 0 | 112782.03 | 112782.03
163 | 400Volts, 55KW, Frame 250M, 4P, Motor for Boom Conveyor of SCR | 0 | 0 | 0 | 377196.98 | 377196.98
164 | Commulating Choke for SCR | 0 | 0 | 0 | 160051.5 | 160051.5
165 | Convertor for SCR | 0 | 0 | 0 | 976518.04 | 976518.04
166 | VACCUME CONTACTOR ,3TF69 44-0C,110V AC,make:Siemens. | 0 | 0 | 0 | 204750.15 | 204750.15
167 | 415Volts, 75kW, 6pole, Frame 315S motor for RWP | 0 | 0 | 0 | 259781 | 259781
168 | 110KW,415V,4 Pole,ND315S,Delta connection,Hydrant pump Motor. | 0 | 0 | 0 | 476410 | 476410
169 | ID FanMotor, 690 V, 800 KW, 8 Pole Horizondal mounted Cage motor | 0 | 0 | 0 | 0 | 0
170 | 37Kw Motor,415V,2Pole,Conn:Delta,Fr:200L-Fire BoosterPump Motor | 0 | 0 | 0 | 118489 | 118489
171 | Out door radio modem unit for 50Mbps | 0 | 0 | 0 | 0 | 0
172 | ONLINE OXYGEN ANALYSER AS PER TECHNICAL SPECIFICATIONS | 0 | 0 | 0 | 0 | 0
173 | Nafion dryer Make Perma pure Model: PD-100T-24MKA as per spec | 0 | 0 | 0 | 0 | 0
174 | DCS Engineer Work Station as per spec. | 0 | 0 | 0 | 0 | 0
175 | Main PC Control circut Card for Spider Control,ver 4.2.1,rev:R2D | 0 | 0 | 0 | 0 | 0
176 | Combox(Gateway MK5),Part no: 2230006800 | 0 | 0 | 0 | 0 | 0
177 | Housing Vibration Module, MODEL NO: 3500/42-01-00 | 0 | 0 | 0 | 576872.78 | 576872.78
178 | DUAL SIESMIC MONITOR MAKE:SHINKAWA, MODEL: VM-5U-921110-000-001-0 | 0 | 0 | 0 | 0 | 0
179 | VM-5 SERIES INSTRUMENT RACK MAKE: SHINKAWA, MODEL: VM-5W1-0 | 0 | 0 | 0 | 0 | 0
180 | HYDRAULIC DEAD WEIGHT TESTER AS PER SPECIFICATIONS | 0 | 0 | 0 | 0 | 0
181 | Electronic Water Drain for SAC part no. 8102042630 | 0 | 227139.97 | 0 | 0 | 0
182 | LIGNITE BUNKER WEIGHT CALIBRATION UNIT AS PER SPEC | 0 | 0 | 0 | 0 | 0
183 | LIGNITE BUNKER WEIGHING INDICATORS AS PER SPEC | 0 | 0 | 0 | 0 | 0
184 | Flexible connector for Equipment complete set-2500A | 0 | 0 | 179485.05 | 179485.05 | 179485.05
185 | Flexible connector for Equipment complete set-1600A | 0 | 0 | 116743.47 | 116743.47 | 116743.47
186 | MOP/LOP(AC) 37KW Motor | 0 | 0 | 125766 | 125766 | 0
187 | AUMA Actuator Model No SAR12B45 | 0 | 0 | 0 | 0 | 0
188 | AUMA Actuator whole assembly Type SA15AF32+Epac . | 0 | 0 | 0 | 0 | 0
189 | Auma actuator whole assembly model SA12E125+TBG. | 0 | 0 | 0 | 0 | 0
190 | AUMA Actuator model SA50-E-90 . | 0 | 0 | 140019.57 | 140019.57 | 140019.57
191 | Gear Box for actuator SA50-E-90 . | 0 | 0 | 148318.16 | 148318.16 | 148318.16
192 | LIMITORQUE MAKE ELECTICAL ACTUATOR MODEL NO. SMB-2-60/4 | 0 | 0 | 1389073 | 1389073 | 1389073
193 | 245 KV,triple pole, Centre Post Rotating Double Break Isolators | 0 | 0 | 244794.03 | 244794.03 | 244794.03
194 | Snubber Board | 0 | 0 | 0 | 0 | 0
195 | ARECA CONTROLLER WITH FIRING CARD | 0 | 0 | 0 | 0 | 0
196 | 6.6kV 415kW 3Phase Squirrel Cage Induction Motor Frame TS500L2. | 1876679 | 0 | 1650000 | 1650000 | 1650000
197 | Stall Torque motor; SBS -125B4 ; Torque: 9.7NM for SCR | 0 | 0 | 571898.83 | 571898.83 | 571898.83
198 | Stall Torque motor; SBS -100B4 ; Torque: 4.3NM | 0 | 0 | 397728.18 | 397728.18 | 397728.18
199 | 6.6KV Grade Slip Ring Assembly for PCRD | 0 | 0 | 116259.01 | 116259.01 | 116259.01
200 | 1.1KV Grade Slip Ring Assembly for CCRD | 0 | 0 | 177447.96 | 177447.96 | 177447.96
201 | BTS2000 BUS TRANSFER SYSTEM MAIN MODULE | 0 | 0 | 0 | 0 | 0
202 | 760KW,6.6KV CWP MOTOR | 0 | 0 | 0 | 0 | 0
203 | 55 kW motor,415v,4Pole, Fr:D280S - CT Fan motor | 0 | 0 | 219000 | 219000 | 0
204 | Quantar Repeater | 0 | 0 | 0 | 0 | 0
205 | 415V, 160KW, 315L, 4Pole, Motor for Fly Ash/Bed Ash Compressor | 0 | 0 | 449553 | 449553 | 449553
206 | 6.6KV, 185KW, 315F, 4Pole Motor for Fly Ash Stg 2 Compressor | 0 | 0 | 1325600 | 1325600 | 1325600
207 | RA#5 SIEMENS SITRANS probe LU Transmitter 7M5221-2BA11 | 0 | 0 | 171232.39 | 171232.39 | 171232.39
208 | GUIDED WAVE RADAR LEVEL TR. | 0 | 0 | 0 | 0 | 0
209 | Flow meter for Circulating water forebay makeup water. | 0 | 0 | 0 | 0 | 0
210 | Flow meter for Boiler blow down (Intermediate blow down). | 0 | 0 | 0 | 0 | 0
211 | DM Conductivity Transmitter Model: 1056-01-22-30-AN +P/N 23820-00 | 0 | 0 | 0 | 0 | 0
212 | LPG Pilot Gas Ignitor ZA1- 150 P/K0K5M | 0 | 0 | 1423421 | 0 | 0
213 | RA#3 compressor Local opertor panel for ZR-37,GA160W,GA200W. | 0 | 0 | 0 | 0 | 0
214 | CPU 360 MODULE MAKE :GE MODEL NO: IC693CPU360 | 0 | 0 | 131080.34 | 131080.34 | 131080.34
215 | GENIUS BUS CONTROLLER MAKE:GE,MODEL NO: IC693BEM331 | 0 | 0 | 126113.82 | 126113.82 | 126113.82
216 | Siemens PLC, MONOMODE PROFIBUS OLM G12-1300 | 0 | 0 | 302919.37 | 302919.37 | 302919.37
217 | Siemens PLC,CP1613 FOR Industrial Ethernet Communication | 0 | 0 | 208324.63 | 208324.63 | 208324.63
218 | Siemens PLC,Communication processor CP 341-1,(POINT TO POINT LINK) | 0 | 0 | 110808.74 | 110808.74 | 110808.74
219 | Siemens PLC, Y-LINK | 0 | 0 | 0 | 0 | 0
220 | Siemens PLC - Function Module , FM350-2 COUNTER in JNT & screen | 0 | 0 | 118079.31 | 118079.31 | 0
221 | PLC HMI Operator\Engineer work station(OWS\EWS) as per spec. | 0 | 0 | 0 | 0 | 0
222 | LIMITORQUE MAKE ELECTICAL ACTUATOR MODEL NO. SMB-3-150/4 | 0 | 1829321 | 1829321 | 1829321 | 1829321
223 | BFP SCOOP MOTOR ACTUATOR ABB MAKE MODEL -RHD250 | 0 | 0 | 0 | 0 | 0
224 | BFP SCOOP CONTROL SUPPLY UNIT ABB MAKE MODEL -EBN853 | 0 | 0 | 0 | 0 | 0
225 | Current Transformer for Inter Bus Transformers | 0 | 1382399.17 | 1382399.17 | 1382399.17 | 1382399.17
226 | Current Transformer for GTs and Feeders. | 0 | 1164802.83 | 1164802.83 | 1164802.83 | 1164802.83
227 | ED7470400311 DIGITAL AVR DC-DC SUPPLY MODULE | 0 | 0 | 0 | 0 | 0
228 | ED7470400141 AVR FIRING &CONTROL MODULE | 0 | 0 | 0 | 0 | 0
229 | ED7470400133 AVR CPU MODULE | 0 | 0 | 0 | 0 | 0
230 | CN 9090389300 PULSE FINAL STAGE | 0 | 0 | 0 | 0 | 0
231 | ED7470400290 16 CHANNEL BINARY OUT PUT MODULE | 0 | 0 | 0 | 0 | 0
232 | ED7470400168 DAVR INT GEN MODULE | 0 | 356983.95 | 356983.95 | 356983.95 | 356983.95
233 | ED7470400281 DAVR I/O MODULE | 0 | 359682.65 | 359682.65 | 359682.65 | 359682.65
234 | CN9090433503 PULSE COUP STAGE MODULE | 0 | 200773.52 | 200773.52 | 200773.52 | 200773.52
235 | ED9090334114,AC/DC-DC CONVERTOR MODULE | 0 | 0 | 0 | 0 | 0
236 | CN9090110704 PULSE SUPERVISION MODULE | 0 | 156809.39 | 0 | 0 | 0
237 | ED7470400206 DAVR 16 CHANNEL O/P MDL | 0 | 124824.59 | 124824.59 | 124824.59 | 124824.59
238 | SA0653980205,AC ISOLATOR 3 POLE WITH MICRO SWITCH | 0 | 234195.85 | 234195.85 | 234195.85 | 234195.85
239 | 3 PH, 6.6 KV, 180 KW, B3, 4 P, S1, IP 55, S.C. IND. MOTOR | 0 | 954678 | 954678 | 954678 | 954678
240 | 415kV, 75kW 3Phase Squirrel Cage Induction Motor, Frame 280M | 0 | 226936.5 | 226936.5 | 226936.5 | 226936.5
241 | 415kV,90kW, 3Phase Squirrel Cage Induction Motor, Frame 315S | 0 | 278654.25 | 278654.25 | 278654.25 | 278654.25
242 | 415kV, 55kW 3Phase Squirrel Cage Induction Motor, Frame 280S | 0 | 195405 | 195405 | 195405 | 195405
243 | 415kV,160 kW, 3Phase Squirrel Cage Induction Motor, Frame 355L | 0 | 509528.25 | 509528.25 | 509528.25 | 509528.25
244 | Siemens make ACB 800amps for stacker cum reclaimer. | 0 | 178205.41 | 178205.41 | 178205.41 | 178205.41
245 | GE 800 A Spectronic ACB with LMZ7 | 0 | 232316 | 232316 | 232316 | 232316
246 | Durag Make Flame Scanner Unit, Model: D-LE-603-UA-P. | 160541 | 0 | 0 | 0 | 0
247 | Durag Make Flame Control Unit, Model-D-UG 660 -115A-420 | 0 | 0 | 0 | 0 | 0
248 | KELTRON Pneumatic Actuator Model No.C0608 252239 for SUB SA | 0 | 179050.99 | 179050.99 | 179050.99 | 179050.99
249 | KELTRON Pneumatic Actuator Model No.C0816 352239 for CombustorSAD | 0 | 195529.01 | 195529.01 | 195529.01 | 195529.01
250 | Pneumatic Actuator for Sec. Air IGV, Keltron, C1216442239 | 0 | 218646.71 | 218646.71 | 218646.71 | 218646.71
251 | PFT ,Indigenous Equivalent to CCI ,make:MASS ModelMG-10+4K | 0 | 0 | 0 | 0 | 0
252 | BFP SCOOP PFT ABB MAKE PART NO 764975 | 0 | 219114.67 | 219114.67 | 219114.67 | 219114.67
253 | MID VALUE SELECTOR MODULE ED69229S901A | 0 | 429578.68 | 429578.68 | 429578.68 | 429578.68
254 | 1 OF 3 I/P SELECTION MODULE ED69229S902A FOR TURBINE-DCS | 0 | 515111.06 | 515111.06 | 515111.06 | 515111.06
255 | POSITION MEASUREMENT MODULE ED69229S910A FOR TURBINE-DCS | 0 | 461024.7 | 461024.7 | 461024.7 | 461024.7
256 | POSITION CONTROL MODULE ED69229S914A FOR TURBINE DCS | 0 | 396036.56 | 396036.56 | 396036.56 | 396036.56
257 | Antivirus server for DCS network | 0 | 0 | 0 | 0 | 0
258 | GE PLC Series 90-30 ETHERNET INTERFACE TCP/IP MODULE, IC693CMM321 | 0 | 196280.84 | 0 | 0 | 0
259 | GE PLC Series 90-30 Genius Bus Controller,IC693BEM331. | 0 | 122274.51 | 122274.51 | 122274.51 | 122274.51
260 | GE PLC Rx3i Ethernet Module IC695ETM001,used at AHS PLC,SILO. | 0 | 111951.83 | 111951.83 | 111951.83 | 111951.83
261 | Regulator ELECTRONIKON IIID for SAC 1900071032. | 0 | 151002.94 | 0 | 0 | 0
262 | REGULATOR for SAC part no. 1900071082 | 0 | 134135.55 | 134135.55 | 134135.55 | 0
263 | ALARM UNIT for SAC part no. 1089045770 | 0 | 235998.78 | 235998.78 | 235998.78 | 117999.39
264 | Regulator ELECTRONIKON IIID for IAC 1900071032 | 0 | 149537.92 | 0 | 0 | 0
265 | Rotork Actuator Type K1000F16A | 174301.41 | 174301.41 | 174301.41 | 174301.41 | 174301.41
266 | Rotork Actuator type K300F14E | 0 | 0 | 0 | 0 | 0
267 | Rotork Actuator type K600F14A | 328445.73 | 328445.73 | 328445.73 | 328445.73 | 328445.73
268 | Rotork Actuator type K300F14A | 0 | 0 | 0 | 0 | 0
269 | Rotork Actuator type K500G3A | 162694.63 | 162694.63 | 162694.63 | 162694.63 | 162694.63
270 | E+H Liquicap Level Transmitter for Turbine Main Oil Tank | 101120.5 | 101120.5 | 101120.5 | 101120.5 | 101120.5
271 | Level control unit for Bunker Level, Endress+Hauser Make | 109250.55 | 0 | 0 | 0 | 0
272 | Ultrosonic Level Probe for Bunker Level, Make: Endress+Hauser | 213361.45 | 0 | 0 | 0 | 0
273 | DVC-6010 AD, Smart Positioner: Thum Adapter, Make Fisher | 258794 | 258794 | 258794 | 0 | 0
274 | SMART POSITIONER FOR MASONEILAN CONTROL VALVE | 0 | 0 | 0 | 0 | 0
275 | PI servo amplifier, Make: MOOG,Model G122-829-001 | 346800 | 346800 | 346800 | 346800 | 346800
|  | 0 | 7216548.58 | 23412012.24 | 45780350.84 | 60019012.56
|  | 11117359.88 | 37503744.54 | 44649001.34 | 49265439.68 | 87131480.81
|  | 3897617.88 | 21112000.04 | 22264741.44 | 35026777.96 | 63294413.62
|  | 7216548.58 | 23608293.08 | 45780350.84 | 60019012.56 | 83856079.75

## ANNEXURE XIX
Annexure-XIX
Name of the Utility: Barsingsar Thermal Power Station - 2 X 125 MW
Name of the Generating Station: Barsingsar Thermal Power Station - 2 X 125 MW
Station/ Stage/ Unit: Barsingsar Thermal Power Station - 2 X 125 MW
Fuel Type (Coal/ Lignite/ Gas/ Liquid Fuel/ Nuclear/ Hydro) :Lignite
Capacity of Plant (MW) : 250 MW (2 X 125 MW)
COD: Unit 1: 20.01.2012 Unit 2: 29.12.2011.
|  | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | Plant Availability Factor (PAF) (%) | 83.9923 | 59 | 67.0527 | 63.4807 | 58.9152 | 68.7888
2 | Plant Load Factors (PLF) (%) | 60.6666 | 58.7659 | 66.1923 | 63.2083 | 58.7194 | 68.4968
3 | Scheduled Energy (MU) | 370.1793 | 1113.309 | 1253.9138 | 1197.386 | 1115.3992 | 1297.5688
4 | Scheduled Generation (MU) | 370.1793 | 1113.309 | 1253.9138 | 1197.386 | 1115.3992 | 1297.5688
5 | Actual Generation (Export) (MU) | 302.1196 | 1114.074 | 1252.7058 | 1190.2515 | 1102.682 | 1271.0437
6 | Quantum of coal consumption (MT) | 304418.2 | 1245504 | 1479367.77 | 1351631.101 | 1212757.4741 | 1412681.79
7 | Value of coal (Rs. Lakh) | 3167.8367 | 12948.7578 | 13926.4723 | 14520.5729 | 13184.6142 | 19666.0845
8 | Specific Coal Consumption (kg/kwh) | 0.87935 | 0.97267 | 1.0288 | 0.97898 | 0.94336 | 0.96544
9 | Gross Calorific Value of Coal (Kcal/ Kg) | 2887 | 2668 | 2613.8891 | 2646.9847 | 2706.3591 | 2631.4268
10 | Heat Contribution of Coal (Kcal/kwh) | 2538.6796 | 2595.0918 | 2689.2283 | 2591.3383 | 2553.0815 | 2540.4774
11 | Cost Of Specific Coal Consumption (Rs./Kwh) – Finally admitted by CERC | 0.94474 | 1.0346 | 0.94394 | 1.034 | 1.0235 | 1.3479
12 | Quantum of Oil Consumption (Lit.) | 110320 | 722230 | 1108870 | 870713 | 1269220 | 1130623
13 | Value of Oil (Rs. lakh) | 82.0757 | 426.53 | 682.1 | 568.01 | 536.25 | 413.41
14 | Gross calorific value of oil (kcal/lit) | 9272.5566 | 9156.036 | 9144.3322 | 8922.6409 | 8782.9753 | 8913.2562
15 | Specific Oil Consumption (ml/KwHr) | 0.39311 | 0.56402 | 0.77116 | 0.63065 | 0.98728 | 0.77268
16 | Cost Of Specific Oil Consumption (Rs./Kwh) –Finally admitted by CERC | 0.092997 | 0.073822 | 0.076891 | 0.065235 | 0.04225 | 0.036565
17 | Heat Contribution of Oil (Kcal/kwh) | 3.6452 | 5.1642 | 7.0518 | 5.6271 | 8.6713 | 6.8871
18 | Station Heat Rate (kcal/kwh) | 2542.3248 | 2600.256 | 2696.2801 | 2596.9654 | 2561.7527 | 2547.3644
19 | Auxiliary Energy Consumption (%) | 12.7291 | 12.68 | 12.6076 | 13.5099 | 13.9406 | 12.8656
20 | Debt at the end of the year (Rs. Crore) | 1125.523 | 1040.84 | 968.49 | 868.9 | 784.55 | 700.21
21 | Equity/IR (Rs. Crore) | 482.36 | 486.87 | 507.24 | 507.24 | 508.16 | 508.16
22 | Working Capital (Rs. Crore) – finally admitted by CERC | 27.75 | 122.57 | 122.22 | 122.04 | 124.45 | 125.11
23 | Capital cost (Rs. Crore) – finally admitted by CERC | 1607.89 | 1622.91 | 1690.81 | 1690.8103 | 1693.8593 | 1693.8593
24 | Capacity Charges/ Annual Fixed Cost (AFC) | 100.66 | 412.63 | 391.63 | 368.66 | 364.2442 | 360.3925
(a) Return on equity – pre tax (admitted by CERC)
| Absolute value | 25.09 | 93.9 | 114.04 | 99.56 | 100.13 | 100.13
| Rate (%) | 22.94 | 20 | 22 | 19.61 | 19.705 | 19.705
(b) interest on Loan
| Absolute value | 24.43 | 101.04 | 93.98 | 94.01 | 85.15 | 76.36
| Rate (%) – Weighted Average Rate | 9.71 | 9.71 | 9.71 | 10.33% | 10.3% | 10.29%
(c) Depreciation (finally allowed by CERC)
| Absolute value | 29.78 | 120.3 | 82.44 | 84.26 | 84.34 | 84.34
| Rate (%) | 8.18 | 7.455 | 4.981 | 4.979 | 4.979 | 4.979
(d) Interest on working Capital
| Absolute value | 3.37 | 14.4 | 14.13 | 16.48 | 16.8 | 16.89
| Rate (%) | 11.75 | 11.75 | 11.75 | 13.5 | 13.5 | 13.5
(e) Operation and maintenance cost (finally admitted by CERC)
| Absolute value | 15.2 | 70.9 | 74.95 | 74.34 | 77.81 | 82.66
Rate (%)
(f) Compensation Allowances
25 | AFC (Rs. Kwh0 | 3.1523 | 2.839 | 2.694 | 2.536 | 2.343 | 2.324
26 | Energy Charge (Rs./Kwh) | 1.0377 | 1.441 | 1.426 | 1.444 | 1.597 | 1.812
27 | Total tariff (Rs. Kwh) | 4.19 | 4.28 | 4.12 | 3.98 | 3.94 | 4.136
28 | Revenue realisation before tax (Rs. Crore) | 127.7059 | 465.9498 | 516.7395 | 451.5063 | 433.9547 | 527.9632
29 | Revenue realisation after tax (Rs. Crore)
30 | Profit/ loss (Rs. Crore0 | 0 | 93.9662 | 115.1937 | 85.5861 | 78.2695 | 175.9812
31 | DSM Generation (MU) | -68.0598 | 0.706 | -1.1779 | -7.1345 | -12.7172 | -26.5251
32 | DSM Rate (Ps/Kwh) | 0.66514 | -0.33994 | -479.2 | -175.8908 | -196.7342 | -193.9946
33 | Revenue from DSM (Rs. Crore) | 0.045269 | -0.024 | -0.56444 | -1.2549 | -2.5019 | -5.1457
Note: | For SL.NO. 31 to 33 values are provisional only, as UI/ DSM Statement yet to be issued by RDPPC.
The sign of DSM energy and rate indicates -ve is payable and + ve is receivable.